## Change Log
Entry # | Date | Name | New Document Name | Cell/Range Modified | Changes Made | Comments
1 | 2020-04-14 | Duncan Prahl | 2020_0414_ac_current_circuits_hourly | Change Log sheet | Change log sheet created
Orlando, Please change the following: 1. Put four columns on each Step1.x sheet, one for each circuit on a single datalogger. That way a single logger export will go into each sheet, with up to four channels from the logger per sheet 2. We need to develop an hourly schedule that can be used by the DEM team in thier calc tool to estimate the interactive effects. What we need to derive is an estimate of hours on and off on a weekday and weekend by comparing the total connected load to the time when the lights start being used and the hours when the lights are turned off.
| 2020-04-27 | Orlando Castillo | 2020_0427_ac_current_circuits_hourly | Results | Results sheet modified calcs | 1. changed the calculations include holiday days
[5 empty] | Raw Data tab | 1. included cells for user to input amount of holiday days that affect schedule 2. added cells that ask user if the panelboard is mixed or dedicated, based on that input the spreadsheet will determine what calculation to perform to determine the % measured load.
| 2020-06-10 | Duncan Prahl | 2020_0610_... | Step4 |  | Formatted Text, modified so calcs matched methodology in guide (Ave hour, day, etc.)
|  |  |  | Step4A |  | Rearranged Days
|  |  | 2020_0625 | Step 1.1 | Raw Data tab | 1. added cell that asks user if load is balanced or unbalanced. 2. user input cells for RMS V, PF and True RMS kW for each phase if load is unbalanced.
|  |  | 2020_0625 | step 2 | power calc | 1. added columns for each circuit that shows kW result for balanced and unbalanced load depending on user input in step 1.1 2. removed sqrt(3) factor in kW calculations since that is only necessary when calculating total panelboard kW
|  |  | 2020_0625 | step 3 | Ave Energy Calc | 1. adjusted function for kWh to determine if the input data is from a balanced or unbalanced load

## Intro
Introduction and Instructions
Input Facility Name, Type
Model Description
Measured variables: Average hourly amperage per circuit, Circuit voltage and power facto, true RMS power (kW) of all lighting measured.
General annual equation: Total lighting energy = Hourly current converted to kW, Sum kW per week (kWh) * 52
Model Instructions
The yellow cells are the input cells.
Data should only be input in the Raw Data Input tab (step 1)
Calculations are shown in Runtime Calculations and Annual Energy Calc
Determine if the panelboard load is balanced or unbalanced.
If unbalanced measure RMS Voltage, True RMS kW and power factor of each phase line
When measuring circuit(s) take note of what phase that circuit is attributed to
If measuring groups of circuits with a single sensor ensure all circuits are attributed to the same phase
Helpful links
to logger tools
to documentation

## Step 1.1 Raw Data
Datetime | Circuit #1 AC Current (Amps) | Circuit #2 AC Current (Amps) | Circuit #3 AC Current (Amps) | Circuit #4 AC Current (Amps) | 1 | Does the Panelboard have a balanced load? Input 0 if balanced, input 1 if unbalanced, input 0 if unsure
2018-02-01 10:00 | 86.7201 | 86.7018 | 87.0329 | 17.3735 |  | 0
2018-02-01 11:00 | 86.6697 | 86.92 | 87.0665 | 66.1149
2018-02-01 12:00 | 86.6209 | 86.8498 | 87.0954 | 66.0992
2018-02-01 13:00 | 86.5003 | 86.7323 | 87.0253 | 66.0279 | 2 | If unbalanced, input phase that each measured circuit is attributed to, if balanced skip to step 3
2018-02-01 14:00 | 86.54 | 86.6804 | 86.9703 | 65.9873 |  | input 1 if phase 1, input 2 is phase 2, input 3 if phase 3
2018-02-01 15:00 | 86.4958 | 86.7079 | 87.0542 | 66.0296
2018-02-01 16:00 | 86.5171 | 86.7857 | 87.0405 | 66.054 |  | Circuit 1 | Circuit 2 | Circuit 3 | Circuit 4
2018-02-01 17:00 | 86.3813 | 86.6392 | 87.0085 | 65.9861
2018-02-01 18:00 | 86.537 | 86.6407 | 87.0695 | 66.0099
2018-02-01 19:00 | 86.6224 | 86.8544 | 87.1382 | 66.1172
2018-02-01 20:00 | 86.537 | 86.7628 | 87.1458 | 66.0853 | 3 | *If the panelboard load is balanced input measured values in the Phase 1 column only
2018-02-01 21:00 | 86.5171 | 86.746 | 86.981 | 66.0163
2018-02-01 22:00 | 86.5278 | 86.7292 | 86.9444 | 65.996 |  |  | Line 1* | Line 2 | Line 3
2018-02-01 23:00 | 86.5461 | 86.8818 | 87.1351 | 66.1264 |  | RMS Voltage (V) | 211
2018-02-02 | 0 | 86.7842 | 87.1504 | 66.0951 |  | Power Factor | 0.99
2018-02-02 01:00 | 0 | 86.8605 | 87.0115 | 66.0714 |  | True RMS Power (kW) | 100
2018-02-02 02:00 | 0 | 86.8482 | 87.1885 | 66.1339
2018-02-02 03:00 | 0 | 86.8681 | 87.1641 | 66.1322
2018-02-02 04:00 | 0 | 86.7994 | 87.1229 | 66.0905 | 4 | How many holiday days affect the normal operating schedule?
2018-02-02 05:00 | 0 | 86.8055 | 87.1916 | 66.1189 |  | 0
2018-02-02 06:00 | 0 | 86.8086 | 87.1778 | 66.1148
2018-02-02 07:00 | 0 | 86.865 | 87.2572 | 66.1664
2018-02-02 08:00 | 0 | 86.7994 | 87.1473 | 66.0997
2018-02-02 09:00 | 0 | 86.8925 | 87.1641 | 66.1415
2018-02-02 10:00 | 0 | 86.8956 | 87.2297 | 66.1676
2018-02-02 11:00 | 0 | 86.7704 | 87.1031 | 66.0719
2018-02-02 12:00 | 0 | 86.8101 | 87.0329 | 66.0603
2018-02-02 13:00 | 0 | 86.8727 | 87.1366 | 66.1235
2018-02-02 14:00 | 0 | 86.7964 | 87.0344 | 66.0557
2018-02-02 15:00 | 0 | 86.6041 | 87.0344 | 65.9826
2018-02-02 16:00 | 0 | 86.8391 | 87.1321 | 66.1091
2018-02-02 17:00 | 0 | 86.804 | 86.9657 | 66.0325
2018-02-02 18:00 | 0 | 86.9017 | 87.187 | 66.1537
2018-02-02 19:00 | 0 | 86.4302 | 86.6423 | 65.7675
2018-02-02 20:00 | 0 | 86.6499 | 86.8513 | 65.9305
2018-02-02 21:00 | 0 | 86.6438 | 86.9703 | 65.9734
2018-02-02 22:00 | 0 | 86.6453 | 86.978 | 65.9769
2018-02-02 23:00 | 0 | 86.5202 | 86.9078 | 65.9026
2018-02-03 | 86.0121 | 0 | 86.5507 | 32.8893
2018-02-03 01:00 | 85.919 | 0 | 86.5324 | 32.8823
2018-02-03 02:00 | 86.0533 | 0 | 86.6453 | 32.9252
2018-02-03 03:00 | 86.1677 | 0 | 86.7002 | 32.9461
2018-02-03 04:00 | 86.3081 | 0 | 86.8513 | 33.0035
2018-02-03 05:00 | 86.2562 | 0 | 86.8605 | 33.007
2018-02-03 06:00 | 86.1234 | 0 | 86.6682 | 32.9339
2018-02-03 07:00 | 86.1906 | 0 | 86.7247 | 32.9554
2018-02-03 08:00 | 86.36 | 0 | 86.952 | 33.0418
2018-02-03 09:00 | 86.4912 | 0 | 87.0588 | 33.0823
2018-02-03 10:00 | 86.1982 | 0 | 86.6392 | 32.9229
2018-02-03 11:00 | 86.1707 | 0 | 86.8849 | 33.0163
2018-02-03 12:00 | 86.5019 | 0 | 87.1504 | 33.1172
2018-02-03 13:00 | 86.6148 | 0 | 87.3167 | 33.1803
2018-02-03 14:00 | 86.4439 | 0 | 87.0832 | 33.0916
2018-02-03 15:00 | 86.5522 | 0 | 87.2938 | 33.1716
2018-02-03 16:00 | 86.5644 | 0 | 87.3579 | 33.196
2018-02-03 17:00 | 86.7445 | 0 | 87.57 | 33.2766
2018-02-03 18:00 | 86.4668 | 0 | 87.3014 | 33.1745
2018-02-03 19:00 | 86.3661 | 0 | 87.0954 | 33.0963
2018-02-03 20:00 | 86.1173 | 0 | 86.891 | 33.0186
2018-02-03 21:00 | 86.1555 | 0 | 86.9245 | 33.0313
2018-02-03 22:00 | 86.2211 | 0 | 87.0054 | 33.0621
2018-02-03 23:00 | 86.2226 | 0 | 87.0787 | 33.0899
2018-02-04 | 86.2364 | 86.7994 | 0 | 32.9838
2018-02-04 01:00 | 86.3188 | 86.952 | 0 | 33.0418
2018-02-04 02:00 | 86.2119 | 86.8177 | 0 | 32.9907
2018-02-04 03:00 | 86.1845 | 86.7857 | 0 | 32.9786
2018-02-04 04:00 | 86.2455 | 86.833 | 0 | 32.9965
2018-02-04 05:00 | 86.2333 | 86.833 | 0 | 32.9965
2018-02-04 06:00 | 86.2776 | 86.8528 | 0 | 33.0041
2018-02-04 07:00 | 86.2867 | 86.8452 | 0 | 33.0012
2018-02-04 08:00 | 86.2989 | 86.9032 | 0 | 33.0232
2018-02-04 09:00 | 86.2867 | 86.8162 | 0 | 32.9902
2018-02-04 10:00 | 86.2882 | 86.8528 | 0 | 33.0041
2018-02-04 11:00 | 86.1845 | 86.743 | 0 | 32.9623
2018-02-04 12:00 | 86.1418 | 86.714 | 0 | 32.9513
2018-02-04 13:00 | 86.1479 | 86.7659 | 0 | 32.971
2018-02-04 14:00 | 86.1112 | 86.7018 | 0 | 32.9467
2018-02-04 15:00 | 86.2455 | 86.8482 | 0 | 33.0023
2018-02-04 16:00 | 86.3447 | 86.9398 | 0 | 33.0371
2018-02-04 17:00 | 86.4805 | 86.9856 | 0 | 33.0545
2018-02-04 18:00 | 86.4332 | 86.92 | 0 | 33.0296
2018-02-04 19:00 | 85.6794 | 85.9266 | 0 | 32.6521
2018-02-04 20:00 | 86.3294 | 86.5888 | 0 | 32.9037
2018-02-04 21:00 | 86.3569 | 86.6728 | 0 | 32.9357
2018-02-04 22:00 | 86.4881 | 86.8086 | 0 | 32.9873
2018-02-04 23:00 | 86.4332 | 86.7353 | 0 | 32.9594
2018-02-05 | 86.4088 | 86.7002 | 86.9352 | 65.9815
2018-02-05 01:00 | 86.0426 | 86.3127 | 86.5278 | 65.6794
2018-02-05 02:00 | 86.392 | 86.6392 | 86.8421 | 65.9229
2018-02-05 03:00 | 86.2776 | 86.5766 | 86.7536 | 65.8655
2018-02-05 04:00 | 86.5034 | 86.8849 | 87.0283 | 66.087
2018-02-05 05:00 | 86.3661 | 86.772 | 87.0054 | 66.0354
2018-02-05 06:00 | 86.2898 | 86.6499 | 86.8147 | 65.9165
2018-02-05 07:00 | 86.2043 | 86.5278 | 86.7079 | 65.8296
2018-02-05 08:00 | 86.3355 | 86.5461 | 86.8025 | 65.8725
2018-02-05 09:00 | 86.3798 | 86.7262 | 86.8711 | 65.967
2018-02-05 10:00 | 86.2272 | 86.5156 | 86.714 | 65.8272
2018-02-05 11:00 | 86.2119 | 86.5141 | 86.7201 | 65.829
2018-02-05 12:00 | 86.389 | 86.6835 | 86.8574 | 65.9455
2018-02-05 13:00 | 86.4027 | 86.6224 | 86.7475 | 65.8806
2018-02-05 14:00 | 86.3783 | 86.6606 | 86.7903 | 65.9113
2018-02-05 15:00 | 86.3355 | 86.5248 | 86.7384 | 65.84
2018-02-05 16:00 | 86.3493 | 86.4912 | 86.685 | 65.807
2018-02-05 17:00 | 86.244 | 86.4683 | 86.6743 | 65.7942
2018-02-05 18:00 | 86.3142 | 86.4378 | 86.5934 | 65.7519
2018-02-05 19:00 | 86.2089 | 86.3508 | 86.5583 | 65.7055
2018-02-05 20:00 | 86.2181 | 86.4836 | 86.6896 | 65.8058
2018-02-05 21:00 | 86.1494 | 86.4759 | 86.63 | 65.7802
2018-02-05 22:00 | 86.2593 | 86.5522 | 86.6468 | 65.8156
2018-02-05 23:00 | 86.4424 | 86.8055 | 86.8864 | 66.0029
2018-02-06 | 86.4637 | 0 | 0 | 0
2018-02-06 01:00 | 86.5629 | 0 | 0 | 0
2018-02-06 02:00 | 86.3706 | 0 | 0 | 0
2018-02-06 03:00 | 86.3523 | 0 | 0 | 0
2018-02-06 04:00 | 86.3676 | 0 | 0 | 0
2018-02-06 05:00 | 86.4027 | 0 | 0 | 0
2018-02-06 06:00 | 86.4652 | 0 | 0 | 0
2018-02-06 07:00 | 86.4012 | 0 | 0 | 0
2018-02-06 08:00 | 86.4515 | 0 | 0 | 0
2018-02-06 09:00 | 86.2028 | 0 | 0 | 0
2018-02-06 10:00 | 86.2715 | 0 | 0 | 0
2018-02-06 11:00 | 86.7567 | 0 | 0 | 0
2018-02-06 12:00 | 86.6194 | 0 | 0 | 0
2018-02-06 13:00 | 86.6377 | 0 | 0 | 0
2018-02-06 14:00 | 86.8757 | 0 | 0 | 0
2018-02-06 15:00 | 86.7994 | 0 | 0 | 0
2018-02-06 16:00 | 86.7674 | 0 | 0 | 0
2018-02-06 17:00 | 86.7384 | 0 | 0 | 0
2018-02-06 18:00 | 86.7124 | 0 | 0 | 0
2018-02-06 19:00 | 86.8376 | 0 | 0 | 0
2018-02-06 20:00 | 86.627 | 0 | 0 | 0
2018-02-06 21:00 | 86.6239 | 0 | 0 | 0
2018-02-06 22:00 | 86.714 | 0 | 0 | 0
2018-02-06 23:00 | 86.8971 | 0 | 0 | 0
2018-02-07 | 0 | 0 | 86.6712 | 32.9351
2018-02-07 01:00 | 0 | 0 | 86.511 | 32.8742
2018-02-07 02:00 | 0 | 0 | 86.7628 | 32.9699
2018-02-07 03:00 | 0 | 0 | 86.7384 | 32.9606
2018-02-07 04:00 | 0 | 0 | 86.8376 | 32.9983
2018-02-07 05:00 | 0 | 0 | 87.0222 | 33.0684
2018-02-07 06:00 | 0 | 0 | 86.9627 | 33.0458
2018-02-07 07:00 | 0 | 0 | 87.1321 | 33.1102
2018-02-07 08:00 | 0 | 0 | 87.1931 | 33.1334
2018-02-07 09:00 | 0 | 0 | 86.7155 | 32.9519
2018-02-07 10:00 | 0 | 0 | 86.6743 | 32.9362
2018-02-07 11:00 | 0 | 0 | 86.8956 | 33.0203
2018-02-07 12:00 | 0 | 0 | 86.9276 | 33.0325
2018-02-07 13:00 | 0 | 0 | 87.2541 | 33.1566
2018-02-07 14:00 | 0 | 0 | 87.4037 | 33.2134
2018-02-07 15:00 | 0 | 0 | 87.2129 | 33.1409
2018-02-07 16:00 | 0 | 0 | 86.9718 | 33.0493
2018-02-07 17:00 | 0 | 0 | 87.1397 | 33.1131
2018-02-07 18:00 | 0 | 0 | 87.2435 | 33.1525
2018-02-07 19:00 | 0 | 0 | 86.8894 | 33.018
2018-02-07 20:00 | 0 | 0 | 87.1839 | 33.1299
2018-02-07 21:00 | 0 | 0 | 87.2419 | 33.1519
2018-02-07 22:00 | 0 | 0 | 87.1733 | 33.1259
2018-02-07 23:00 | 0 | 0 | 87.2557 | 33.1572
2018-02-08 | 86.5492 | 0 | 0 | 0
2018-02-08 01:00 | 86.7201 | 0 | 0 | 0
2018-02-08 02:00 | 86.5095 | 0 | 0 | 0
2018-02-08 03:00 | 86.4576 | 0 | 0 | 0
2018-02-08 04:00 | 86.6316 | 0 | 0 | 0
2018-02-08 05:00 | 86.569 | 0 | 0 | 0
2018-02-08 06:00 | 86.6468 | 0 | 0 | 0
2018-02-08 07:00 | 86.6361 | 0 | 0 | 0
2018-02-08 08:00 | 86.6819 | 0 | 0 | 0
2018-02-08 09:00 | 86.7094 | 0 | 0 | 0
2018-02-08 10:00 | 86.7933 | 0 | 0 | 0
2018-02-08 11:00 | 86.8009 | 0 | 0 | 0
2018-02-08 12:00 | 86.6728 | 0 | 0 | 0
2018-02-08 13:00 | 86.6316 | 0 | 0 | 0
2018-02-08 14:00 | 86.6316 | 0 | 0 | 0
2018-02-08 15:00 | 86.6636 | 0 | 0 | 0
2018-02-08 16:00 | 86.5568 | 0 | 0 | 0
2018-02-08 17:00 | 86.6865 | 0 | 0 | 0
2018-02-08 18:00 | 86.7262 | 0 | 0 | 0
2018-02-08 19:00 | 86.5187 | 0 | 0 | 0
2018-02-08 20:00 | 86.5766 | 0 | 0 | 0
2018-02-08 21:00 | 86.6194 | 0 | 0 | 0
2018-02-08 22:00 | 86.6743 | 0 | 0 | 0
2018-02-08 23:00 | 86.5644 | 0 | 0 | 0
2018-02-09 | 86.2226 | 86.688 | 0 | 32.9414
2018-02-09 01:00 | 86.1128 | 86.5232 | 0 | 32.8788
2018-02-09 02:00 | 86.2791 | 86.6896 | 0 | 32.942
2018-02-09 03:00 | 86.0014 | 86.4485 | 0 | 32.8504
2018-02-09 04:00 | 86.0533 | 86.4347 | 0 | 32.8452
2018-02-09 05:00 | 86.2257 | 86.6117 | 0 | 32.9124
2018-02-09 06:00 | 86.4332 | 86.9352 | 0 | 33.0354
2018-02-09 07:00 | 86.5873 | 87.0619 | 0 | 33.0835
2018-02-09 08:00 | 86.3691 | 86.7811 | 0 | 32.9768
2018-02-09 09:00 | 86.334 | 86.7399 | 0 | 32.9612
2018-02-09 10:00 | 86.5126 | 86.862 | 0 | 33.0076
2018-02-09 11:00 | 86.5003 | 86.9306 | 0 | 33.0336
2018-02-09 12:00 | 86.7002 | 87.1412 | 0 | 33.1137
2018-02-09 13:00 | 86.363 | 86.8009 | 0 | 32.9843
2018-02-09 14:00 | 86.4408 | 86.8635 | 0 | 33.0081
2018-02-09 15:00 | 86.2943 | 86.6743 | 0 | 32.9362
2018-02-09 16:00 | 86.3706 | 86.7491 | 0 | 32.9647
2018-02-09 17:00 | 86.2882 | 86.7445 | 0 | 32.9629
2018-02-09 18:00 | 86.1875 | 86.6667 | 0 | 32.9333
2018-02-09 19:00 | 86.099 | 86.5431 | 0 | 32.8864
2018-02-09 20:00 | 86.1997 | 86.5187 | 0 | 32.8771
2018-02-09 21:00 | 86.3767 | 86.7247 | 0 | 32.9554
2018-02-09 22:00 | 86.3691 | 86.7659 | 0 | 32.971
2018-02-09 23:00 | 86.4012 | 86.7918 | 0 | 32.9809
2018-02-10 | 86.0121 | 0 | 86.5507 | 32.8893
2018-02-10 01:00 | 85.919 | 0 | 86.5324 | 32.8823
2018-02-10 02:00 | 86.0533 | 0 | 86.6453 | 32.9252
2018-02-10 03:00 | 86.1677 | 0 | 86.7002 | 32.9461
2018-02-10 04:00 | 86.3081 | 0 | 86.8513 | 33.0035
2018-02-10 05:00 | 86.2562 | 0 | 86.8605 | 33.007
2018-02-10 06:00 | 86.1234 | 0 | 86.6682 | 32.9339
2018-02-10 07:00 | 86.1906 | 0 | 86.7247 | 32.9554
2018-02-10 08:00 | 86.36 | 0 | 86.952 | 33.0418
2018-02-10 09:00 | 86.4912 | 0 | 87.0588 | 33.0823
2018-02-10 10:00 | 86.1982 | 0 | 86.6392 | 32.9229
2018-02-10 11:00 | 86.1707 | 0 | 86.8849 | 33.0163
2018-02-10 12:00 | 86.5019 | 0 | 87.1504 | 33.1172
2018-02-10 13:00 | 86.6148 | 0 | 87.3167 | 33.1803
2018-02-10 14:00 | 86.4439 | 0 | 87.0832 | 33.0916
2018-02-10 15:00 | 86.5522 | 0 | 87.2938 | 33.1716
2018-02-10 16:00 | 86.5644 | 0 | 87.3579 | 33.196
2018-02-10 17:00 | 86.7445 | 0 | 87.57 | 33.2766
2018-02-10 18:00 | 86.4668 | 0 | 87.3014 | 33.1745
2018-02-10 19:00 | 86.3661 | 0 | 87.0954 | 33.0963
2018-02-10 20:00 | 86.1173 | 0 | 86.891 | 33.0186
2018-02-10 21:00 | 86.1555 | 0 | 86.9245 | 33.0313
2018-02-10 22:00 | 86.2211 | 0 | 87.0054 | 33.0621
2018-02-10 23:00 | 86.2226 | 0 | 87.0787 | 33.0899
2018-02-11 | 86.2364 | 86.7994 | 0 | 32.9838
2018-02-11 01:00 | 86.3188 | 86.952 | 0 | 33.0418
2018-02-11 02:00 | 86.2119 | 86.8177 | 0 | 32.9907
2018-02-11 03:00 | 86.1845 | 86.7857 | 0 | 32.9786
2018-02-11 04:00 | 86.2455 | 86.833 | 0 | 32.9965
2018-02-11 05:00 | 86.2333 | 86.833 | 0 | 32.9965
2018-02-11 06:00 | 86.2776 | 86.8528 | 0 | 33.0041
2018-02-11 07:00 | 86.2867 | 86.8452 | 0 | 33.0012
2018-02-11 08:00 | 86.2989 | 86.9032 | 0 | 33.0232
2018-02-11 09:00 | 86.2867 | 86.8162 | 0 | 32.9902
2018-02-11 10:00 | 86.2882 | 86.8528 | 0 | 33.0041
2018-02-11 11:00 | 86.1845 | 86.743 | 0 | 32.9623
2018-02-11 12:00 | 86.1418 | 86.714 | 0 | 32.9513
2018-02-11 13:00 | 86.1479 | 86.7659 | 0 | 32.971
2018-02-11 14:00 | 86.1112 | 86.7018 | 0 | 32.9467
2018-02-11 15:00 | 86.2455 | 86.8482 | 0 | 33.0023
2018-02-11 16:00 | 86.3447 | 86.9398 | 0 | 33.0371
2018-02-11 17:00 | 86.4805 | 86.9856 | 0 | 33.0545
2018-02-11 18:00 | 86.4332 | 86.92 | 0 | 33.0296
2018-02-11 19:00 | 85.6794 | 85.9266 | 0 | 32.6521
2018-02-11 20:00 | 86.3294 | 86.5888 | 0 | 32.9037
2018-02-11 21:00 | 86.3569 | 86.6728 | 0 | 32.9357
2018-02-11 22:00 | 86.4881 | 86.8086 | 0 | 32.9873
2018-02-11 23:00 | 86.4332 | 86.7353 | 0 | 32.9594
2018-02-12 | 86.4088 | 86.7002 | 86.9352 | 65.9815
2018-02-12 01:00 | 86.0426 | 86.3127 | 86.5278 | 65.6794
2018-02-12 02:00 | 86.392 | 86.6392 | 86.8421 | 65.9229
2018-02-12 03:00 | 86.2776 | 86.5766 | 86.7536 | 65.8655
2018-02-12 04:00 | 86.5034 | 86.8849 | 87.0283 | 66.087
2018-02-12 05:00 | 86.3661 | 86.772 | 87.0054 | 66.0354
2018-02-12 06:00 | 86.2898 | 86.6499 | 86.8147 | 65.9165
2018-02-12 07:00 | 86.2043 | 86.5278 | 86.7079 | 65.8296
2018-02-12 08:00 | 86.3355 | 86.5461 | 86.8025 | 65.8725
2018-02-12 09:00 | 86.3798 | 86.7262 | 86.8711 | 65.967
2018-02-12 10:00 | 86.2272 | 86.5156 | 86.714 | 65.8272
2018-02-12 11:00 | 86.2119 | 86.5141 | 86.7201 | 65.829
2018-02-12 12:00 | 86.389 | 86.6835 | 86.8574 | 65.9455
2018-02-12 13:00 | 86.4027 | 86.6224 | 86.7475 | 65.8806
2018-02-12 14:00 | 86.3783 | 86.6606 | 86.7903 | 65.9113
2018-02-12 15:00 | 86.3355 | 86.5248 | 86.7384 | 65.84
2018-02-12 16:00 | 86.3493 | 86.4912 | 86.685 | 65.807
2018-02-12 17:00 | 86.244 | 86.4683 | 86.6743 | 65.7942
2018-02-12 18:00 | 86.3142 | 86.4378 | 86.5934 | 65.7519
2018-02-12 19:00 | 86.2089 | 86.3508 | 86.5583 | 65.7055
2018-02-12 20:00 | 86.2181 | 86.4836 | 86.6896 | 65.8058
2018-02-12 21:00 | 86.1494 | 86.4759 | 86.63 | 65.7802
2018-02-12 22:00 | 86.2593 | 86.5522 | 86.6468 | 65.8156
2018-02-12 23:00 | 86.4424 | 86.8055 | 86.8864 | 66.0029
2018-02-13 | 86.4637 | 0 | 0 | 0
2018-02-13 01:00 | 86.5629 | 0 | 0 | 0
2018-02-13 02:00 | 86.3706 | 0 | 0 | 0
2018-02-13 03:00 | 86.3523 | 0 | 0 | 0
2018-02-13 04:00 | 86.3676 | 0 | 0 | 0
2018-02-13 05:00 | 86.4027 | 0 | 0 | 0
2018-02-13 06:00 | 86.4652 | 0 | 0 | 0
2018-02-13 07:00 | 86.4012 | 0 | 0 | 0
2018-02-13 08:00 | 86.4515 | 0 | 0 | 0
2018-02-13 09:00 | 86.2028 | 0 | 0 | 0
2018-02-13 10:00 | 86.2715 | 0 | 0 | 0
2018-02-13 11:00 | 86.7567 | 0 | 0 | 0
2018-02-13 12:00 | 86.6194 | 0 | 0 | 0
2018-02-13 13:00 | 86.6377 | 0 | 0 | 0
2018-02-13 14:00 | 86.8757 | 0 | 0 | 0
2018-02-13 15:00 | 86.7994 | 0 | 0 | 0
2018-02-13 16:00 | 86.7674 | 0 | 0 | 0
2018-02-13 17:00 | 86.7384 | 0 | 0 | 0
2018-02-13 18:00 | 86.7124 | 0 | 0 | 0
2018-02-13 19:00 | 86.8376 | 0 | 0 | 0
2018-02-13 20:00 | 86.627 | 0 | 0 | 0
2018-02-13 21:00 | 86.6239 | 0 | 0 | 0
2018-02-13 22:00 | 86.714 | 0 | 0 | 0
2018-02-13 23:00 | 86.8971 | 0 | 0 | 0
2018-02-14 | 0 | 0 | 86.6712 | 32.9351
2018-02-14 01:00 | 0 | 0 | 86.511 | 32.8742
2018-02-14 02:00 | 0 | 0 | 86.7628 | 32.9699
2018-02-14 03:00 | 0 | 0 | 86.7384 | 32.9606
2018-02-14 04:00 | 0 | 0 | 86.8376 | 32.9983
2018-02-14 05:00 | 0 | 0 | 87.0222 | 33.0684
2018-02-14 06:00 | 0 | 0 | 86.9627 | 33.0458
2018-02-14 07:00 | 0 | 0 | 87.1321 | 33.1102
2018-02-14 08:00 | 0 | 0 | 87.1931 | 33.1334
2018-02-14 09:00 | 0 | 0 | 86.7155 | 32.9519
2018-02-14 10:00 | 0 | 0 | 86.6743 | 32.9362
2018-02-14 11:00 | 0 | 0 | 86.8956 | 33.0203
2018-02-14 12:00 | 0 | 0 | 86.9276 | 33.0325
2018-02-14 13:00 | 0 | 0 | 87.2541 | 33.1566
2018-02-14 14:00 | 0 | 0 | 87.4037 | 33.2134
2018-02-14 15:00 | 0 | 0 | 87.2129 | 33.1409
2018-02-14 16:00 | 0 | 0 | 86.9718 | 33.0493
2018-02-14 17:00 | 0 | 0 | 87.1397 | 33.1131
2018-02-14 18:00 | 0 | 0 | 87.2435 | 33.1525
2018-02-14 19:00 | 0 | 0 | 86.8894 | 33.018
2018-02-14 20:00 | 0 | 0 | 87.1839 | 33.1299
2018-02-14 21:00 | 0 | 0 | 87.2419 | 33.1519
2018-02-14 22:00 | 0 | 0 | 87.1733 | 33.1259
2018-02-14 23:00 | 0 | 0 | 87.2557 | 33.1572
2018-02-15 | 86.5492 | 0 | 0 | 0
2018-02-15 01:00 | 86.7201 | 0 | 0 | 0
2018-02-15 02:00 | 86.5095 | 0 | 0 | 0
2018-02-15 03:00 | 86.4576 | 0 | 0 | 0
2018-02-15 04:00 | 86.6316 | 0 | 0 | 0
2018-02-15 05:00 | 86.569 | 0 | 0 | 0
2018-02-15 06:00 | 86.6468 | 0 | 0 | 0
2018-02-15 07:00 | 86.6361 | 0 | 0 | 0
2018-02-15 08:00 | 86.6819 | 0 | 0 | 0
2018-02-15 09:00 | 86.7094 | 0 | 0 | 0
2018-02-15 10:00 | 86.7933 | 0 | 0 | 0
2018-02-15 11:00 | 86.8009 | 0 | 0 | 0
2018-02-15 12:00 | 86.6728 | 0 | 0 | 0
2018-02-15 13:00 | 86.6316 | 0 | 0 | 0
2018-02-15 14:00 | 86.6316 | 0 | 0 | 0
2018-02-15 15:00 | 86.6636 | 0 | 0 | 0
2018-02-15 16:00 | 86.5568 | 0 | 0 | 0
2018-02-15 17:00 | 86.6865 | 0 | 0 | 0
2018-02-15 18:00 | 86.7262 | 0 | 0 | 0
2018-02-15 19:00 | 86.5187 | 0 | 0 | 0
2018-02-15 20:00 | 86.5766 | 0 | 0 | 0
2018-02-15 21:00 | 86.6194 | 0 | 0 | 0
2018-02-15 22:00 | 86.6743 | 0 | 0 | 0
2018-02-15 23:00 | 86.5644 | 0 | 0 | 0
2018-02-16 | 86.2226 | 86.688 | 0 | 32.9414
2018-02-16 01:00 | 86.1128 | 86.5232 | 0 | 32.8788
2018-02-16 02:00 | 86.2791 | 86.6896 | 0 | 32.942
2018-02-16 03:00 | 86.0014 | 86.4485 | 0 | 32.8504
2018-02-16 04:00 | 86.0533 | 86.4347 | 0 | 32.8452
2018-02-16 05:00 | 86.2257 | 86.6117 | 0 | 32.9124
2018-02-16 06:00 | 86.4332 | 86.9352 | 0 | 33.0354
2018-02-16 07:00 | 86.5873 | 87.0619 | 0 | 33.0835
2018-02-16 08:00 | 86.3691 | 86.7811 | 0 | 32.9768
2018-02-16 09:00 | 86.334 | 86.7399 | 0 | 32.9612
2018-02-16 10:00 | 86.5126 | 86.862 | 0 | 33.0076
2018-02-16 11:00 | 86.5003 | 86.9306 | 0 | 33.0336
2018-02-16 12:00 | 86.7002 | 87.1412 | 0 | 33.1137
2018-02-16 13:00 | 86.363 | 86.8009 | 0 | 32.9843
2018-02-16 14:00 | 86.4408 | 86.8635 | 0 | 33.0081
2018-02-16 15:00 | 86.2943 | 86.6743 | 0 | 32.9362
2018-02-16 16:00 | 86.3706 | 86.7491 | 0 | 32.9647
2018-02-16 17:00 | 86.2882 | 86.7445 | 0 | 32.9629
2018-02-16 18:00 | 86.1875 | 86.6667 | 0 | 32.9333
2018-02-16 19:00 | 86.099 | 86.5431 | 0 | 32.8864
2018-02-16 20:00 | 86.1997 | 86.5187 | 0 | 32.8771
2018-02-16 21:00 | 86.3767 | 86.7247 | 0 | 32.9554
2018-02-16 22:00 | 86.3691 | 86.7659 | 0 | 32.971
2018-02-16 23:00 | 86.4012 | 86.7918 | 0 | 32.9809
2018-02-17 | 86.0121 | 0 | 86.5507 | 32.8893
2018-02-17 01:00 | 85.919 | 0 | 86.5324 | 32.8823
2018-02-17 02:00 | 86.0533 | 0 | 86.6453 | 32.9252
2018-02-17 03:00 | 86.1677 | 0 | 86.7002 | 32.9461
2018-02-17 04:00 | 86.3081 | 0 | 86.8513 | 33.0035
2018-02-17 05:00 | 86.2562 | 0 | 86.8605 | 33.007
2018-02-17 06:00 | 86.1234 | 0 | 86.6682 | 32.9339
2018-02-17 07:00 | 86.1906 | 0 | 86.7247 | 32.9554
2018-02-17 08:00 | 86.36 | 0 | 86.952 | 33.0418
2018-02-17 09:00 | 86.4912 | 0 | 87.0588 | 33.0823
2018-02-17 10:00 | 86.1982 | 0 | 86.6392 | 32.9229
2018-02-17 11:00 | 86.1707 | 0 | 86.8849 | 33.0163
2018-02-17 12:00 | 86.5019 | 0 | 87.1504 | 33.1172
2018-02-17 13:00 | 86.6148 | 0 | 87.3167 | 33.1803
2018-02-17 14:00 | 86.4439 | 0 | 87.0832 | 33.0916
2018-02-17 15:00 | 86.5522 | 0 | 87.2938 | 33.1716
2018-02-17 16:00 | 86.5644 | 0 | 87.3579 | 33.196
2018-02-17 17:00 | 86.7445 | 0 | 87.57 | 33.2766
2018-02-17 18:00 | 86.4668 | 0 | 87.3014 | 33.1745
2018-02-17 19:00 | 86.3661 | 0 | 87.0954 | 33.0963
2018-02-17 20:00 | 86.1173 | 0 | 86.891 | 33.0186
2018-02-17 21:00 | 86.1555 | 0 | 86.9245 | 33.0313
2018-02-17 22:00 | 86.2211 | 0 | 87.0054 | 33.0621
2018-02-17 23:00 | 86.2226 | 0 | 87.0787 | 33.0899
2018-02-18 | 86.2364 | 86.7994 | 0 | 32.9838
2018-02-18 01:00 | 86.3188 | 86.952 | 0 | 33.0418
2018-02-18 02:00 | 86.2119 | 86.8177 | 0 | 32.9907
2018-02-18 03:00 | 86.1845 | 86.7857 | 0 | 32.9786
2018-02-18 04:00 | 86.2455 | 86.833 | 0 | 32.9965
2018-02-18 05:00 | 86.2333 | 86.833 | 0 | 32.9965
2018-02-18 06:00 | 86.2776 | 86.8528 | 0 | 33.0041
2018-02-18 07:00 | 86.2867 | 86.8452 | 0 | 33.0012
2018-02-18 08:00 | 86.2989 | 86.9032 | 0 | 33.0232
2018-02-18 09:00 | 86.2867 | 86.8162 | 0 | 32.9902
2018-02-18 10:00 | 86.2882 | 86.8528 | 0 | 33.0041
2018-02-18 11:00 | 86.1845 | 86.743 | 0 | 32.9623
2018-02-18 12:00 | 86.1418 | 86.714 | 0 | 32.9513
2018-02-18 13:00 | 86.1479 | 86.7659 | 0 | 32.971
2018-02-18 14:00 | 86.1112 | 86.7018 | 0 | 32.9467
2018-02-18 15:00 | 86.2455 | 86.8482 | 0 | 33.0023
2018-02-18 16:00 | 86.3447 | 86.9398 | 0 | 33.0371
2018-02-18 17:00 | 86.4805 | 86.9856 | 0 | 33.0545
2018-02-18 18:00 | 86.4332 | 86.92 | 0 | 33.0296
2018-02-18 19:00 | 85.6794 | 85.9266 | 0 | 32.6521
2018-02-18 20:00 | 86.3294 | 86.5888 | 0 | 32.9037
2018-02-18 21:00 | 86.3569 | 86.6728 | 0 | 32.9357
2018-02-18 22:00 | 86.4881 | 86.8086 | 0 | 32.9873
2018-02-18 23:00 | 86.4332 | 86.7353 | 0 | 32.9594
2018-02-19 | 86.4088 | 86.7002 | 86.9352 | 65.9815
2018-02-19 01:00 | 86.0426 | 86.3127 | 86.5278 | 65.6794
2018-02-19 02:00 | 86.392 | 86.6392 | 86.8421 | 65.9229
2018-02-19 03:00 | 86.2776 | 86.5766 | 86.7536 | 65.8655
2018-02-19 04:00 | 86.5034 | 86.8849 | 87.0283 | 66.087
2018-02-19 05:00 | 86.3661 | 86.772 | 87.0054 | 66.0354
2018-02-19 06:00 | 86.2898 | 86.6499 | 86.8147 | 65.9165
2018-02-19 07:00 | 86.2043 | 86.5278 | 86.7079 | 65.8296
2018-02-19 08:00 | 86.3355 | 86.5461 | 86.8025 | 65.8725
2018-02-19 09:00 | 86.3798 | 86.7262 | 86.8711 | 65.967
2018-02-19 10:00 | 86.2272 | 86.5156 | 86.714 | 65.8272
2018-02-19 11:00 | 86.2119 | 86.5141 | 86.7201 | 65.829
2018-02-19 12:00 | 86.389 | 86.6835 | 86.8574 | 65.9455
2018-02-19 13:00 | 86.4027 | 86.6224 | 86.7475 | 65.8806
2018-02-19 14:00 | 86.3783 | 86.6606 | 86.7903 | 65.9113
2018-02-19 15:00 | 86.3355 | 86.5248 | 86.7384 | 65.84
2018-02-19 16:00 | 86.3493 | 86.4912 | 86.685 | 65.807
2018-02-19 17:00 | 86.244 | 86.4683 | 86.6743 | 65.7942
2018-02-19 18:00 | 86.3142 | 86.4378 | 86.5934 | 65.7519
2018-02-19 19:00 | 86.2089 | 86.3508 | 86.5583 | 65.7055
2018-02-19 20:00 | 86.2181 | 86.4836 | 86.6896 | 65.8058
2018-02-19 21:00 | 86.1494 | 86.4759 | 86.63 | 65.7802
2018-02-19 22:00 | 86.2593 | 86.5522 | 86.6468 | 65.8156
2018-02-19 23:00 | 86.4424 | 86.8055 | 86.8864 | 66.0029
2018-02-20 | 86.4637 | 0 | 0 | 0
2018-02-20 01:00 | 86.5629 | 0 | 0 | 0
2018-02-20 02:00 | 86.3706 | 0 | 0 | 0
2018-02-20 03:00 | 86.3523 | 0 | 0 | 0
2018-02-20 04:00 | 86.3676 | 0 | 0 | 0
2018-02-20 05:00 | 86.4027 | 0 | 0 | 0
2018-02-20 06:00 | 86.4652 | 0 | 0 | 0
2018-02-20 07:00 | 86.4012 | 0 | 0 | 0
2018-02-20 08:00 | 86.4515 | 0 | 0 | 0
2018-02-20 09:00 | 86.2028 | 0 | 0 | 0
2018-02-20 10:00 | 86.2715 | 0 | 0 | 0
2018-02-20 11:00 | 86.7567 | 0 | 0 | 0
2018-02-20 12:00 | 86.6194 | 0 | 0 | 0
2018-02-20 13:00 | 86.6377 | 0 | 0 | 0
2018-02-20 14:00 | 86.8757 | 0 | 0 | 0
2018-02-20 15:00 | 86.7994 | 0 | 0 | 0
2018-02-20 16:00 | 86.7674 | 0 | 0 | 0
2018-02-20 17:00 | 86.7384 | 0 | 0 | 0
2018-02-20 18:00 | 86.7124 | 0 | 0 | 0
2018-02-20 19:00 | 86.8376 | 0 | 0 | 0
2018-02-20 20:00 | 86.627 | 0 | 0 | 0
2018-02-20 21:00 | 86.6239 | 0 | 0 | 0
2018-02-20 22:00 | 86.714 | 0 | 0 | 0
2018-02-20 23:00 | 86.8971 | 0 | 0 | 0
2018-02-21 | 0 | 0 | 86.6712 | 32.9351
2018-02-21 01:00 | 0 | 0 | 86.511 | 32.8742
2018-02-21 02:00 | 0 | 0 | 86.7628 | 32.9699
2018-02-21 03:00 | 0 | 0 | 86.7384 | 32.9606
2018-02-21 04:00 | 0 | 0 | 86.8376 | 32.9983
2018-02-21 05:00 | 0 | 0 | 87.0222 | 33.0684
2018-02-21 06:00 | 0 | 0 | 86.9627 | 33.0458
2018-02-21 07:00 | 0 | 0 | 87.1321 | 33.1102
2018-02-21 08:00 | 0 | 0 | 87.1931 | 33.1334
2018-02-21 09:00 | 0 | 0 | 86.7155 | 32.9519
2018-02-21 10:00 | 0 | 0 | 86.6743 | 32.9362
2018-02-21 11:00 | 0 | 0 | 86.8956 | 33.0203
2018-02-21 12:00 | 0 | 0 | 86.9276 | 33.0325
2018-02-21 13:00 | 0 | 0 | 87.2541 | 33.1566
2018-02-21 14:00 | 0 | 0 | 87.4037 | 33.2134
2018-02-21 15:00 | 0 | 0 | 87.2129 | 33.1409
2018-02-21 16:00 | 0 | 0 | 86.9718 | 33.0493
2018-02-21 17:00 | 0 | 0 | 87.1397 | 33.1131
2018-02-21 18:00 | 0 | 0 | 87.2435 | 33.1525
2018-02-21 19:00 | 0 | 0 | 86.8894 | 33.018
2018-02-21 20:00 | 0 | 0 | 87.1839 | 33.1299
2018-02-21 21:00 | 0 | 0 | 87.2419 | 33.1519
2018-02-21 22:00 | 0 | 0 | 87.1733 | 33.1259
2018-02-21 23:00 | 0 | 0 | 87.2557 | 33.1572
2018-02-22 | 86.5492 | 0 | 0 | 0
2018-02-22 01:00 | 86.7201 | 0 | 0 | 0
2018-02-22 02:00 | 86.5095 | 0 | 0 | 0
2018-02-22 03:00 | 86.4576 | 0 | 0 | 0
2018-02-22 04:00 | 86.6316 | 0 | 0 | 0
2018-02-22 05:00 | 86.569 | 0 | 0 | 0
2018-02-22 06:00 | 86.6468 | 0 | 0 | 0
2018-02-22 07:00 | 86.6361 | 0 | 0 | 0
2018-02-22 08:00 | 86.6819 | 0 | 0 | 0
2018-02-22 09:00 | 86.7094 | 0 | 0 | 0
2018-02-22 10:00 | 86.7933 | 0 | 0 | 0
2018-02-22 11:00 | 86.8009 | 0 | 0 | 0
2018-02-22 12:00 | 86.6728 | 0 | 0 | 0
2018-02-22 13:00 | 86.6316 | 0 | 0 | 0
2018-02-22 14:00 | 86.6316 | 0 | 0 | 0
2018-02-22 15:00 | 86.6636 | 0 | 0 | 0
2018-02-22 16:00 | 86.5568 | 0 | 0 | 0
2018-02-22 17:00 | 86.6865 | 0 | 0 | 0
2018-02-22 18:00 | 86.7262 | 0 | 0 | 0
2018-02-22 19:00 | 86.5187 | 0 | 0 | 0
2018-02-22 20:00 | 86.5766 | 0 | 0 | 0
2018-02-22 21:00 | 86.6194 | 0 | 0 | 0
2018-02-22 22:00 | 86.6743 | 0 | 0 | 0
2018-02-22 23:00 | 86.5644 | 0 | 0 | 0
2018-02-23 | 86.2226 | 86.688 | 0 | 32.9414
2018-02-23 01:00 | 86.1128 | 86.5232 | 0 | 32.8788
2018-02-23 02:00 | 86.2791 | 86.6896 | 0 | 32.942
2018-02-23 03:00 | 86.0014 | 86.4485 | 0 | 32.8504
2018-02-23 04:00 | 86.0533 | 86.4347 | 0 | 32.8452
2018-02-23 05:00 | 86.2257 | 86.6117 | 0 | 32.9124
2018-02-23 06:00 | 86.4332 | 86.9352 | 0 | 33.0354
2018-02-23 07:00 | 86.5873 | 87.0619 | 0 | 33.0835
2018-02-23 08:00 | 86.3691 | 86.7811 | 0 | 32.9768
2018-02-23 09:00 | 86.334 | 86.7399 | 0 | 32.9612
2018-02-23 10:00 | 86.5126 | 86.862 | 0 | 33.0076
2018-02-23 11:00 | 86.5003 | 86.9306 | 0 | 33.0336
2018-02-23 12:00 | 86.7002 | 87.1412 | 0 | 33.1137
2018-02-23 13:00 | 86.363 | 86.8009 | 0 | 32.9843
2018-02-23 14:00 | 86.4408 | 86.8635 | 0 | 33.0081
2018-02-23 15:00 | 86.2943 | 86.6743 | 0 | 32.9362
2018-02-23 16:00 | 86.3706 | 86.7491 | 0 | 32.9647
2018-02-23 17:00 | 86.2882 | 86.7445 | 0 | 32.9629
2018-02-23 18:00 | 86.1875 | 86.6667 | 0 | 32.9333
2018-02-23 19:00 | 86.099 | 86.5431 | 0 | 32.8864
2018-02-23 20:00 | 86.1997 | 86.5187 | 0 | 32.8771
2018-02-23 21:00 | 86.3767 | 86.7247 | 0 | 32.9554
2018-02-23 22:00 | 86.3691 | 86.7659 | 0 | 32.971
2018-02-23 23:00 | 86.4012 | 86.7918 | 0 | 32.9809
2018-02-24 | 86.0121 | 0 | 86.5507 | 32.8893
2018-02-24 01:00 | 85.919 | 0 | 86.5324 | 32.8823
2018-02-24 02:00 | 86.0533 | 0 | 86.6453 | 32.9252
2018-02-24 03:00 | 86.1677 | 0 | 86.7002 | 32.9461
2018-02-24 04:00 | 86.3081 | 0 | 86.8513 | 33.0035
2018-02-24 05:00 | 86.2562 | 0 | 86.8605 | 33.007
2018-02-24 06:00 | 86.1234 | 0 | 86.6682 | 32.9339
2018-02-24 07:00 | 86.1906 | 0 | 86.7247 | 32.9554
2018-02-24 08:00 | 86.36 | 0 | 86.952 | 33.0418
2018-02-24 09:00 | 86.4912 | 0 | 87.0588 | 33.0823
2018-02-24 10:00 | 86.1982 | 0 | 86.6392 | 32.9229
2018-02-24 11:00 | 86.1707 | 0 | 86.8849 | 33.0163
2018-02-24 12:00 | 86.5019 | 0 | 87.1504 | 33.1172
2018-02-24 13:00 | 86.6148 | 0 | 87.3167 | 33.1803
2018-02-24 14:00 | 86.4439 | 0 | 87.0832 | 33.0916
2018-02-24 15:00 | 86.5522 | 0 | 87.2938 | 33.1716
2018-02-24 16:00 | 86.5644 | 0 | 87.3579 | 33.196
2018-02-24 17:00 | 86.7445 | 0 | 87.57 | 33.2766
2018-02-24 18:00 | 86.4668 | 0 | 87.3014 | 33.1745
2018-02-24 19:00 | 86.3661 | 0 | 87.0954 | 33.0963
2018-02-24 20:00 | 86.1173 | 0 | 86.891 | 33.0186
2018-02-24 21:00 | 86.1555 | 0 | 86.9245 | 33.0313
2018-02-24 22:00 | 86.2211 | 0 | 87.0054 | 33.0621
2018-02-24 23:00 | 86.2226 | 0 | 87.0787 | 33.0899
2018-02-25 | 86.2364 | 86.7994 | 0 | 32.9838
2018-02-25 01:00 | 86.3188 | 86.952 | 0 | 33.0418
2018-02-25 02:00 | 86.2119 | 86.8177 | 0 | 32.9907
2018-02-25 03:00 | 86.1845 | 86.7857 | 0 | 32.9786
2018-02-25 04:00 | 86.2455 | 86.833 | 0 | 32.9965
2018-02-25 05:00 | 86.2333 | 86.833 | 0 | 32.9965
2018-02-25 06:00 | 86.2776 | 86.8528 | 0 | 33.0041
2018-02-25 07:00 | 86.2867 | 86.8452 | 0 | 33.0012
2018-02-25 08:00 | 86.2989 | 86.9032 | 0 | 33.0232
2018-02-25 09:00 | 86.2867 | 86.8162 | 0 | 32.9902
2018-02-25 10:00 | 86.2882 | 86.8528 | 0 | 33.0041
2018-02-25 11:00 | 86.1845 | 86.743 | 0 | 32.9623
2018-02-25 12:00 | 86.1418 | 86.714 | 0 | 32.9513
2018-02-25 13:00 | 86.1479 | 86.7659 | 0 | 32.971
2018-02-25 14:00 | 86.1112 | 86.7018 | 0 | 32.9467
2018-02-25 15:00 | 86.2455 | 86.8482 | 0 | 33.0023
2018-02-25 16:00 | 86.3447 | 86.9398 | 0 | 33.0371
2018-02-25 17:00 | 86.4805 | 86.9856 | 0 | 33.0545
2018-02-25 18:00 | 86.4332 | 86.92 | 0 | 33.0296
2018-02-25 19:00 | 85.6794 | 85.9266 | 0 | 32.6521
2018-02-25 20:00 | 86.3294 | 86.5888 | 0 | 32.9037
2018-02-25 21:00 | 86.3569 | 86.6728 | 0 | 32.9357
2018-02-25 22:00 | 86.4881 | 86.8086 | 0 | 32.9873
2018-02-25 23:00 | 86.4332 | 86.7353 | 0 | 32.9594
2018-02-26 | 86.4088 | 86.7002 | 86.9352 | 65.9815
2018-02-26 01:00 | 86.0426 | 86.3127 | 86.5278 | 65.6794
2018-02-26 02:00 | 86.392 | 86.6392 | 86.8421 | 65.9229
2018-02-26 03:00 | 86.2776 | 86.5766 | 86.7536 | 65.8655
2018-02-26 04:00 | 86.5034 | 86.8849 | 87.0283 | 66.087
2018-02-26 05:00 | 86.3661 | 86.772 | 87.0054 | 66.0354
2018-02-26 06:00 | 86.2898 | 86.6499 | 86.8147 | 65.9165
2018-02-26 07:00 | 86.2043 | 86.5278 | 86.7079 | 65.8296
2018-02-26 08:00 | 86.3355 | 86.5461 | 86.8025 | 65.8725
2018-02-26 09:00 | 86.3798 | 86.7262 | 86.8711 | 65.967
2018-02-26 10:00 | 86.2272 | 86.5156 | 86.714 | 65.8272
2018-02-26 11:00 | 86.2119 | 86.5141 | 86.7201 | 65.829
2018-02-26 12:00 | 86.389 | 86.6835 | 86.8574 | 65.9455
2018-02-26 13:00 | 86.4027 | 86.6224 | 86.7475 | 65.8806
2018-02-26 14:00 | 86.3783 | 86.6606 | 86.7903 | 65.9113
2018-02-26 15:00 | 86.3355 | 86.5248 | 86.7384 | 65.84
2018-02-26 16:00 | 86.3493 | 86.4912 | 86.685 | 65.807
2018-02-26 17:00 | 86.244 | 86.4683 | 86.6743 | 65.7942
2018-02-26 18:00 | 86.3142 | 86.4378 | 86.5934 | 65.7519
2018-02-26 19:00 | 86.2089 | 86.3508 | 86.5583 | 65.7055
2018-02-26 20:00 | 86.2181 | 86.4836 | 86.6896 | 65.8058
2018-02-26 21:00 | 86.1494 | 86.4759 | 86.63 | 65.7802
2018-02-26 22:00 | 86.2593 | 86.5522 | 86.6468 | 65.8156
2018-02-26 23:00 | 86.4424 | 86.8055 | 86.8864 | 66.0029
2018-02-27 | 86.4637 | 0 | 0 | 0
2018-02-27 01:00 | 86.5629 | 0 | 0 | 0
2018-02-27 02:00 | 86.3706 | 0 | 0 | 0
2018-02-27 03:00 | 86.3523 | 0 | 0 | 0
2018-02-27 04:00 | 86.3676 | 0 | 0 | 0
2018-02-27 05:00 | 86.4027 | 0 | 0 | 0
2018-02-27 06:00 | 86.4652 | 0 | 0 | 0
2018-02-27 07:00 | 86.4012 | 0 | 0 | 0
2018-02-27 08:00 | 86.4515 | 0 | 0 | 0
2018-02-27 09:00 | 86.2028 | 0 | 0 | 0
2018-02-27 10:00 | 86.2715 | 0 | 0 | 0
2018-02-27 11:00 | 86.7567 | 0 | 0 | 0
2018-02-27 12:00 | 86.6194 | 0 | 0 | 0
2018-02-27 13:00 | 86.6377 | 0 | 0 | 0
2018-02-27 14:00 | 86.8757 | 0 | 0 | 0
2018-02-27 15:00 | 86.7994 | 0 | 0 | 0
2018-02-27 16:00 | 86.7674 | 0 | 0 | 0
2018-02-27 17:00 | 86.7384 | 0 | 0 | 0
2018-02-27 18:00 | 86.7124 | 0 | 0 | 0
2018-02-27 19:00 | 86.8376 | 0 | 0 | 0
2018-02-27 20:00 | 86.627 | 0 | 0 | 0
2018-02-27 21:00 | 86.6239 | 0 | 0 | 0
2018-02-27 22:00 | 86.714 | 0 | 0 | 0
2018-02-27 23:00 | 86.8971 | 0 | 0 | 0
2018-02-28 | 0 | 0 | 86.6712 | 32.9351
2018-02-28 01:00 | 0 | 0 | 86.511 | 32.8742
2018-02-28 02:00 | 0 | 0 | 86.7628 | 32.9699
2018-02-28 03:00 | 0 | 0 | 86.7384 | 32.9606
2018-02-28 04:00 | 0 | 0 | 86.8376 | 32.9983
2018-02-28 05:00 | 0 | 0 | 87.0222 | 33.0684
2018-02-28 06:00 | 0 | 0 | 86.9627 | 33.0458
2018-02-28 07:00 | 0 | 0 | 87.1321 | 33.1102
2018-02-28 08:00 | 0 | 0 | 87.1931 | 33.1334
2018-02-28 09:00 | 0 | 0 | 86.7155 | 32.9519
2018-02-28 10:00 | 0 | 0 | 86.6743 | 32.9362
2018-02-28 11:00 | 0 | 0 | 86.8956 | 33.0203
2018-02-28 12:00 | 0 | 0 | 86.9276 | 33.0325
2018-02-28 13:00 | 0 | 0 | 87.2541 | 33.1566
2018-02-28 14:00 | 0 | 0 | 87.4037 | 33.2134
2018-02-28 15:00 | 0 | 0 | 87.2129 | 33.1409
2018-02-28 16:00 | 0 | 0 | 86.9718 | 33.0493
2018-02-28 17:00 | 0 | 0 | 87.1397 | 33.1131
2018-02-28 18:00 | 0 | 0 | 87.2435 | 33.1525
2018-02-28 19:00 | 0 | 0 | 86.8894 | 33.018
2018-02-28 20:00 | 0 | 0 | 87.1839 | 33.1299
2018-02-28 21:00 | 0 | 0 | 87.2419 | 33.1519
2018-02-28 22:00 | 0 | 0 | 87.1733 | 33.1259
2018-02-28 23:00 | 0 | 0 | 87.2557 | 33.1572
2018-03-01 | 86.5492 | 0 | 0 | 0
2018-03-01 01:00 | 86.7201 | 0 | 0 | 0
2018-03-01 02:00 | 86.5095 | 0 | 0 | 0
2018-03-01 03:00 | 86.4576 | 0 | 0 | 0
2018-03-01 04:00 | 86.6316 | 0 | 0 | 0
2018-03-01 05:00 | 86.569 | 0 | 0 | 0
2018-03-01 06:00 | 86.6468 | 0 | 0 | 0
2018-03-01 07:00 | 86.6361 | 0 | 0 | 0
2018-03-01 08:00 | 86.6819 | 0 | 0 | 0
2018-03-01 09:00 | 86.7094 | 0 | 0 | 0
2018-03-01 10:00 | 86.7933 | 0 | 0 | 0
2018-03-01 11:00 | 86.8009 | 0 | 0 | 0
2018-03-01 12:00 | 86.6728 | 0 | 0 | 0
2018-03-01 13:00 | 86.6316 | 0 | 0 | 0
2018-03-01 14:00 | 86.6316 | 0 | 0 | 0
2018-03-01 15:00 | 86.6636 | 0 | 0 | 0
2018-03-01 16:00 | 86.5568 | 0 | 0 | 0
2018-03-01 17:00 | 86.6865 | 0 | 0 | 0
2018-03-01 18:00 | 86.7262 | 0 | 0 | 0
2018-03-01 19:00 | 86.5187 | 0 | 0 | 0
2018-03-01 20:00 | 86.5766 | 0 | 0 | 0
2018-03-01 21:00 | 86.6194 | 0 | 0 | 0
2018-03-01 22:00 | 86.6743 | 0 | 0 | 0
2018-03-01 23:00 | 86.5644 | 0 | 0 | 0
2018-03-02 | 86.2226 | 86.688 | 0 | 32.9414
2018-03-02 01:00 | 86.1128 | 86.5232 | 0 | 32.8788
2018-03-02 02:00 | 86.2791 | 86.6896 | 0 | 32.942
2018-03-02 03:00 | 86.0014 | 86.4485 | 0 | 32.8504
2018-03-02 04:00 | 86.0533 | 86.4347 | 0 | 32.8452
2018-03-02 05:00 | 86.2257 | 86.6117 | 0 | 32.9124
2018-03-02 06:00 | 86.4332 | 86.9352 | 0 | 33.0354
2018-03-02 07:00 | 86.5873 | 87.0619 | 0 | 33.0835
2018-03-02 08:00 | 86.3691 | 86.7811 | 0 | 32.9768
2018-03-02 09:00 | 86.334 | 86.7399 | 0 | 32.9612
2018-03-02 10:00 | 86.5126 | 86.862 | 0 | 33.0076
2018-03-02 11:00 | 86.5003 | 86.9306 | 0 | 33.0336
2018-03-02 12:00 | 86.7002 | 87.1412 | 0 | 33.1137
2018-03-02 13:00 | 86.363 | 86.8009 | 0 | 32.9843
2018-03-02 14:00 | 86.4408 | 86.8635 | 0 | 33.0081
2018-03-02 15:00 | 86.2943 | 86.6743 | 0 | 32.9362
2018-03-02 16:00 | 86.3706 | 86.7491 | 0 | 32.9647
2018-03-02 17:00 | 86.2882 | 86.7445 | 0 | 32.9629
2018-03-02 18:00 | 86.1875 | 86.6667 | 0 | 32.9333
2018-03-02 19:00 | 86.099 | 86.5431 | 0 | 32.8864
2018-03-02 20:00 | 86.1997 | 86.5187 | 0 | 32.8771
2018-03-02 21:00 | 86.3767 | 86.7247 | 0 | 32.9554
2018-03-02 22:00 | 86.3691 | 86.7659 | 0 | 32.971
2018-03-02 23:00 | 86.4012 | 86.7918 | 0 | 32.9809
2018-03-03 | 86.0121 | 0 | 86.5507 | 32.8893
2018-03-03 01:00 | 85.919 | 0 | 86.5324 | 32.8823
2018-03-03 02:00 | 86.0533 | 0 | 86.6453 | 32.9252
2018-03-03 03:00 | 86.1677 | 0 | 86.7002 | 32.9461
2018-03-03 04:00 | 86.3081 | 0 | 86.8513 | 33.0035
2018-03-03 05:00 | 86.2562 | 0 | 86.8605 | 33.007
2018-03-03 06:00 | 86.1234 | 0 | 86.6682 | 32.9339
2018-03-03 07:00 | 86.1906 | 0 | 86.7247 | 32.9554
2018-03-03 08:00 | 86.36 | 0 | 86.952 | 33.0418
2018-03-03 09:00 | 86.4912 | 0 | 87.0588 | 33.0823
2018-03-03 10:00 | 86.1982 | 0 | 86.6392 | 32.9229
2018-03-03 11:00 | 86.1707 | 0 | 86.8849 | 33.0163
2018-03-03 12:00 | 86.5019 | 0 | 87.1504 | 33.1172
2018-03-03 13:00 | 86.6148 | 0 | 87.3167 | 33.1803
2018-03-03 14:00 | 86.4439 | 0 | 87.0832 | 33.0916
2018-03-03 15:00 | 86.5522 | 0 | 87.2938 | 33.1716
2018-03-03 16:00 | 86.5644 | 0 | 87.3579 | 33.196
2018-03-03 17:00 | 86.7445 | 0 | 87.57 | 33.2766
2018-03-03 18:00 | 86.4668 | 0 | 87.3014 | 33.1745
2018-03-03 19:00 | 86.3661 | 0 | 87.0954 | 33.0963
2018-03-03 20:00 | 86.1173 | 0 | 86.891 | 33.0186
2018-03-03 21:00 | 86.1555 | 0 | 86.9245 | 33.0313
2018-03-03 22:00 | 86.2211 | 0 | 87.0054 | 33.0621
2018-03-03 23:00 | 86.2226 | 0 | 87.0787 | 33.0899
2018-03-04 | 86.2364 | 86.7994 | 0 | 32.9838
2018-03-04 01:00 | 86.3188 | 86.952 | 0 | 33.0418
2018-03-04 02:00 | 86.2119 | 86.8177 | 0 | 32.9907
2018-03-04 03:00 | 86.1845 | 86.7857 | 0 | 32.9786
2018-03-04 04:00 | 86.2455 | 86.833 | 0 | 32.9965
2018-03-04 05:00 | 86.2333 | 86.833 | 0 | 32.9965
2018-03-04 06:00 | 86.2776 | 86.8528 | 0 | 33.0041
2018-03-04 07:00 | 86.2867 | 86.8452 | 0 | 33.0012
2018-03-04 08:00 | 86.2989 | 86.9032 | 0 | 33.0232
2018-03-04 09:00 | 86.2867 | 86.8162 | 0 | 32.9902
2018-03-04 10:00 | 86.2882 | 86.8528 | 0 | 33.0041
2018-03-04 11:00 | 86.1845 | 86.743 | 0 | 32.9623
2018-03-04 12:00 | 86.1418 | 86.714 | 0 | 32.9513
2018-03-04 13:00 | 86.1479 | 86.7659 | 0 | 32.971
2018-03-04 14:00 | 86.1112 | 86.7018 | 0 | 32.9467
2018-03-04 15:00 | 86.2455 | 86.8482 | 0 | 33.0023
2018-03-04 16:00 | 86.3447 | 86.9398 | 0 | 33.0371
2018-03-04 17:00 | 86.4805 | 86.9856 | 0 | 33.0545
2018-03-04 18:00 | 86.4332 | 86.92 | 0 | 33.0296
2018-03-04 19:00 | 85.6794 | 85.9266 | 0 | 32.6521
2018-03-04 20:00 | 86.3294 | 86.5888 | 0 | 32.9037
2018-03-04 21:00 | 86.3569 | 86.6728 | 0 | 32.9357
2018-03-04 22:00 | 86.4881 | 86.8086 | 0 | 32.9873
2018-03-04 23:00 | 86.4332 | 86.7353 | 0 | 32.9594
2018-03-05 | 86.4088 | 86.7002 | 86.9352 | 65.9815
2018-03-05 01:00 | 86.0426 | 86.3127 | 86.5278 | 65.6794
2018-03-05 02:00 | 86.392 | 86.6392 | 86.8421 | 65.9229
2018-03-05 03:00 | 86.2776 | 86.5766 | 86.7536 | 65.8655
2018-03-05 04:00 | 86.5034 | 86.8849 | 87.0283 | 66.087
2018-03-05 05:00 | 86.3661 | 86.772 | 87.0054 | 66.0354
2018-03-05 06:00 | 86.2898 | 86.6499 | 86.8147 | 65.9165
2018-03-05 07:00 | 86.2043 | 86.5278 | 86.7079 | 65.8296
2018-03-05 08:00 | 86.3355 | 86.5461 | 86.8025 | 65.8725
2018-03-05 09:00 | 86.3798 | 86.7262 | 86.8711 | 65.967
2018-03-05 10:00 | 86.2272 | 86.5156 | 86.714 | 65.8272
2018-03-05 11:00 | 86.2119 | 86.5141 | 86.7201 | 65.829
2018-03-05 12:00 | 86.389 | 86.6835 | 86.8574 | 65.9455
2018-03-05 13:00 | 86.4027 | 86.6224 | 86.7475 | 65.8806
2018-03-05 14:00 | 86.3783 | 86.6606 | 86.7903 | 65.9113
2018-03-05 15:00 | 86.3355 | 86.5248 | 86.7384 | 65.84
2018-03-05 16:00 | 86.3493 | 86.4912 | 86.685 | 65.807
2018-03-05 17:00 | 86.244 | 86.4683 | 86.6743 | 65.7942
2018-03-05 18:00 | 86.3142 | 86.4378 | 86.5934 | 65.7519
2018-03-05 19:00 | 86.2089 | 86.3508 | 86.5583 | 65.7055
2018-03-05 20:00 | 86.2181 | 86.4836 | 86.6896 | 65.8058
2018-03-05 21:00 | 86.1494 | 86.4759 | 86.63 | 65.7802
2018-03-05 22:00 | 86.2593 | 86.5522 | 86.6468 | 65.8156
2018-03-05 23:00 | 86.4424 | 86.8055 | 86.8864 | 66.0029
2018-03-06 | 86.4637 | 0 | 0 | 0
2018-03-06 01:00 | 86.5629 | 0 | 0 | 0
2018-03-06 02:00 | 86.3706 | 0 | 0 | 0
2018-03-06 03:00 | 86.3523 | 0 | 0 | 0
2018-03-06 04:00 | 86.3676 | 0 | 0 | 0
2018-03-06 05:00 | 86.4027 | 0 | 0 | 0
2018-03-06 06:00 | 86.4652 | 0 | 0 | 0
2018-03-06 07:00 | 86.4012 | 0 | 0 | 0
2018-03-06 08:00 | 86.4515 | 0 | 0 | 0
2018-03-06 09:00 | 86.2028 | 0 | 0 | 0
2018-03-06 10:00 | 86.2715 | 0 | 0 | 0
2018-03-06 11:00 | 86.7567 | 0 | 0 | 0
2018-03-06 12:00 | 86.6194 | 0 | 0 | 0
2018-03-06 13:00 | 86.6377 | 0 | 0 | 0
2018-03-06 14:00 | 86.8757 | 0 | 0 | 0
2018-03-06 15:00 | 86.7994 | 0 | 0 | 0
2018-03-06 16:00 | 86.7674 | 0 | 0 | 0
2018-03-06 17:00 | 86.7384 | 0 | 0 | 0
2018-03-06 18:00 | 86.7124 | 0 | 0 | 0
2018-03-06 19:00 | 86.8376 | 0 | 0 | 0
2018-03-06 20:00 | 86.627 | 0 | 0 | 0
2018-03-06 21:00 | 86.6239 | 0 | 0 | 0
2018-03-06 22:00 | 86.714 | 0 | 0 | 0
2018-03-06 23:00 | 86.8971 | 0 | 0 | 0
2018-03-07 | 0 | 0 | 86.6712 | 32.9351
2018-03-07 01:00 | 0 | 0 | 86.511 | 32.8742
2018-03-07 02:00 | 0 | 0 | 86.7628 | 32.9699
2018-03-07 03:00 | 0 | 0 | 86.7384 | 32.9606
2018-03-07 04:00 | 0 | 0 | 86.8376 | 32.9983
2018-03-07 05:00 | 0 | 0 | 87.0222 | 33.0684
2018-03-07 06:00 | 0 | 0 | 86.9627 | 33.0458
2018-03-07 07:00 | 0 | 0 | 87.1321 | 33.1102
2018-03-07 08:00 | 0 | 0 | 87.1931 | 33.1334
2018-03-07 09:00 | 0 | 0 | 86.7155 | 32.9519
2018-03-07 10:00 | 0 | 0 | 86.6743 | 32.9362
2018-03-07 11:00 | 0 | 0 | 86.8956 | 33.0203
2018-03-07 12:00 | 0 | 0 | 86.9276 | 33.0325
2018-03-07 13:00 | 0 | 0 | 87.2541 | 33.1566
2018-03-07 14:00 | 0 | 0 | 87.4037 | 33.2134
2018-03-07 15:00 | 0 | 0 | 87.2129 | 33.1409
2018-03-07 16:00 | 0 | 0 | 86.9718 | 33.0493
2018-03-07 17:00 | 0 | 0 | 87.1397 | 33.1131
2018-03-07 18:00 | 0 | 0 | 87.2435 | 33.1525
2018-03-07 19:00 | 0 | 0 | 86.8894 | 33.018
2018-03-07 20:00 | 0 | 0 | 87.1839 | 33.1299
2018-03-07 21:00 | 0 | 0 | 87.2419 | 33.1519
2018-03-07 22:00 | 0 | 0 | 87.1733 | 33.1259
2018-03-07 23:00 | 0 | 0 | 87.2557 | 33.1572
2018-03-08 | 86.5492 | 0 | 0 | 0
2018-03-08 01:00 | 86.7201 | 0 | 0 | 0
2018-03-08 02:00 | 86.5095 | 0 | 0 | 0
2018-03-08 03:00 | 86.4576 | 0 | 0 | 0
2018-03-08 04:00 | 86.6316 | 0 | 0 | 0
2018-03-08 05:00 | 86.569 | 0 | 0 | 0
2018-03-08 06:00 | 86.6468 | 0 | 0 | 0
2018-03-08 07:00 | 86.6361 | 0 | 0 | 0
2018-03-08 08:00 | 86.6819 | 0 | 0 | 0
2018-03-08 09:00 | 86.7094 | 0 | 0 | 0
2018-03-08 10:00 | 86.7933 | 0 | 0 | 0
2018-03-08 11:00 | 86.8009 | 0 | 0 | 0
2018-03-08 12:00 | 86.6728 | 0 | 0 | 0
2018-03-08 13:00 | 86.6316 | 0 | 0 | 0
2018-03-08 14:00 | 86.6316 | 0 | 0 | 0
2018-03-08 15:00 | 86.6636 | 0 | 0 | 0
2018-03-08 16:00 | 86.5568 | 0 | 0 | 0
2018-03-08 17:00 | 86.6865 | 0 | 0 | 0
2018-03-08 18:00 | 86.7262 | 0 | 0 | 0
2018-03-08 19:00 | 86.5187 | 0 | 0 | 0
2018-03-08 20:00 | 86.5766 | 0 | 0 | 0
2018-03-08 21:00 | 86.6194 | 0 | 0 | 0
2018-03-08 22:00 | 86.6743 | 0 | 0 | 0
2018-03-08 23:00 | 86.5644 | 0 | 0 | 0
2018-03-09 | 86.2226 | 86.688 | 0 | 32.9414
2018-03-09 01:00 | 86.1128 | 86.5232 | 0 | 32.8788
2018-03-09 02:00 | 86.2791 | 86.6896 | 0 | 32.942
2018-03-09 03:00 | 86.0014 | 86.4485 | 0 | 32.8504
2018-03-09 04:00 | 86.0533 | 86.4347 | 0 | 32.8452
2018-03-09 05:00 | 86.2257 | 86.6117 | 0 | 32.9124
2018-03-09 06:00 | 86.4332 | 86.9352 | 0 | 33.0354
2018-03-09 07:00 | 86.5873 | 87.0619 | 0 | 33.0835
2018-03-09 08:00 | 86.3691 | 86.7811 | 0 | 32.9768
2018-03-09 09:00 | 86.334 | 86.7399 | 0 | 32.9612
2018-03-09 10:00 | 86.5126 | 86.862 | 0 | 33.0076
2018-03-09 11:00 | 86.5003 | 86.9306 | 0 | 33.0336
2018-03-09 12:00 | 86.7002 | 87.1412 | 0 | 33.1137
2018-03-09 13:00 | 86.363 | 86.8009 | 0 | 32.9843
2018-03-09 14:00 | 86.4408 | 86.8635 | 0 | 33.0081
2018-03-09 15:00 | 86.2943 | 86.6743 | 0 | 32.9362
2018-03-09 16:00 | 86.3706 | 86.7491 | 0 | 32.9647
2018-03-09 17:00 | 86.2882 | 86.7445 | 0 | 32.9629
2018-03-09 18:00 | 86.1875 | 86.6667 | 0 | 32.9333
2018-03-09 19:00 | 86.099 | 86.5431 | 0 | 32.8864
2018-03-09 20:00 | 86.1997 | 86.5187 | 0 | 32.8771
2018-03-09 21:00 | 86.3767 | 86.7247 | 0 | 32.9554
2018-03-09 22:00 | 86.3691 | 86.7659 | 0 | 32.971
2018-03-09 23:00 | 86.4012 | 86.7918 | 0 | 32.9809
2018-03-10 | 86.0121 | 0 | 86.5507 | 32.8893
2018-03-10 01:00 | 85.919 | 0 | 86.5324 | 32.8823
2018-03-10 02:00 | 86.0533 | 0 | 86.6453 | 32.9252
2018-03-10 03:00 | 86.1677 | 0 | 86.7002 | 32.9461
2018-03-10 04:00 | 86.3081 | 0 | 86.8513 | 33.0035
2018-03-10 05:00 | 86.2562 | 0 | 86.8605 | 33.007
2018-03-10 06:00 | 86.1234 | 0 | 86.6682 | 32.9339
2018-03-10 07:00 | 86.1906 | 0 | 86.7247 | 32.9554
2018-03-10 08:00 | 86.36 | 0 | 86.952 | 33.0418
2018-03-10 09:00 | 86.4912 | 0 | 87.0588 | 33.0823
2018-03-10 10:00 | 86.1982 | 0 | 86.6392 | 32.9229
2018-03-10 11:00 | 86.1707 | 0 | 86.8849 | 33.0163
2018-03-10 12:00 | 86.5019 | 0 | 87.1504 | 33.1172
2018-03-10 13:00 | 86.6148 | 0 | 87.3167 | 33.1803
2018-03-10 14:00 | 86.4439 | 0 | 87.0832 | 33.0916
2018-03-10 15:00 | 86.5522 | 0 | 87.2938 | 33.1716
2018-03-10 16:00 | 86.5644 | 0 | 87.3579 | 33.196
2018-03-10 17:00 | 86.7445 | 0 | 87.57 | 33.2766
2018-03-10 18:00 | 86.4668 | 0 | 87.3014 | 33.1745
2018-03-10 19:00 | 86.3661 | 0 | 87.0954 | 33.0963
2018-03-10 20:00 | 86.1173 | 0 | 86.891 | 33.0186
2018-03-10 21:00 | 86.1555 | 0 | 86.9245 | 33.0313
2018-03-10 22:00 | 86.2211 | 0 | 87.0054 | 33.0621
2018-03-10 23:00 | 86.2226 | 0 | 87.0787 | 33.0899
2018-03-11 | 86.2364 | 86.7994 | 0 | 32.9838
2018-03-11 01:00 | 86.3188 | 86.952 | 0 | 33.0418
2018-03-11 02:00 | 86.2119 | 86.8177 | 0 | 32.9907
2018-03-11 03:00 | 86.1845 | 86.7857 | 0 | 32.9786
2018-03-11 04:00 | 86.2455 | 86.833 | 0 | 32.9965
2018-03-11 05:00 | 86.2333 | 86.833 | 0 | 32.9965
2018-03-11 06:00 | 86.2776 | 86.8528 | 0 | 33.0041
2018-03-11 07:00 | 86.2867 | 86.8452 | 0 | 33.0012
2018-03-11 08:00 | 86.2989 | 86.9032 | 0 | 33.0232
2018-03-11 09:00 | 86.2867 | 86.8162 | 0 | 32.9902
2018-03-11 10:00 | 86.2882 | 86.8528 | 0 | 33.0041
2018-03-11 11:00 | 86.1845 | 86.743 | 0 | 32.9623
2018-03-11 12:00 | 86.1418 | 86.714 | 0 | 32.9513
2018-03-11 13:00 | 86.1479 | 86.7659 | 0 | 32.971
2018-03-11 14:00 | 86.1112 | 86.7018 | 0 | 32.9467
2018-03-11 15:00 | 86.2455 | 86.8482 | 0 | 33.0023
2018-03-11 16:00 | 86.3447 | 86.9398 | 0 | 33.0371
2018-03-11 17:00 | 86.4805 | 86.9856 | 0 | 33.0545
2018-03-11 18:00 | 86.4332 | 86.92 | 0 | 33.0296
2018-03-11 19:00 | 85.6794 | 85.9266 | 0 | 32.6521
2018-03-11 20:00 | 86.3294 | 86.5888 | 0 | 32.9037
2018-03-11 21:00 | 86.3569 | 86.6728 | 0 | 32.9357
2018-03-11 22:00 | 86.4881 | 86.8086 | 0 | 32.9873
2018-03-11 23:00 | 86.4332 | 86.7353 | 0 | 32.9594
2018-03-12 | 86.4088 | 86.7002 | 86.9352 | 65.9815
2018-03-12 01:00 | 86.0426 | 86.3127 | 86.5278 | 65.6794
2018-03-12 02:00 | 86.392 | 86.6392 | 86.8421 | 65.9229
2018-03-12 03:00 | 86.2776 | 86.5766 | 86.7536 | 65.8655
2018-03-12 04:00 | 86.5034 | 86.8849 | 87.0283 | 66.087
2018-03-12 05:00 | 86.3661 | 86.772 | 87.0054 | 66.0354
2018-03-12 06:00 | 86.2898 | 86.6499 | 86.8147 | 65.9165
2018-03-12 07:00 | 86.2043 | 86.5278 | 86.7079 | 65.8296
2018-03-12 08:00 | 86.3355 | 86.5461 | 86.8025 | 65.8725
2018-03-12 09:00 | 86.3798 | 86.7262 | 86.8711 | 65.967
2018-03-12 10:00 | 86.2272 | 86.5156 | 86.714 | 65.8272
2018-03-12 11:00 | 86.2119 | 86.5141 | 86.7201 | 65.829
2018-03-12 12:00 | 86.389 | 86.6835 | 86.8574 | 65.9455
2018-03-12 13:00 | 86.4027 | 86.6224 | 86.7475 | 65.8806
2018-03-12 14:00 | 86.3783 | 86.6606 | 86.7903 | 65.9113
2018-03-12 15:00 | 86.3355 | 86.5248 | 86.7384 | 65.84
2018-03-12 16:00 | 86.3493 | 86.4912 | 86.685 | 65.807
2018-03-12 17:00 | 86.244 | 86.4683 | 86.6743 | 65.7942
2018-03-12 18:00 | 86.3142 | 86.4378 | 86.5934 | 65.7519
2018-03-12 19:00 | 86.2089 | 86.3508 | 86.5583 | 65.7055
2018-03-12 20:00 | 86.2181 | 86.4836 | 86.6896 | 65.8058
2018-03-12 21:00 | 86.1494 | 86.4759 | 86.63 | 65.7802
2018-03-12 22:00 | 86.2593 | 86.5522 | 86.6468 | 65.8156
2018-03-12 23:00 | 86.4424 | 86.8055 | 86.8864 | 66.0029
2018-03-13 | 86.4637 | 0 | 0 | 0
2018-03-13 01:00 | 86.5629 | 0 | 0 | 0
2018-03-13 02:00 | 86.3706 | 0 | 0 | 0
2018-03-13 03:00 | 86.3523 | 0 | 0 | 0
2018-03-13 04:00 | 86.3676 | 0 | 0 | 0
2018-03-13 05:00 | 86.4027 | 0 | 0 | 0
2018-03-13 06:00 | 86.4652 | 0 | 0 | 0
2018-03-13 07:00 | 86.4012 | 0 | 0 | 0
2018-03-13 08:00 | 86.4515 | 0 | 0 | 0
2018-03-13 09:00 | 86.2028 | 0 | 0 | 0
2018-03-13 10:00 | 86.2715 | 0 | 0 | 0
2018-03-13 11:00 | 86.7567 | 0 | 0 | 0
2018-03-13 12:00 | 86.6194 | 0 | 0 | 0
2018-03-13 13:00 | 86.6377 | 0 | 0 | 0
2018-03-13 14:00 | 86.8757 | 0 | 0 | 0
2018-03-13 15:00 | 86.7994 | 0 | 0 | 0
2018-03-13 16:00 | 86.7674 | 0 | 0 | 0
2018-03-13 17:00 | 86.7384 | 0 | 0 | 0
2018-03-13 18:00 | 86.7124 | 0 | 0 | 0
2018-03-13 19:00 | 86.8376 | 0 | 0 | 0
2018-03-13 20:00 | 86.627 | 0 | 0 | 0
2018-03-13 21:00 | 86.6239 | 0 | 0 | 0
2018-03-13 22:00 | 86.714 | 0 | 0 | 0
2018-03-13 23:00 | 86.8971 | 0 | 0 | 0
2018-03-14 | 0 | 0 | 86.6712 | 32.9351
2018-03-14 01:00 | 0 | 0 | 86.511 | 32.8742
2018-03-14 02:00 | 0 | 0 | 86.7628 | 32.9699
2018-03-14 03:00 | 0 | 0 | 86.7384 | 32.9606
2018-03-14 04:00 | 0 | 0 | 86.8376 | 32.9983
2018-03-14 05:00 | 0 | 0 | 87.0222 | 33.0684
2018-03-14 06:00 | 0 | 0 | 86.9627 | 33.0458
2018-03-14 07:00 | 0 | 0 | 87.1321 | 33.1102
2018-03-14 08:00 | 0 | 0 | 87.1931 | 33.1334
2018-03-14 09:00 | 0 | 0 | 86.7155 | 32.9519
2018-03-14 10:00 | 0 | 0 | 86.6743 | 32.9362
2018-03-14 11:00 | 0 | 0 | 86.8956 | 33.0203
2018-03-14 12:00 | 0 | 0 | 86.9276 | 33.0325
2018-03-14 13:00 | 0 | 0 | 87.2541 | 33.1566
2018-03-14 14:00 | 0 | 0 | 87.4037 | 33.2134
2018-03-14 15:00 | 0 | 0 | 87.2129 | 33.1409
2018-03-14 16:00 | 0 | 0 | 86.9718 | 33.0493
2018-03-14 17:00 | 0 | 0 | 87.1397 | 33.1131
2018-03-14 18:00 | 0 | 0 | 87.2435 | 33.1525
2018-03-14 19:00 | 0 | 0 | 86.8894 | 33.018
2018-03-14 20:00 | 0 | 0 | 87.1839 | 33.1299
2018-03-14 21:00 | 0 | 0 | 87.2419 | 33.1519
2018-03-14 22:00 | 0 | 0 | 87.1733 | 33.1259
2018-03-14 23:00 | 0 | 0 | 87.2557 | 33.1572
2018-03-15 | 86.5492 | 0 | 0 | 0
2018-03-15 01:00 | 86.7201 | 0 | 0 | 0
2018-03-15 02:00 | 86.5095 | 0 | 0 | 0
2018-03-15 03:00 | 86.4576 | 0 | 0 | 0
2018-03-15 04:00 | 86.6316 | 0 | 0 | 0
2018-03-15 05:00 | 86.569 | 0 | 0 | 0
2018-03-15 06:00 | 86.6468 | 0 | 0 | 0
2018-03-15 07:00 | 86.6361 | 0 | 0 | 0
2018-03-15 08:00 | 86.6819 | 0 | 0 | 0
2018-03-15 09:00 | 86.7094 | 0 | 0 | 0
2018-03-15 10:00 | 86.7933 | 0 | 0 | 0
2018-03-15 11:00 | 86.8009 | 0 | 0 | 0
2018-03-15 12:00 | 86.6728 | 0 | 0 | 0
2018-03-15 13:00 | 86.6316 | 0 | 0 | 0
2018-03-15 14:00 | 86.6316 | 0 | 0 | 0
2018-03-15 15:00 | 86.6636 | 0 | 0 | 0
2018-03-15 16:00 | 86.5568 | 0 | 0 | 0
2018-03-15 17:00 | 86.6865 | 0 | 0 | 0
2018-03-15 18:00 | 86.7262 | 0 | 0 | 0
2018-03-15 19:00 | 86.5187 | 0 | 0 | 0
2018-03-15 20:00 | 86.5766 | 0 | 0 | 0
2018-03-15 21:00 | 86.6194 | 0 | 0 | 0
2018-03-15 22:00 | 86.6743 | 0 | 0 | 0
2018-03-15 23:00 | 86.5644 | 0 | 0 | 0
2018-03-16 | 86.2226 | 86.688 | 0 | 32.9414
2018-03-16 01:00 | 86.1128 | 86.5232 | 0 | 32.8788
2018-03-16 02:00 | 86.2791 | 86.6896 | 0 | 32.942
2018-03-16 03:00 | 86.0014 | 86.4485 | 0 | 32.8504
2018-03-16 04:00 | 86.0533 | 86.4347 | 0 | 32.8452
2018-03-16 05:00 | 86.2257 | 86.6117 | 0 | 32.9124
2018-03-16 06:00 | 86.4332 | 86.9352 | 0 | 33.0354
2018-03-16 07:00 | 86.5873 | 87.0619 | 0 | 33.0835
2018-03-16 08:00 | 86.3691 | 86.7811 | 0 | 32.9768
2018-03-16 09:00 | 86.334 | 86.7399 | 0 | 32.9612
2018-03-16 10:00 | 86.5126 | 86.862 | 0 | 33.0076
2018-03-16 11:00 | 86.5003 | 86.9306 | 0 | 33.0336
2018-03-16 12:00 | 86.7002 | 87.1412 | 0 | 33.1137
2018-03-16 13:00 | 86.363 | 86.8009 | 0 | 32.9843
2018-03-16 14:00 | 86.4408 | 86.8635 | 0 | 33.0081
2018-03-16 15:00 | 86.2943 | 86.6743 | 0 | 32.9362
2018-03-16 16:00 | 86.3706 | 86.7491 | 0 | 32.9647
2018-03-16 17:00 | 86.2882 | 86.7445 | 0 | 32.9629
2018-03-16 18:00 | 86.1875 | 86.6667 | 0 | 32.9333
2018-03-16 19:00 | 86.099 | 86.5431 | 0 | 32.8864
2018-03-16 20:00 | 86.1997 | 86.5187 | 0 | 32.8771
2018-03-16 21:00 | 86.3767 | 86.7247 | 0 | 32.9554
2018-03-16 22:00 | 86.3691 | 86.7659 | 0 | 32.971
2018-03-16 23:00 | 86.4012 | 86.7918 | 0 | 32.9809
2018-03-17 | 86.0121 | 0 | 86.5507 | 32.8893
2018-03-17 01:00 | 85.919 | 0 | 86.5324 | 32.8823
2018-03-17 02:00 | 86.0533 | 0 | 86.6453 | 32.9252
2018-03-17 03:00 | 86.1677 | 0 | 86.7002 | 32.9461
2018-03-17 04:00 | 86.3081 | 0 | 86.8513 | 33.0035
2018-03-17 05:00 | 86.2562 | 0 | 86.8605 | 33.007
2018-03-17 06:00 | 86.1234 | 0 | 86.6682 | 32.9339
2018-03-17 07:00 | 86.1906 | 0 | 86.7247 | 32.9554
2018-03-17 08:00 | 86.36 | 0 | 86.952 | 33.0418
2018-03-17 09:00 | 86.4912 | 0 | 87.0588 | 33.0823
2018-03-17 10:00 | 86.1982 | 0 | 86.6392 | 32.9229
2018-03-17 11:00 | 86.1707 | 0 | 86.8849 | 33.0163
2018-03-17 12:00 | 86.5019 | 0 | 87.1504 | 33.1172
2018-03-17 13:00 | 86.6148 | 0 | 87.3167 | 33.1803
2018-03-17 14:00 | 86.4439 | 0 | 87.0832 | 33.0916
2018-03-17 15:00 | 86.5522 | 0 | 87.2938 | 33.1716
2018-03-17 16:00 | 86.5644 | 0 | 87.3579 | 33.196
2018-03-17 17:00 | 86.7445 | 0 | 87.57 | 33.2766
2018-03-17 18:00 | 86.4668 | 0 | 87.3014 | 33.1745
2018-03-17 19:00 | 86.3661 | 0 | 87.0954 | 33.0963
2018-03-17 20:00 | 86.1173 | 0 | 86.891 | 33.0186
2018-03-17 21:00 | 86.1555 | 0 | 86.9245 | 33.0313
2018-03-17 22:00 | 86.2211 | 0 | 87.0054 | 33.0621
2018-03-17 23:00 | 86.2226 | 0 | 87.0787 | 33.0899
2018-03-18 | 86.2364 | 86.7994 | 0 | 32.9838
2018-03-18 01:00 | 86.3188 | 86.952 | 0 | 33.0418
2018-03-18 02:00 | 86.2119 | 86.8177 | 0 | 32.9907
2018-03-18 03:00 | 86.1845 | 86.7857 | 0 | 32.9786
2018-03-18 04:00 | 86.2455 | 86.833 | 0 | 32.9965
2018-03-18 05:00 | 86.2333 | 86.833 | 0 | 32.9965
2018-03-18 06:00 | 86.2776 | 86.8528 | 0 | 33.0041
2018-03-18 07:00 | 86.2867 | 86.8452 | 0 | 33.0012
2018-03-18 08:00 | 86.2989 | 86.9032 | 0 | 33.0232
2018-03-18 09:00 | 86.2867 | 86.8162 | 0 | 32.9902
2018-03-18 10:00 | 86.2882 | 86.8528 | 0 | 33.0041
2018-03-18 11:00 | 86.1845 | 86.743 | 0 | 32.9623
2018-03-18 12:00 | 86.1418 | 86.714 | 0 | 32.9513
2018-03-18 13:00 | 86.1479 | 86.7659 | 0 | 32.971
2018-03-18 14:00 | 86.1112 | 86.7018 | 0 | 32.9467
2018-03-18 15:00 | 86.2455 | 86.8482 | 0 | 33.0023
2018-03-18 16:00 | 86.3447 | 86.9398 | 0 | 33.0371
2018-03-18 17:00 | 86.4805 | 86.9856 | 0 | 33.0545
2018-03-18 18:00 | 86.4332 | 86.92 | 0 | 33.0296
2018-03-18 19:00 | 85.6794 | 85.9266 | 0 | 32.6521
2018-03-18 20:00 | 86.3294 | 86.5888 | 0 | 32.9037
2018-03-18 21:00 | 86.3569 | 86.6728 | 0 | 32.9357
2018-03-18 22:00 | 86.4881 | 86.8086 | 0 | 32.9873
2018-03-18 23:00 | 86.4332 | 86.7353 | 0 | 32.9594
2018-03-19 | 86.4088 | 86.7002 | 86.9352 | 65.9815
2018-03-19 01:00 | 86.0426 | 86.3127 | 86.5278 | 65.6794
2018-03-19 02:00 | 86.392 | 86.6392 | 86.8421 | 65.9229
2018-03-19 03:00 | 86.2776 | 86.5766 | 86.7536 | 65.8655
2018-03-19 04:00 | 86.5034 | 86.8849 | 87.0283 | 66.087
2018-03-19 05:00 | 86.3661 | 86.772 | 87.0054 | 66.0354
2018-03-19 06:00 | 86.2898 | 86.6499 | 86.8147 | 65.9165
2018-03-19 07:00 | 86.2043 | 86.5278 | 86.7079 | 65.8296
2018-03-19 08:00 | 86.3355 | 86.5461 | 86.8025 | 65.8725
2018-03-19 09:00 | 86.3798 | 86.7262 | 86.8711 | 65.967
2018-03-19 10:00 | 86.2272 | 86.5156 | 86.714 | 65.8272
2018-03-19 11:00 | 86.2119 | 86.5141 | 86.7201 | 65.829
2018-03-19 12:00 | 86.389 | 86.6835 | 86.8574 | 65.9455
2018-03-19 13:00 | 86.4027 | 86.6224 | 86.7475 | 65.8806
2018-03-19 14:00 | 86.3783 | 86.6606 | 86.7903 | 65.9113
2018-03-19 15:00 | 86.3355 | 86.5248 | 86.7384 | 65.84
2018-03-19 16:00 | 86.3493 | 86.4912 | 86.685 | 65.807
2018-03-19 17:00 | 86.244 | 86.4683 | 86.6743 | 65.7942
2018-03-19 18:00 | 86.3142 | 86.4378 | 86.5934 | 65.7519
2018-03-19 19:00 | 86.2089 | 86.3508 | 86.5583 | 65.7055
2018-03-19 20:00 | 86.2181 | 86.4836 | 86.6896 | 65.8058
2018-03-19 21:00 | 86.1494 | 86.4759 | 86.63 | 65.7802
2018-03-19 22:00 | 86.2593 | 86.5522 | 86.6468 | 65.8156
2018-03-19 23:00 | 86.4424 | 86.8055 | 86.8864 | 66.0029
2018-03-20 | 86.4637 | 0 | 0 | 0
2018-03-20 01:00 | 86.5629 | 0 | 0 | 0
2018-03-20 02:00 | 86.3706 | 0 | 0 | 0
2018-03-20 03:00 | 86.3523 | 0 | 0 | 0
2018-03-20 04:00 | 86.3676 | 0 | 0 | 0
2018-03-20 05:00 | 86.4027 | 0 | 0 | 0
2018-03-20 06:00 | 86.4652 | 0 | 0 | 0
2018-03-20 07:00 | 86.4012 | 0 | 0 | 0
2018-03-20 08:00 | 86.4515 | 0 | 0 | 0
2018-03-20 09:00 | 86.2028 | 0 | 0 | 0
2018-03-20 10:00 | 86.2715 | 0 | 0 | 0
2018-03-20 11:00 | 86.7567 | 0 | 0 | 0
2018-03-20 12:00 | 86.6194 | 0 | 0 | 0
2018-03-20 13:00 | 86.6377 | 0 | 0 | 0
2018-03-20 14:00 | 86.8757 | 0 | 0 | 0
2018-03-20 15:00 | 86.7994 | 0 | 0 | 0
2018-03-20 16:00 | 86.7674 | 0 | 0 | 0
2018-03-20 17:00 | 86.7384 | 0 | 0 | 0
2018-03-20 18:00 | 86.7124 | 0 | 0 | 0
2018-03-20 19:00 | 86.8376 | 0 | 0 | 0
2018-03-20 20:00 | 86.627 | 0 | 0 | 0
2018-03-20 21:00 | 86.6239 | 0 | 0 | 0
2018-03-20 22:00 | 86.714 | 0 | 0 | 0
2018-03-20 23:00 | 86.8971 | 0 | 0 | 0
2018-03-21 | 0 | 0 | 86.6712 | 32.9351
2018-03-21 01:00 | 0 | 0 | 86.511 | 32.8742
2018-03-21 02:00 | 0 | 0 | 86.7628 | 32.9699
2018-03-21 03:00 | 0 | 0 | 86.7384 | 32.9606
2018-03-21 04:00 | 0 | 0 | 86.8376 | 32.9983
2018-03-21 05:00 | 0 | 0 | 87.0222 | 33.0684
2018-03-21 06:00 | 0 | 0 | 86.9627 | 33.0458
2018-03-21 07:00 | 0 | 0 | 87.1321 | 33.1102
2018-03-21 08:00 | 0 | 0 | 87.1931 | 33.1334
2018-03-21 09:00 | 0 | 0 | 86.7155 | 32.9519
2018-03-21 10:00 | 0 | 0 | 86.6743 | 32.9362
2018-03-21 11:00 | 0 | 0 | 86.8956 | 33.0203
2018-03-21 12:00 | 0 | 0 | 86.9276 | 33.0325
2018-03-21 13:00 | 0 | 0 | 87.2541 | 33.1566
2018-03-21 14:00 | 0 | 0 | 87.4037 | 33.2134
2018-03-21 15:00 | 0 | 0 | 87.2129 | 33.1409
2018-03-21 16:00 | 0 | 0 | 86.9718 | 33.0493
2018-03-21 17:00 | 0 | 0 | 87.1397 | 33.1131
2018-03-21 18:00 | 0 | 0 | 87.2435 | 33.1525
2018-03-21 19:00 | 0 | 0 | 86.8894 | 33.018
2018-03-21 20:00 | 0 | 0 | 87.1839 | 33.1299
2018-03-21 21:00 | 0 | 0 | 87.2419 | 33.1519
2018-03-21 22:00 | 0 | 0 | 87.1733 | 33.1259
2018-03-21 23:00 | 0 | 0 | 87.2557 | 33.1572
2018-03-22 | 86.5492 | 0 | 0 | 0
2018-03-22 01:00 | 86.7201 | 0 | 0 | 0
2018-03-22 02:00 | 86.5095 | 0 | 0 | 0
2018-03-22 03:00 | 86.4576 | 0 | 0 | 0
2018-03-22 04:00 | 86.6316 | 0 | 0 | 0
2018-03-22 05:00 | 86.569 | 0 | 0 | 0
2018-03-22 06:00 | 86.6468 | 0 | 0 | 0
2018-03-22 07:00 | 86.6361 | 0 | 0 | 0
2018-03-22 08:00 | 86.6819 | 0 | 0 | 0
2018-03-22 09:00 | 86.7094 | 0 | 0 | 0
2018-03-22 10:00 | 86.7933 | 0 | 0 | 0
2018-03-22 11:00 | 86.8009 | 0 | 0 | 0
2018-03-22 12:00 | 86.6728 | 0 | 0 | 0
2018-03-22 13:00 | 86.6316 | 0 | 0 | 0
2018-03-22 14:00 | 86.6316 | 0 | 0 | 0
2018-03-22 15:00 | 86.6636 | 0 | 0 | 0
2018-03-22 16:00 | 86.5568 | 0 | 0 | 0
2018-03-22 17:00 | 86.6865 | 0 | 0 | 0
2018-03-22 18:00 | 86.7262 | 0 | 0 | 0
2018-03-22 19:00 | 86.5187 | 0 | 0 | 0
2018-03-22 20:00 | 86.5766 | 0 | 0 | 0
2018-03-22 21:00 | 86.6194 | 0 | 0 | 0
2018-03-22 22:00 | 86.6743 | 0 | 0 | 0
2018-03-22 23:00 | 86.5644 | 0 | 0 | 0
2018-03-23 | 86.2226 | 86.688 | 0 | 32.9414
2018-03-23 01:00 | 86.1128 | 86.5232 | 0 | 32.8788
2018-03-23 02:00 | 86.2791 | 86.6896 | 0 | 32.942
2018-03-23 03:00 | 86.0014 | 86.4485 | 0 | 32.8504
2018-03-23 04:00 | 86.0533 | 86.4347 | 0 | 32.8452
2018-03-23 05:00 | 86.2257 | 86.6117 | 0 | 32.9124
2018-03-23 06:00 | 86.4332 | 86.9352 | 0 | 33.0354
2018-03-23 07:00 | 86.5873 | 87.0619 | 0 | 33.0835
2018-03-23 08:00 | 86.3691 | 86.7811 | 0 | 32.9768
2018-03-23 09:00 | 86.334 | 86.7399 | 0 | 32.9612
2018-03-23 10:00 | 86.5126 | 86.862 | 0 | 33.0076
2018-03-23 11:00 | 86.5003 | 86.9306 | 0 | 33.0336
2018-03-23 12:00 | 86.7002 | 87.1412 | 0 | 33.1137
2018-03-23 13:00 | 86.363 | 86.8009 | 0 | 32.9843
2018-03-23 14:00 | 86.4408 | 86.8635 | 0 | 33.0081
2018-03-23 15:00 | 86.2943 | 86.6743 | 0 | 32.9362
2018-03-23 16:00 | 86.3706 | 86.7491 | 0 | 32.9647
2018-03-23 17:00 | 86.2882 | 86.7445 | 0 | 32.9629
2018-03-23 18:00 | 86.1875 | 86.6667 | 0 | 32.9333
2018-03-23 19:00 | 86.099 | 86.5431 | 0 | 32.8864
2018-03-23 20:00 | 86.1997 | 86.5187 | 0 | 32.8771
2018-03-23 21:00 | 86.3767 | 86.7247 | 0 | 32.9554
2018-03-23 22:00 | 86.3691 | 86.7659 | 0 | 32.971
2018-03-23 23:00 | 86.4012 | 86.7918 | 0 | 32.9809
2018-03-24 | 86.0121 | 0 | 86.5507 | 32.8893
2018-03-24 01:00 | 85.919 | 0 | 86.5324 | 32.8823
2018-03-24 02:00 | 86.0533 | 0 | 86.6453 | 32.9252
2018-03-24 03:00 | 86.1677 | 0 | 86.7002 | 32.9461
2018-03-24 04:00 | 86.3081 | 0 | 86.8513 | 33.0035
2018-03-24 05:00 | 86.2562 | 0 | 86.8605 | 33.007
2018-03-24 06:00 | 86.1234 | 0 | 86.6682 | 32.9339
2018-03-24 07:00 | 86.1906 | 0 | 86.7247 | 32.9554
2018-03-24 08:00 | 86.36 | 0 | 86.952 | 33.0418
2018-03-24 09:00 | 86.4912 | 0 | 87.0588 | 33.0823
2018-03-24 10:00 | 86.1982 | 0 | 86.6392 | 32.9229
2018-03-24 11:00 | 86.1707 | 0 | 86.8849 | 33.0163
2018-03-24 12:00 | 86.5019 | 0 | 87.1504 | 33.1172
2018-03-24 13:00 | 86.6148 | 0 | 87.3167 | 33.1803
2018-03-24 14:00 | 86.4439 | 0 | 87.0832 | 33.0916
2018-03-24 15:00 | 86.5522 | 0 | 87.2938 | 33.1716
2018-03-24 16:00 | 86.5644 | 0 | 87.3579 | 33.196
2018-03-24 17:00 | 86.7445 | 0 | 87.57 | 33.2766
2018-03-24 18:00 | 86.4668 | 0 | 87.3014 | 33.1745
2018-03-24 19:00 | 86.3661 | 0 | 87.0954 | 33.0963
2018-03-24 20:00 | 86.1173 | 0 | 86.891 | 33.0186
2018-03-24 21:00 | 86.1555 | 0 | 86.9245 | 33.0313
2018-03-24 22:00 | 86.2211 | 0 | 87.0054 | 33.0621
2018-03-24 23:00 | 86.2226 | 0 | 87.0787 | 33.0899
2018-03-25 | 86.2364 | 86.7994 | 0 | 32.9838
2018-03-25 01:00 | 86.3188 | 86.952 | 0 | 33.0418
2018-03-25 02:00 | 86.2119 | 86.8177 | 0 | 32.9907
2018-03-25 03:00 | 86.1845 | 86.7857 | 0 | 32.9786
2018-03-25 04:00 | 86.2455 | 86.833 | 0 | 32.9965
2018-03-25 05:00 | 86.2333 | 86.833 | 0 | 32.9965
2018-03-25 06:00 | 86.2776 | 86.8528 | 0 | 33.0041
2018-03-25 07:00 | 86.2867 | 86.8452 | 0 | 33.0012
2018-03-25 08:00 | 86.2989 | 86.9032 | 0 | 33.0232
2018-03-25 09:00 | 86.2867 | 86.8162 | 0 | 32.9902
2018-03-25 10:00 | 86.2882 | 86.8528 | 0 | 33.0041
2018-03-25 11:00 | 86.1845 | 86.743 | 0 | 32.9623
2018-03-25 12:00 | 86.1418 | 86.714 | 0 | 32.9513
2018-03-25 13:00 | 86.1479 | 86.7659 | 0 | 32.971
2018-03-25 14:00 | 86.1112 | 86.7018 | 0 | 32.9467
2018-03-25 15:00 | 86.2455 | 86.8482 | 0 | 33.0023
2018-03-25 16:00 | 86.3447 | 86.9398 | 0 | 33.0371
2018-03-25 17:00 | 86.4805 | 86.9856 | 0 | 33.0545
2018-03-25 18:00 | 86.4332 | 86.92 | 0 | 33.0296
2018-03-25 19:00 | 85.6794 | 85.9266 | 0 | 32.6521
2018-03-25 20:00 | 86.3294 | 86.5888 | 0 | 32.9037
2018-03-25 21:00 | 86.3569 | 86.6728 | 0 | 32.9357
2018-03-25 22:00 | 86.4881 | 86.8086 | 0 | 32.9873
2018-03-25 23:00 | 86.4332 | 86.7353 | 0 | 32.9594
2018-03-26 | 86.4088 | 86.7002 | 86.9352 | 65.9815
2018-03-26 01:00 | 86.0426 | 86.3127 | 86.5278 | 65.6794
2018-03-26 02:00 | 86.392 | 86.6392 | 86.8421 | 65.9229
2018-03-26 03:00 | 86.2776 | 86.5766 | 86.7536 | 65.8655
2018-03-26 04:00 | 86.5034 | 86.8849 | 87.0283 | 66.087
2018-03-26 05:00 | 86.3661 | 86.772 | 87.0054 | 66.0354
2018-03-26 06:00 | 86.2898 | 86.6499 | 86.8147 | 65.9165
2018-03-26 07:00 | 86.2043 | 86.5278 | 86.7079 | 65.8296
2018-03-26 08:00 | 86.3355 | 86.5461 | 86.8025 | 65.8725
2018-03-26 09:00 | 86.3798 | 86.7262 | 86.8711 | 65.967
2018-03-26 10:00 | 86.2272 | 86.5156 | 86.714 | 65.8272
2018-03-26 11:00 | 86.2119 | 86.5141 | 86.7201 | 65.829
2018-03-26 12:00 | 86.389 | 86.6835 | 86.8574 | 65.9455
2018-03-26 13:00 | 86.4027 | 86.6224 | 86.7475 | 65.8806
2018-03-26 14:00 | 86.3783 | 86.6606 | 86.7903 | 65.9113
2018-03-26 15:00 | 86.3355 | 86.5248 | 86.7384 | 65.84
2018-03-26 16:00 | 86.3493 | 86.4912 | 86.685 | 65.807
2018-03-26 17:00 | 86.244 | 86.4683 | 86.6743 | 65.7942
2018-03-26 18:00 | 86.3142 | 86.4378 | 86.5934 | 65.7519
2018-03-26 19:00 | 86.2089 | 86.3508 | 86.5583 | 65.7055
2018-03-26 20:00 | 86.2181 | 86.4836 | 86.6896 | 65.8058
2018-03-26 21:00 | 86.1494 | 86.4759 | 86.63 | 65.7802
2018-03-26 22:00 | 86.2593 | 86.5522 | 86.6468 | 65.8156
2018-03-26 23:00 | 86.4424 | 86.8055 | 86.8864 | 66.0029
2018-03-27 | 86.4637 | 0 | 0 | 0
2018-03-27 01:00 | 86.5629 | 0 | 0 | 0
2018-03-27 02:00 | 86.3706 | 0 | 0 | 0
2018-03-27 03:00 | 86.3523 | 0 | 0 | 0
2018-03-27 04:00 | 86.3676 | 0 | 0 | 0
2018-03-27 05:00 | 86.4027 | 0 | 0 | 0
2018-03-27 06:00 | 86.4652 | 0 | 0 | 0
2018-03-27 07:00 | 86.4012 | 0 | 0 | 0
2018-03-27 08:00 | 86.4515 | 0 | 0 | 0
2018-03-27 09:00 | 86.2028 | 0 | 0 | 0
2018-03-27 10:00 | 86.2715 | 0 | 0 | 0
2018-03-27 11:00 | 86.7567 | 0 | 0 | 0
2018-03-27 12:00 | 86.6194 | 0 | 0 | 0
2018-03-27 13:00 | 86.6377 | 0 | 0 | 0
2018-03-27 14:00 | 86.8757 | 0 | 0 | 0
2018-03-27 15:00 | 86.7994 | 0 | 0 | 0
2018-03-27 16:00 | 86.7674 | 0 | 0 | 0
2018-03-27 17:00 | 86.7384 | 0 | 0 | 0
2018-03-27 18:00 | 86.7124 | 0 | 0 | 0
2018-03-27 19:00 | 86.8376 | 0 | 0 | 0
2018-03-27 20:00 | 86.627 | 0 | 0 | 0
2018-03-27 21:00 | 86.6239 | 0 | 0 | 0
2018-03-27 22:00 | 86.714 | 0 | 0 | 0
2018-03-27 23:00 | 86.8971 | 0 | 0 | 0
2018-03-28 | 0 | 0 | 86.6712 | 32.9351
2018-03-28 01:00 | 0 | 0 | 86.511 | 32.8742
2018-03-28 02:00 | 0 | 0 | 86.7628 | 32.9699
2018-03-28 03:00 | 0 | 0 | 86.7384 | 32.9606
2018-03-28 04:00 | 0 | 0 | 86.8376 | 32.9983
2018-03-28 05:00 | 0 | 0 | 87.0222 | 33.0684
2018-03-28 06:00 | 0 | 0 | 86.9627 | 33.0458
2018-03-28 07:00 | 0 | 0 | 87.1321 | 33.1102
2018-03-28 08:00 | 0 | 0 | 87.1931 | 33.1334
2018-03-28 09:00 | 0 | 0 | 86.7155 | 32.9519
2018-03-28 10:00 | 0 | 0 | 86.6743 | 32.9362
2018-03-28 11:00 | 0 | 0 | 86.8956 | 33.0203
2018-03-28 12:00 | 0 | 0 | 86.9276 | 33.0325
2018-03-28 13:00 | 0 | 0 | 87.2541 | 33.1566
2018-03-28 14:00 | 0 | 0 | 87.4037 | 33.2134
2018-03-28 15:00 | 0 | 0 | 87.2129 | 33.1409
2018-03-28 16:00 | 0 | 0 | 86.9718 | 33.0493
2018-03-28 17:00 | 0 | 0 | 87.1397 | 33.1131
2018-03-28 18:00 | 0 | 0 | 87.2435 | 33.1525
2018-03-28 19:00 | 0 | 0 | 86.8894 | 33.018
2018-03-28 20:00 | 0 | 0 | 87.1839 | 33.1299
2018-03-28 21:00 | 0 | 0 | 87.2419 | 33.1519
2018-03-28 22:00 | 0 | 0 | 87.1733 | 33.1259
2018-03-28 23:00 | 0 | 0 | 87.2557 | 33.1572
2018-03-29 | 86.5492 | 0 | 0 | 0
2018-03-29 01:00 | 86.7201 | 0 | 0 | 0
2018-03-29 02:00 | 86.5095 | 0 | 0 | 0
2018-03-29 03:00 | 86.4576 | 0 | 0 | 0
2018-03-29 04:00 | 86.6316 | 0 | 0 | 0
2018-03-29 05:00 | 86.569 | 0 | 0 | 0
2018-03-29 06:00 | 86.6468 | 0 | 0 | 0
2018-03-29 07:00 | 86.6361 | 0 | 0 | 0
2018-03-29 08:00 | 86.6819 | 0 | 0 | 0
2018-03-29 09:00 | 86.7094 | 0 | 0 | 0
2018-03-29 10:00 | 86.7933 | 0 | 0 | 0
2018-03-29 11:00 | 86.8009 | 0 | 0 | 0
2018-03-29 12:00 | 86.6728 | 0 | 0 | 0
2018-03-29 13:00 | 86.6316 | 0 | 0 | 0
2018-03-29 14:00 | 86.6316 | 0 | 0 | 0
2018-03-29 15:00 | 86.6636 | 0 | 0 | 0
2018-03-29 16:00 | 86.5568 | 0 | 0 | 0
2018-03-29 17:00 | 86.6865 | 0 | 0 | 0
2018-03-29 18:00 | 86.7262 | 0 | 0 | 0
2018-03-29 19:00 | 86.5187 | 0 | 0 | 0
2018-03-29 20:00 | 86.5766 | 0 | 0 | 0
2018-03-29 21:00 | 86.6194 | 0 | 0 | 0
2018-03-29 22:00 | 86.6743 | 0 | 0 | 0
2018-03-29 23:00 | 86.5644 | 0 | 0 | 0
2018-03-30 | 86.2226 | 86.688 | 0 | 32.9414
2018-03-30 01:00 | 86.1128 | 86.5232 | 0 | 32.8788
2018-03-30 02:00 | 86.2791 | 86.6896 | 0 | 32.942
2018-03-30 03:00 | 86.0014 | 86.4485 | 0 | 32.8504
2018-03-30 04:00 | 86.0533 | 86.4347 | 0 | 32.8452
2018-03-30 05:00 | 86.2257 | 86.6117 | 0 | 32.9124
2018-03-30 06:00 | 86.4332 | 86.9352 | 0 | 33.0354
2018-03-30 07:00 | 86.5873 | 87.0619 | 0 | 33.0835
2018-03-30 08:00 | 86.3691 | 86.7811 | 0 | 32.9768
2018-03-30 09:00 | 86.334 | 86.7399 | 0 | 32.9612
2018-03-30 10:00 | 86.5126 | 86.862 | 0 | 33.0076
2018-03-30 11:00 | 86.5003 | 86.9306 | 0 | 33.0336
2018-03-30 12:00 | 86.7002 | 87.1412 | 0 | 33.1137
2018-03-30 13:00 | 86.363 | 86.8009 | 0 | 32.9843
2018-03-30 14:00 | 86.4408 | 86.8635 | 0 | 33.0081
2018-03-30 15:00 | 86.2943 | 86.6743 | 0 | 32.9362
2018-03-30 16:00 | 86.3706 | 86.7491 | 0 | 32.9647
2018-03-30 17:00 | 86.2882 | 86.7445 | 0 | 32.9629
2018-03-30 18:00 | 86.1875 | 86.6667 | 0 | 32.9333
2018-03-30 19:00 | 86.099 | 86.5431 | 0 | 32.8864
2018-03-30 20:00 | 86.1997 | 86.5187 | 0 | 32.8771
2018-03-30 21:00 | 86.3767 | 86.7247 | 0 | 32.9554
2018-03-30 22:00 | 86.3691 | 86.7659 | 0 | 32.971
2018-03-30 23:00 | 86.4012 | 86.7918 | 0 | 32.9809
2018-03-31 | 86.0121 | 0 | 86.5507 | 32.8893
2018-03-31 01:00 | 85.919 | 0 | 86.5324 | 32.8823
2018-03-31 02:00 | 86.0533 | 0 | 86.6453 | 32.9252
2018-03-31 03:00 | 86.1677 | 0 | 86.7002 | 32.9461
2018-03-31 04:00 | 86.3081 | 0 | 86.8513 | 33.0035
2018-03-31 05:00 | 86.2562 | 0 | 86.8605 | 33.007
2018-03-31 06:00 | 86.1234 | 0 | 86.6682 | 32.9339
2018-03-31 07:00 | 86.1906 | 0 | 86.7247 | 32.9554
2018-03-31 08:00 | 86.36 | 0 | 86.952 | 33.0418
2018-03-31 09:00 | 86.4912 | 0 | 87.0588 | 33.0823
2018-03-31 10:00 | 86.1982 | 0 | 86.6392 | 32.9229
2018-03-31 11:00 | 86.1707 | 0 | 86.8849 | 33.0163
2018-03-31 12:00 | 86.5019 | 0 | 87.1504 | 33.1172
2018-03-31 13:00 | 86.6148 | 0 | 87.3167 | 33.1803
2018-03-31 14:00 | 86.4439 | 0 | 87.0832 | 33.0916
2018-03-31 15:00 | 86.5522 | 0 | 87.2938 | 33.1716
2018-03-31 16:00 | 86.5644 | 0 | 87.3579 | 33.196
2018-03-31 17:00 | 86.7445 | 0 | 87.57 | 33.2766
2018-03-31 18:00 | 86.4668 | 0 | 87.3014 | 33.1745
2018-03-31 19:00 | 86.3661 | 0 | 87.0954 | 33.0963
2018-03-31 20:00 | 86.1173 | 0 | 86.891 | 33.0186
2018-03-31 21:00 | 86.1555 | 0 | 86.9245 | 33.0313
2018-03-31 22:00 | 86.2211 | 0 | 87.0054 | 33.0621
2018-03-31 23:00 | 86.2226 | 0 | 87.0787 | 33.0899
2018-04-01 | 86.2364 | 86.7994 | 0 | 32.9838
2018-04-01 01:00 | 86.3188 | 86.952 | 0 | 33.0418
2018-04-01 02:00 | 86.2119 | 86.8177 | 0 | 32.9907
2018-04-01 03:00 | 86.1845 | 86.7857 | 0 | 32.9786
2018-04-01 04:00 | 86.2455 | 86.833 | 0 | 32.9965
2018-04-01 05:00 | 86.2333 | 86.833 | 0 | 32.9965
2018-04-01 06:00 | 86.2776 | 86.8528 | 0 | 33.0041
2018-04-01 07:00 | 86.2867 | 86.8452 | 0 | 33.0012
2018-04-01 08:00 | 86.2989 | 86.9032 | 0 | 33.0232
2018-04-01 09:00 | 86.2867 | 86.8162 | 0 | 32.9902
2018-04-01 10:00 | 86.2882 | 86.8528 | 0 | 33.0041
2018-04-01 11:00 | 86.1845 | 86.743 | 0 | 32.9623
2018-04-01 12:00 | 86.1418 | 86.714 | 0 | 32.9513
2018-04-01 13:00 | 86.1479 | 86.7659 | 0 | 32.971
2018-04-01 14:00 | 86.1112 | 86.7018 | 0 | 32.9467
2018-04-01 15:00 | 86.2455 | 86.8482 | 0 | 33.0023
2018-04-01 16:00 | 86.3447 | 86.9398 | 0 | 33.0371
2018-04-01 17:00 | 86.4805 | 86.9856 | 0 | 33.0545
2018-04-01 18:00 | 86.4332 | 86.92 | 0 | 33.0296
2018-04-01 19:00 | 85.6794 | 85.9266 | 0 | 32.6521
2018-04-01 20:00 | 86.3294 | 86.5888 | 0 | 32.9037
2018-04-01 21:00 | 86.3569 | 86.6728 | 0 | 32.9357
2018-04-01 22:00 | 86.4881 | 86.8086 | 0 | 32.9873
2018-04-01 23:00 | 86.4332 | 86.7353 | 0 | 32.9594
2018-04-02 | 86.4088 | 86.7002 | 86.9352 | 65.9815
2018-04-02 01:00 | 86.0426 | 86.3127 | 86.5278 | 65.6794
2018-04-02 02:00 | 86.392 | 86.6392 | 86.8421 | 65.9229
2018-04-02 03:00 | 86.2776 | 86.5766 | 86.7536 | 65.8655
2018-04-02 04:00 | 86.5034 | 86.8849 | 87.0283 | 66.087
2018-04-02 05:00 | 86.3661 | 86.772 | 87.0054 | 66.0354
2018-04-02 06:00 | 86.2898 | 86.6499 | 86.8147 | 65.9165
2018-04-02 07:00 | 86.2043 | 86.5278 | 86.7079 | 65.8296
2018-04-02 08:00 | 86.3355 | 86.5461 | 86.8025 | 65.8725
2018-04-02 09:00 | 86.3798 | 86.7262 | 86.8711 | 65.967
2018-04-02 10:00 | 86.2272 | 86.5156 | 86.714 | 65.8272
2018-04-02 11:00 | 86.2119 | 86.5141 | 86.7201 | 65.829
2018-04-02 12:00 | 86.389 | 86.6835 | 86.8574 | 65.9455
2018-04-02 13:00 | 86.4027 | 86.6224 | 86.7475 | 65.8806
2018-04-02 14:00 | 86.3783 | 86.6606 | 86.7903 | 65.9113
2018-04-02 15:00 | 86.3355 | 86.5248 | 86.7384 | 65.84
2018-04-02 16:00 | 86.3493 | 86.4912 | 86.685 | 65.807
2018-04-02 17:00 | 86.244 | 86.4683 | 86.6743 | 65.7942
2018-04-02 18:00 | 86.3142 | 86.4378 | 86.5934 | 65.7519
2018-04-02 19:00 | 86.2089 | 86.3508 | 86.5583 | 65.7055
2018-04-02 20:00 | 86.2181 | 86.4836 | 86.6896 | 65.8058
2018-04-02 21:00 | 86.1494 | 86.4759 | 86.63 | 65.7802
2018-04-02 22:00 | 86.2593 | 86.5522 | 86.6468 | 65.8156
2018-04-02 23:00 | 86.4424 | 86.8055 | 86.8864 | 66.0029
2018-04-03 | 86.4637 | 0 | 0 | 0
2018-04-03 01:00 | 86.5629 | 0 | 0 | 0
2018-04-03 02:00 | 86.3706 | 0 | 0 | 0
2018-04-03 03:00 | 86.3523 | 0 | 0 | 0
2018-04-03 04:00 | 86.3676 | 0 | 0 | 0
2018-04-03 05:00 | 86.4027 | 0 | 0 | 0
2018-04-03 06:00 | 86.4652 | 0 | 0 | 0
2018-04-03 07:00 | 86.4012 | 0 | 0 | 0
2018-04-03 08:00 | 86.4515 | 0 | 0 | 0
2018-04-03 09:00 | 86.2028 | 0 | 0 | 0
2018-04-03 10:00 | 86.2715 | 0 | 0 | 0
2018-04-03 11:00 | 86.7567 | 0 | 0 | 0
2018-04-03 12:00 | 86.6194 | 0 | 0 | 0
2018-04-03 13:00 | 86.6377 | 0 | 0 | 0
2018-04-03 14:00 | 86.8757 | 0 | 0 | 0
2018-04-03 15:00 | 86.7994 | 0 | 0 | 0
2018-04-03 16:00 | 86.7674 | 0 | 0 | 0
2018-04-03 17:00 | 86.7384 | 0 | 0 | 0
2018-04-03 18:00 | 86.7124 | 0 | 0 | 0
2018-04-03 19:00 | 86.8376 | 0 | 0 | 0
2018-04-03 20:00 | 86.627 | 0 | 0 | 0
2018-04-03 21:00 | 86.6239 | 0 | 0 | 0
2018-04-03 22:00 | 86.714 | 0 | 0 | 0
2018-04-03 23:00 | 86.8971 | 0 | 0 | 0
2018-04-04 | 0 | 0 | 86.6712 | 32.9351
2018-04-04 01:00 | 0 | 0 | 86.511 | 32.8742
2018-04-04 02:00 | 0 | 0 | 86.7628 | 32.9699
2018-04-04 03:00 | 0 | 0 | 86.7384 | 32.9606
2018-04-04 04:00 | 0 | 0 | 86.8376 | 32.9983
2018-04-04 05:00 | 0 | 0 | 87.0222 | 33.0684
2018-04-04 06:00 | 0 | 0 | 86.9627 | 33.0458
2018-04-04 07:00 | 0 | 0 | 87.1321 | 33.1102
2018-04-04 08:00 | 0 | 0 | 87.1931 | 33.1334
2018-04-04 09:00 | 0 | 0 | 86.7155 | 32.9519
2018-04-04 10:00 | 0 | 0 | 86.6743 | 32.9362
2018-04-04 11:00 | 0 | 0 | 86.8956 | 33.0203
2018-04-04 12:00 | 0 | 0 | 86.9276 | 33.0325
2018-04-04 13:00 | 0 | 0 | 87.2541 | 33.1566
2018-04-04 14:00 | 0 | 0 | 87.4037 | 33.2134
2018-04-04 15:00 | 0 | 0 | 87.2129 | 33.1409
2018-04-04 16:00 | 0 | 0 | 86.9718 | 33.0493
2018-04-04 17:00 | 0 | 0 | 87.1397 | 33.1131
2018-04-04 18:00 | 0 | 0 | 87.2435 | 33.1525
2018-04-04 19:00 | 0 | 0 | 86.8894 | 33.018
2018-04-04 20:00 | 0 | 0 | 87.1839 | 33.1299
2018-04-04 21:00 | 0 | 0 | 87.2419 | 33.1519
2018-04-04 22:00 | 0 | 0 | 87.1733 | 33.1259
2018-04-04 23:00 | 0 | 0 | 87.2557 | 33.1572
2018-04-05 | 86.5492 | 0 | 0 | 0
2018-04-05 01:00 | 86.7201 | 0 | 0 | 0
2018-04-05 02:00 | 86.5095 | 0 | 0 | 0
2018-04-05 03:00 | 86.4576 | 0 | 0 | 0
2018-04-05 04:00 | 86.6316 | 0 | 0 | 0
2018-04-05 05:00 | 86.569 | 0 | 0 | 0
2018-04-05 06:00 | 86.6468 | 0 | 0 | 0
2018-04-05 07:00 | 86.6361 | 0 | 0 | 0
2018-04-05 08:00 | 86.6819 | 0 | 0 | 0
2018-04-05 09:00 | 86.7094 | 0 | 0 | 0
2018-04-05 10:00 | 86.7933 | 0 | 0 | 0
2018-04-05 11:00 | 86.8009 | 0 | 0 | 0
2018-04-05 12:00 | 86.6728 | 0 | 0 | 0
2018-04-05 13:00 | 86.6316 | 0 | 0 | 0
2018-04-05 14:00 | 86.6316 | 0 | 0 | 0
2018-04-05 15:00 | 86.6636 | 0 | 0 | 0
2018-04-05 16:00 | 86.5568 | 0 | 0 | 0
2018-04-05 17:00 | 86.6865 | 0 | 0 | 0
2018-04-05 18:00 | 86.7262 | 0 | 0 | 0
2018-04-05 19:00 | 86.5187 | 0 | 0 | 0
2018-04-05 20:00 | 86.5766 | 0 | 0 | 0
2018-04-05 21:00 | 86.6194 | 0 | 0 | 0
2018-04-05 22:00 | 86.6743 | 0 | 0 | 0
2018-04-05 23:00 | 86.5644 | 0 | 0 | 0
2018-04-06 | 86.2226 | 86.688 | 0 | 32.9414
2018-04-06 01:00 | 86.1128 | 86.5232 | 0 | 32.8788
2018-04-06 02:00 | 86.2791 | 86.6896 | 0 | 32.942
2018-04-06 03:00 | 86.0014 | 86.4485 | 0 | 32.8504
2018-04-06 04:00 | 86.0533 | 86.4347 | 0 | 32.8452
2018-04-06 05:00 | 86.2257 | 86.6117 | 0 | 32.9124
2018-04-06 06:00 | 86.4332 | 86.9352 | 0 | 33.0354
2018-04-06 07:00 | 86.5873 | 87.0619 | 0 | 33.0835
2018-04-06 08:00 | 86.3691 | 86.7811 | 0 | 32.9768
2018-04-06 09:00 | 86.334 | 86.7399 | 0 | 32.9612
2018-04-06 10:00 | 86.5126 | 86.862 | 0 | 33.0076
2018-04-06 11:00 | 86.5003 | 86.9306 | 0 | 33.0336
2018-04-06 12:00 | 86.7002 | 87.1412 | 0 | 33.1137
2018-04-06 13:00 | 86.363 | 86.8009 | 0 | 32.9843
2018-04-06 14:00 | 86.4408 | 86.8635 | 0 | 33.0081
2018-04-06 15:00 | 86.2943 | 86.6743 | 0 | 32.9362
2018-04-06 16:00 | 86.3706 | 86.7491 | 0 | 32.9647
2018-04-06 17:00 | 86.2882 | 86.7445 | 0 | 32.9629
2018-04-06 18:00 | 86.1875 | 86.6667 | 0 | 32.9333
2018-04-06 19:00 | 86.099 | 86.5431 | 0 | 32.8864
2018-04-06 20:00 | 86.1997 | 86.5187 | 0 | 32.8771
2018-04-06 21:00 | 86.3767 | 86.7247 | 0 | 32.9554
2018-04-06 22:00 | 86.3691 | 86.7659 | 0 | 32.971
2018-04-06 23:00 | 86.4012 | 86.7918 | 0 | 32.9809
2018-04-07 | 86.0121 | 0 | 86.5507 | 32.8893
2018-04-07 01:00 | 85.919 | 0 | 86.5324 | 32.8823
2018-04-07 02:00 | 86.0533 | 0 | 86.6453 | 32.9252
2018-04-07 03:00 | 86.1677 | 0 | 86.7002 | 32.9461
2018-04-07 04:00 | 86.3081 | 0 | 86.8513 | 33.0035
2018-04-07 05:00 | 86.2562 | 0 | 86.8605 | 33.007
2018-04-07 06:00 | 86.1234 | 0 | 86.6682 | 32.9339
2018-04-07 07:00 | 86.1906 | 0 | 86.7247 | 32.9554
2018-04-07 08:00 | 86.36 | 0 | 86.952 | 33.0418
2018-04-07 09:00 | 86.4912 | 0 | 87.0588 | 33.0823
2018-04-07 10:00 | 86.1982 | 0 | 86.6392 | 32.9229
2018-04-07 11:00 | 86.1707 | 0 | 86.8849 | 33.0163
2018-04-07 12:00 | 86.5019 | 0 | 87.1504 | 33.1172
2018-04-07 13:00 | 86.6148 | 0 | 87.3167 | 33.1803
2018-04-07 14:00 | 86.4439 | 0 | 87.0832 | 33.0916
2018-04-07 15:00 | 86.5522 | 0 | 87.2938 | 33.1716
2018-04-07 16:00 | 86.5644 | 0 | 87.3579 | 33.196
2018-04-07 17:00 | 86.7445 | 0 | 87.57 | 33.2766
2018-04-07 18:00 | 86.4668 | 0 | 87.3014 | 33.1745
2018-04-07 19:00 | 86.3661 | 0 | 87.0954 | 33.0963
2018-04-07 20:00 | 86.1173 | 0 | 86.891 | 33.0186
2018-04-07 21:00 | 86.1555 | 0 | 86.9245 | 33.0313
2018-04-07 22:00 | 86.2211 | 0 | 87.0054 | 33.0621
2018-04-07 23:00 | 86.2226 | 0 | 87.0787 | 33.0899
2018-04-08 | 86.2364 | 86.7994 | 0 | 32.9838
2018-04-08 01:00 | 86.3188 | 86.952 | 0 | 33.0418
2018-04-08 02:00 | 86.2119 | 86.8177 | 0 | 32.9907
2018-04-08 03:00 | 86.1845 | 86.7857 | 0 | 32.9786
2018-04-08 04:00 | 86.2455 | 86.833 | 0 | 32.9965
2018-04-08 05:00 | 86.2333 | 86.833 | 0 | 32.9965
2018-04-08 06:00 | 86.2776 | 86.8528 | 0 | 33.0041
2018-04-08 07:00 | 86.2867 | 86.8452 | 0 | 33.0012
2018-04-08 08:00 | 86.2989 | 86.9032 | 0 | 33.0232
2018-04-08 09:00 | 86.2867 | 86.8162 | 0 | 32.9902
2018-04-08 10:00 | 86.2882 | 86.8528 | 0 | 33.0041
2018-04-08 11:00 | 86.1845 | 86.743 | 0 | 32.9623
2018-04-08 12:00 | 86.1418 | 86.714 | 0 | 32.9513
2018-04-08 13:00 | 86.1479 | 86.7659 | 0 | 32.971
2018-04-08 14:00 | 86.1112 | 86.7018 | 0 | 32.9467
2018-04-08 15:00 | 86.2455 | 86.8482 | 0 | 33.0023
2018-04-08 16:00 | 86.3447 | 86.9398 | 0 | 33.0371
2018-04-08 17:00 | 86.4805 | 86.9856 | 0 | 33.0545
2018-04-08 18:00 | 86.4332 | 86.92 | 0 | 33.0296
2018-04-08 19:00 | 85.6794 | 85.9266 | 0 | 32.6521
2018-04-08 20:00 | 86.3294 | 86.5888 | 0 | 32.9037
2018-04-08 21:00 | 86.3569 | 86.6728 | 0 | 32.9357
2018-04-08 22:00 | 86.4881 | 86.8086 | 0 | 32.9873
2018-04-08 23:00 | 86.4332 | 86.7353 | 0 | 32.9594
2018-04-09 | 86.4088 | 86.7002 | 86.9352 | 65.9815
2018-04-09 01:00 | 86.0426 | 86.3127 | 86.5278 | 65.6794
2018-04-09 02:00 | 86.392 | 86.6392 | 86.8421 | 65.9229
2018-04-09 03:00 | 86.2776 | 86.5766 | 86.7536 | 65.8655
2018-04-09 04:00 | 86.5034 | 86.8849 | 87.0283 | 66.087
2018-04-09 05:00 | 86.3661 | 86.772 | 87.0054 | 66.0354
2018-04-09 06:00 | 86.2898 | 86.6499 | 86.8147 | 65.9165
2018-04-09 07:00 | 86.2043 | 86.5278 | 86.7079 | 65.8296
2018-04-09 08:00 | 86.3355 | 86.5461 | 86.8025 | 65.8725
2018-04-09 09:00 | 86.3798 | 86.7262 | 86.8711 | 65.967
2018-04-09 10:00 | 86.2272 | 86.5156 | 86.714 | 65.8272
2018-04-09 11:00 | 86.2119 | 86.5141 | 86.7201 | 65.829
2018-04-09 12:00 | 86.389 | 86.6835 | 86.8574 | 65.9455
2018-04-09 13:00 | 86.4027 | 86.6224 | 86.7475 | 65.8806
2018-04-09 14:00 | 86.3783 | 86.6606 | 86.7903 | 65.9113
2018-04-09 15:00 | 86.3355 | 86.5248 | 86.7384 | 65.84
2018-04-09 16:00 | 86.3493 | 86.4912 | 86.685 | 65.807
2018-04-09 17:00 | 86.244 | 86.4683 | 86.6743 | 65.7942
2018-04-09 18:00 | 86.3142 | 86.4378 | 86.5934 | 65.7519
2018-04-09 19:00 | 86.2089 | 86.3508 | 86.5583 | 65.7055
2018-04-09 20:00 | 86.2181 | 86.4836 | 86.6896 | 65.8058
2018-04-09 21:00 | 86.1494 | 86.4759 | 86.63 | 65.7802
2018-04-09 22:00 | 86.2593 | 86.5522 | 86.6468 | 65.8156
2018-04-09 23:00 | 86.4424 | 86.8055 | 86.8864 | 66.0029
2018-04-10 | 86.4637 | 0 | 0 | 0
2018-04-10 01:00 | 86.5629 | 0 | 0 | 0
2018-04-10 02:00 | 86.3706 | 0 | 0 | 0
2018-04-10 03:00 | 86.3523 | 0 | 0 | 0
2018-04-10 04:00 | 86.3676 | 0 | 0 | 0
2018-04-10 05:00 | 86.4027 | 0 | 0 | 0
2018-04-10 06:00 | 86.4652 | 0 | 0 | 0
2018-04-10 07:00 | 86.4012 | 0 | 0 | 0
2018-04-10 08:00 | 86.4515 | 0 | 0 | 0
2018-04-10 09:00 | 86.2028 | 0 | 0 | 0
2018-04-10 10:00 | 86.2715 | 0 | 0 | 0
2018-04-10 11:00 | 86.7567 | 0 | 0 | 0
2018-04-10 12:00 | 86.6194 | 0 | 0 | 0
2018-04-10 13:00 | 86.6377 | 0 | 0 | 0
2018-04-10 14:00 | 86.8757 | 0 | 0 | 0
2018-04-10 15:00 | 86.7994 | 0 | 0 | 0
2018-04-10 16:00 | 86.7674 | 0 | 0 | 0
2018-04-10 17:00 | 86.7384 | 0 | 0 | 0
2018-04-10 18:00 | 86.7124 | 0 | 0 | 0
2018-04-10 19:00 | 86.8376 | 0 | 0 | 0
2018-04-10 20:00 | 86.627 | 0 | 0 | 0
2018-04-10 21:00 | 86.6239 | 0 | 0 | 0
2018-04-10 22:00 | 86.714 | 0 | 0 | 0
2018-04-10 23:00 | 86.8971 | 0 | 0 | 0
2018-04-11 | 0 | 0 | 86.6712 | 32.9351
2018-04-11 01:00 | 0 | 0 | 86.511 | 32.8742
2018-04-11 02:00 | 0 | 0 | 86.7628 | 32.9699
2018-04-11 03:00 | 0 | 0 | 86.7384 | 32.9606
2018-04-11 04:00 | 0 | 0 | 86.8376 | 32.9983
2018-04-11 05:00 | 0 | 0 | 87.0222 | 33.0684
2018-04-11 06:00 | 0 | 0 | 86.9627 | 33.0458
2018-04-11 07:00 | 0 | 0 | 87.1321 | 33.1102
2018-04-11 08:00 | 0 | 0 | 87.1931 | 33.1334
2018-04-11 09:00 | 0 | 0 | 86.7155 | 32.9519
2018-04-11 10:00 | 0 | 0 | 86.6743 | 32.9362
2018-04-11 11:00 | 0 | 0 | 86.8956 | 33.0203
2018-04-11 12:00 | 0 | 0 | 86.9276 | 33.0325
2018-04-11 13:00 | 0 | 0 | 87.2541 | 33.1566
2018-04-11 14:00 | 0 | 0 | 87.4037 | 33.2134
2018-04-11 15:00 | 0 | 0 | 87.2129 | 33.1409
2018-04-11 16:00 | 0 | 0 | 86.9718 | 33.0493
2018-04-11 17:00 | 0 | 0 | 87.1397 | 33.1131
2018-04-11 18:00 | 0 | 0 | 87.2435 | 33.1525
2018-04-11 19:00 | 0 | 0 | 86.8894 | 33.018
2018-04-11 20:00 | 0 | 0 | 87.1839 | 33.1299
2018-04-11 21:00 | 0 | 0 | 87.2419 | 33.1519
2018-04-11 22:00 | 0 | 0 | 87.1733 | 33.1259
2018-04-11 23:00 | 0 | 0 | 87.2557 | 33.1572
2018-04-12 | 86.5492 | 0 | 0 | 0
2018-04-12 01:00 | 86.7201 | 0 | 0 | 0
2018-04-12 02:00 | 86.5095 | 0 | 0 | 0
2018-04-12 03:00 | 86.4576 | 0 | 0 | 0
2018-04-12 04:00 | 86.6316 | 0 | 0 | 0
2018-04-12 05:00 | 86.569 | 0 | 0 | 0
2018-04-12 06:00 | 86.6468 | 0 | 0 | 0
2018-04-12 07:00 | 86.6361 | 0 | 0 | 0
2018-04-12 08:00 | 86.6819 | 0 | 0 | 0
2018-04-12 09:00 | 86.7094 | 0 | 0 | 0
2018-04-12 10:00 | 86.7933 | 0 | 0 | 0
2018-04-12 11:00 | 86.8009 | 0 | 0 | 0
2018-04-12 12:00 | 86.6728 | 0 | 0 | 0
2018-04-12 13:00 | 86.6316 | 0 | 0 | 0
2018-04-12 14:00 | 86.6316 | 0 | 0 | 0
2018-04-12 15:00 | 86.6636 | 0 | 0 | 0
2018-04-12 16:00 | 86.5568 | 0 | 0 | 0
2018-04-12 17:00 | 86.6865 | 0 | 0 | 0
2018-04-12 18:00 | 86.7262 | 0 | 0 | 0
2018-04-12 19:00 | 86.5187 | 0 | 0 | 0
2018-04-12 20:00 | 86.5766 | 0 | 0 | 0
2018-04-12 21:00 | 86.6194 | 0 | 0 | 0
2018-04-12 22:00 | 86.6743 | 0 | 0 | 0
2018-04-12 23:00 | 86.5644 | 0 | 0 | 0
2018-04-13 | 86.2226 | 86.688 | 0 | 32.9414
2018-04-13 01:00 | 86.1128 | 86.5232 | 0 | 32.8788
2018-04-13 02:00 | 86.2791 | 86.6896 | 0 | 32.942
2018-04-13 03:00 | 86.0014 | 86.4485 | 0 | 32.8504
2018-04-13 04:00 | 86.0533 | 86.4347 | 0 | 32.8452
2018-04-13 05:00 | 86.2257 | 86.6117 | 0 | 32.9124
2018-04-13 06:00 | 86.4332 | 86.9352 | 0 | 33.0354
2018-04-13 07:00 | 86.5873 | 87.0619 | 0 | 33.0835
2018-04-13 08:00 | 86.3691 | 86.7811 | 0 | 32.9768
2018-04-13 09:00 | 86.334 | 86.7399 | 0 | 32.9612
2018-04-13 10:00 | 86.5126 | 86.862 | 0 | 33.0076
2018-04-13 11:00 | 86.5003 | 86.9306 | 0 | 33.0336
2018-04-13 12:00 | 86.7002 | 87.1412 | 0 | 33.1137
2018-04-13 13:00 | 86.363 | 86.8009 | 0 | 32.9843
2018-04-13 14:00 | 86.4408 | 86.8635 | 0 | 33.0081
2018-04-13 15:00 | 86.2943 | 86.6743 | 0 | 32.9362
2018-04-13 16:00 | 86.3706 | 86.7491 | 0 | 32.9647
2018-04-13 17:00 | 86.2882 | 86.7445 | 0 | 32.9629
2018-04-13 18:00 | 86.1875 | 86.6667 | 0 | 32.9333
2018-04-13 19:00 | 86.099 | 86.5431 | 0 | 32.8864
2018-04-13 20:00 | 86.1997 | 86.5187 | 0 | 32.8771
2018-04-13 21:00 | 86.3767 | 86.7247 | 0 | 32.9554
2018-04-13 22:00 | 86.3691 | 86.7659 | 0 | 32.971
2018-04-13 23:00 | 86.4012 | 86.7918 | 0 | 32.9809
2018-04-14 | 86.0121 | 0 | 86.5507 | 32.8893
2018-04-14 01:00 | 85.919 | 0 | 86.5324 | 32.8823
2018-04-14 02:00 | 86.0533 | 0 | 86.6453 | 32.9252
2018-04-14 03:00 | 86.1677 | 0 | 86.7002 | 32.9461
2018-04-14 04:00 | 86.3081 | 0 | 86.8513 | 33.0035
2018-04-14 05:00 | 86.2562 | 0 | 86.8605 | 33.007
2018-04-14 06:00 | 86.1234 | 0 | 86.6682 | 32.9339
2018-04-14 07:00 | 86.1906 | 0 | 86.7247 | 32.9554
2018-04-14 08:00 | 86.36 | 0 | 86.952 | 33.0418
2018-04-14 09:00 | 86.4912 | 0 | 87.0588 | 33.0823
2018-04-14 10:00 | 86.1982 | 0 | 86.6392 | 32.9229
2018-04-14 11:00 | 86.1707 | 0 | 86.8849 | 33.0163
2018-04-14 12:00 | 86.5019 | 0 | 87.1504 | 33.1172
2018-04-14 13:00 | 86.6148 | 0 | 87.3167 | 33.1803
2018-04-14 14:00 | 86.4439 | 0 | 87.0832 | 33.0916
2018-04-14 15:00 | 86.5522 | 0 | 87.2938 | 33.1716
2018-04-14 16:00 | 86.5644 | 0 | 87.3579 | 33.196
2018-04-14 17:00 | 86.7445 | 0 | 87.57 | 33.2766
2018-04-14 18:00 | 86.4668 | 0 | 87.3014 | 33.1745
2018-04-14 19:00 | 86.3661 | 0 | 87.0954 | 33.0963
2018-04-14 20:00 | 86.1173 | 0 | 86.891 | 33.0186
2018-04-14 21:00 | 86.1555 | 0 | 86.9245 | 33.0313
2018-04-14 22:00 | 86.2211 | 0 | 87.0054 | 33.0621
2018-04-14 23:00 | 86.2226 | 0 | 87.0787 | 33.0899
2018-04-15 | 86.2364 | 86.7994 | 0 | 32.9838
2018-04-15 01:00 | 86.3188 | 86.952 | 0 | 33.0418
2018-04-15 02:00 | 86.2119 | 86.8177 | 0 | 32.9907
2018-04-15 03:00 | 86.1845 | 86.7857 | 0 | 32.9786
2018-04-15 04:00 | 86.2455 | 86.833 | 0 | 32.9965
2018-04-15 05:00 | 86.2333 | 86.833 | 0 | 32.9965
2018-04-15 06:00 | 86.2776 | 86.8528 | 0 | 33.0041
2018-04-15 07:00 | 86.2867 | 86.8452 | 0 | 33.0012
2018-04-15 08:00 | 86.2989 | 86.9032 | 0 | 33.0232
2018-04-15 09:00 | 86.2867 | 86.8162 | 0 | 32.9902
2018-04-15 10:00 | 86.2882 | 86.8528 | 0 | 33.0041
2018-04-15 11:00 | 86.1845 | 86.743 | 0 | 32.9623
2018-04-15 12:00 | 86.1418 | 86.714 | 0 | 32.9513
2018-04-15 13:00 | 86.1479 | 86.7659 | 0 | 32.971
2018-04-15 14:00 | 86.1112 | 86.7018 | 0 | 32.9467
2018-04-15 15:00 | 86.2455 | 86.8482 | 0 | 33.0023
2018-04-15 16:00 | 86.3447 | 86.9398 | 0 | 33.0371
2018-04-15 17:00 | 86.4805 | 86.9856 | 0 | 33.0545
2018-04-15 18:00 | 86.4332 | 86.92 | 0 | 33.0296
2018-04-15 19:00 | 85.6794 | 85.9266 | 0 | 32.6521
2018-04-15 20:00 | 86.3294 | 86.5888 | 0 | 32.9037
2018-04-15 21:00 | 86.3569 | 86.6728 | 0 | 32.9357
2018-04-15 22:00 | 86.4881 | 86.8086 | 0 | 32.9873
2018-04-15 23:00 | 86.4332 | 86.7353 | 0 | 32.9594
2018-04-16 | 86.4088 | 86.7002 | 86.9352 | 65.9815
2018-04-16 01:00 | 86.0426 | 86.3127 | 86.5278 | 65.6794
2018-04-16 02:00 | 86.392 | 86.6392 | 86.8421 | 65.9229
2018-04-16 03:00 | 86.2776 | 86.5766 | 86.7536 | 65.8655
2018-04-16 04:00 | 86.5034 | 86.8849 | 87.0283 | 66.087
2018-04-16 05:00 | 86.3661 | 86.772 | 87.0054 | 66.0354
2018-04-16 06:00 | 86.2898 | 86.6499 | 86.8147 | 65.9165
2018-04-16 07:00 | 86.2043 | 86.5278 | 86.7079 | 65.8296
2018-04-16 08:00 | 86.3355 | 86.5461 | 86.8025 | 65.8725
2018-04-16 09:00 | 86.3798 | 86.7262 | 86.8711 | 65.967
2018-04-16 10:00 | 86.2272 | 86.5156 | 86.714 | 65.8272
2018-04-16 11:00 | 86.2119 | 86.5141 | 86.7201 | 65.829
2018-04-16 12:00 | 86.389 | 86.6835 | 86.8574 | 65.9455
2018-04-16 13:00 | 86.4027 | 86.6224 | 86.7475 | 65.8806
2018-04-16 14:00 | 86.3783 | 86.6606 | 86.7903 | 65.9113
2018-04-16 15:00 | 86.3355 | 86.5248 | 86.7384 | 65.84
2018-04-16 16:00 | 86.3493 | 86.4912 | 86.685 | 65.807
2018-04-16 17:00 | 86.244 | 86.4683 | 86.6743 | 65.7942
2018-04-16 18:00 | 86.3142 | 86.4378 | 86.5934 | 65.7519
2018-04-16 19:00 | 86.2089 | 86.3508 | 86.5583 | 65.7055
2018-04-16 20:00 | 86.2181 | 86.4836 | 86.6896 | 65.8058
2018-04-16 21:00 | 86.1494 | 86.4759 | 86.63 | 65.7802
2018-04-16 22:00 | 86.2593 | 86.5522 | 86.6468 | 65.8156
2018-04-16 23:00 | 86.4424 | 86.8055 | 86.8864 | 66.0029
2018-04-17 | 86.4637 | 0 | 0 | 0
2018-04-17 01:00 | 86.5629 | 0 | 0 | 0
2018-04-17 02:00 | 86.3706 | 0 | 0 | 0
2018-04-17 03:00 | 86.3523 | 0 | 0 | 0
2018-04-17 04:00 | 86.3676 | 0 | 0 | 0
2018-04-17 05:00 | 86.4027 | 0 | 0 | 0
2018-04-17 06:00 | 86.4652 | 0 | 0 | 0
2018-04-17 07:00 | 86.4012 | 0 | 0 | 0
2018-04-17 08:00 | 86.4515 | 0 | 0 | 0
2018-04-17 09:00 | 86.2028 | 0 | 0 | 0
2018-04-17 10:00 | 86.2715 | 0 | 0 | 0
2018-04-17 11:00 | 86.7567 | 0 | 0 | 0
2018-04-17 12:00 | 86.6194 | 0 | 0 | 0
2018-04-17 13:00 | 86.6377 | 0 | 0 | 0
2018-04-17 14:00 | 86.8757 | 0 | 0 | 0
2018-04-17 15:00 | 86.7994 | 0 | 0 | 0
2018-04-17 16:00 | 86.7674 | 0 | 0 | 0
2018-04-17 17:00 | 86.7384 | 0 | 0 | 0
2018-04-17 18:00 | 86.7124 | 0 | 0 | 0
2018-04-17 19:00 | 86.8376 | 0 | 0 | 0
2018-04-17 20:00 | 86.627 | 0 | 0 | 0
2018-04-17 21:00 | 86.6239 | 0 | 0 | 0
2018-04-17 22:00 | 86.714 | 0 | 0 | 0
2018-04-17 23:00 | 86.8971 | 0 | 0 | 0
2018-04-18 | 0 | 0 | 86.6712 | 32.9351
2018-04-18 01:00 | 0 | 0 | 86.511 | 32.8742
2018-04-18 02:00 | 0 | 0 | 86.7628 | 32.9699
2018-04-18 03:00 | 0 | 0 | 86.7384 | 32.9606
2018-04-18 04:00 | 0 | 0 | 86.8376 | 32.9983
2018-04-18 05:00 | 0 | 0 | 87.0222 | 33.0684
2018-04-18 06:00 | 0 | 0 | 86.9627 | 33.0458
2018-04-18 07:00 | 0 | 0 | 87.1321 | 33.1102
2018-04-18 08:00 | 0 | 0 | 87.1931 | 33.1334
2018-04-18 09:00 | 0 | 0 | 86.7155 | 32.9519
2018-04-18 10:00 | 0 | 0 | 86.6743 | 32.9362
2018-04-18 11:00 | 0 | 0 | 86.8956 | 33.0203
2018-04-18 12:00 | 0 | 0 | 86.9276 | 33.0325
2018-04-18 13:00 | 0 | 0 | 87.2541 | 33.1566
2018-04-18 14:00 | 0 | 0 | 87.4037 | 33.2134
2018-04-18 15:00 | 0 | 0 | 87.2129 | 33.1409
2018-04-18 16:00 | 0 | 0 | 86.9718 | 33.0493
2018-04-18 17:00 | 0 | 0 | 87.1397 | 33.1131
2018-04-18 18:00 | 0 | 0 | 87.2435 | 33.1525
2018-04-18 19:00 | 0 | 0 | 86.8894 | 33.018
2018-04-18 20:00 | 0 | 0 | 87.1839 | 33.1299
2018-04-18 21:00 | 0 | 0 | 87.2419 | 33.1519
2018-04-18 22:00 | 0 | 0 | 87.1733 | 33.1259
2018-04-18 23:00 | 0 | 0 | 87.2557 | 33.1572
2018-04-19 | 86.5492 | 0 | 0 | 0
2018-04-19 01:00 | 86.7201 | 0 | 0 | 0
2018-04-19 02:00 | 86.5095 | 0 | 0 | 0
2018-04-19 03:00 | 86.4576 | 0 | 0 | 0
2018-04-19 04:00 | 86.6316 | 0 | 0 | 0
2018-04-19 05:00 | 86.569 | 0 | 0 | 0
2018-04-19 06:00 | 86.6468 | 0 | 0 | 0
2018-04-19 07:00 | 86.6361 | 0 | 0 | 0
2018-04-19 08:00 | 86.6819 | 0 | 0 | 0
2018-04-19 09:00 | 86.7094 | 0 | 0 | 0
2018-04-19 10:00 | 86.7933 | 0 | 0 | 0
2018-04-19 11:00 | 86.8009 | 0 | 0 | 0
2018-04-19 12:00 | 86.6728 | 0 | 0 | 0
2018-04-19 13:00 | 86.6316 | 0 | 0 | 0
2018-04-19 14:00 | 86.6316 | 0 | 0 | 0
2018-04-19 15:00 | 86.6636 | 0 | 0 | 0
2018-04-19 16:00 | 86.5568 | 0 | 0 | 0
2018-04-19 17:00 | 86.6865 | 0 | 0 | 0
2018-04-19 18:00 | 86.7262 | 0 | 0 | 0
2018-04-19 19:00 | 86.5187 | 0 | 0 | 0
2018-04-19 20:00 | 86.5766 | 0 | 0 | 0
2018-04-19 21:00 | 86.6194 | 0 | 0 | 0
2018-04-19 22:00 | 86.6743 | 0 | 0 | 0
2018-04-19 23:00 | 86.5644 | 0 | 0 | 0
2018-04-20 | 86.2226 | 86.688 | 0 | 32.9414
2018-04-20 01:00 | 86.1128 | 86.5232 | 0 | 32.8788
2018-04-20 02:00 | 86.2791 | 86.6896 | 0 | 32.942
2018-04-20 03:00 | 86.0014 | 86.4485 | 0 | 32.8504
2018-04-20 04:00 | 86.0533 | 86.4347 | 0 | 32.8452
2018-04-20 05:00 | 86.2257 | 86.6117 | 0 | 32.9124
2018-04-20 06:00 | 86.4332 | 86.9352 | 0 | 33.0354
2018-04-20 07:00 | 86.5873 | 87.0619 | 0 | 33.0835
2018-04-20 08:00 | 86.3691 | 86.7811 | 0 | 32.9768
2018-04-20 09:00 | 86.334 | 86.7399 | 0 | 32.9612
2018-04-20 10:00 | 86.5126 | 86.862 | 0 | 33.0076
2018-04-20 11:00 | 86.5003 | 86.9306 | 0 | 33.0336
2018-04-20 12:00 | 86.7002 | 87.1412 | 0 | 33.1137
2018-04-20 13:00 | 86.363 | 86.8009 | 0 | 32.9843
2018-04-20 14:00 | 86.4408 | 86.8635 | 0 | 33.0081
2018-04-20 15:00 | 86.2943 | 86.6743 | 0 | 32.9362
2018-04-20 16:00 | 86.3706 | 86.7491 | 0 | 32.9647
2018-04-20 17:00 | 86.2882 | 86.7445 | 0 | 32.9629
2018-04-20 18:00 | 86.1875 | 86.6667 | 0 | 32.9333
2018-04-20 19:00 | 86.099 | 86.5431 | 0 | 32.8864
2018-04-20 20:00 | 86.1997 | 86.5187 | 0 | 32.8771
2018-04-20 21:00 | 86.3767 | 86.7247 | 0 | 32.9554
2018-04-20 22:00 | 86.3691 | 86.7659 | 0 | 32.971
2018-04-20 23:00 | 86.4012 | 86.7918 | 0 | 32.9809
2018-04-21 | 86.0121 | 0 | 86.5507 | 32.8893
2018-04-21 01:00 | 85.919 | 0 | 86.5324 | 32.8823
2018-04-21 02:00 | 86.0533 | 0 | 86.6453 | 32.9252
2018-04-21 03:00 | 86.1677 | 0 | 86.7002 | 32.9461
2018-04-21 04:00 | 86.3081 | 0 | 86.8513 | 33.0035
2018-04-21 05:00 | 86.2562 | 0 | 86.8605 | 33.007
2018-04-21 06:00 | 86.1234 | 0 | 86.6682 | 32.9339
2018-04-21 07:00 | 86.1906 | 0 | 86.7247 | 32.9554
2018-04-21 08:00 | 86.36 | 0 | 86.952 | 33.0418
2018-04-21 09:00 | 86.4912 | 0 | 87.0588 | 33.0823
2018-04-21 10:00 | 86.1982 | 0 | 86.6392 | 32.9229
2018-04-21 11:00 | 86.1707 | 0 | 86.8849 | 33.0163
2018-04-21 12:00 | 86.5019 | 0 | 87.1504 | 33.1172
2018-04-21 13:00 | 86.6148 | 0 | 87.3167 | 33.1803
2018-04-21 14:00 | 86.4439 | 0 | 87.0832 | 33.0916
2018-04-21 15:00 | 86.5522 | 0 | 87.2938 | 33.1716
2018-04-21 16:00 | 86.5644 | 0 | 87.3579 | 33.196
2018-04-21 17:00 | 86.7445 | 0 | 87.57 | 33.2766
2018-04-21 18:00 | 86.4668 | 0 | 87.3014 | 33.1745
2018-04-21 19:00 | 86.3661 | 0 | 87.0954 | 33.0963
2018-04-21 20:00 | 86.1173 | 0 | 86.891 | 33.0186
2018-04-21 21:00 | 86.1555 | 0 | 86.9245 | 33.0313
2018-04-21 22:00 | 86.2211 | 0 | 87.0054 | 33.0621
2018-04-21 23:00 | 86.2226 | 0 | 87.0787 | 33.0899
2018-04-22 | 86.2364 | 86.7994 | 0 | 32.9838
2018-04-22 01:00 | 86.3188 | 86.952 | 0 | 33.0418
2018-04-22 02:00 | 86.2119 | 86.8177 | 0 | 32.9907
2018-04-22 03:00 | 86.1845 | 86.7857 | 0 | 32.9786
2018-04-22 04:00 | 86.2455 | 86.833 | 0 | 32.9965
2018-04-22 05:00 | 86.2333 | 86.833 | 0 | 32.9965
2018-04-22 06:00 | 86.2776 | 86.8528 | 0 | 33.0041
2018-04-22 07:00 | 86.2867 | 86.8452 | 0 | 33.0012
2018-04-22 08:00 | 86.2989 | 86.9032 | 0 | 33.0232
2018-04-22 09:00 | 86.2867 | 86.8162 | 0 | 32.9902
2018-04-22 10:00 | 86.2882 | 86.8528 | 0 | 33.0041
2018-04-22 11:00 | 86.1845 | 86.743 | 0 | 32.9623
2018-04-22 12:00 | 86.1418 | 86.714 | 0 | 32.9513
2018-04-22 13:00 | 86.1479 | 86.7659 | 0 | 32.971
2018-04-22 14:00 | 86.1112 | 86.7018 | 0 | 32.9467
2018-04-22 15:00 | 86.2455 | 86.8482 | 0 | 33.0023
2018-04-22 16:00 | 86.3447 | 86.9398 | 0 | 33.0371
2018-04-22 17:00 | 86.4805 | 86.9856 | 0 | 33.0545
2018-04-22 18:00 | 86.4332 | 86.92 | 0 | 33.0296
2018-04-22 19:00 | 85.6794 | 85.9266 | 0 | 32.6521
2018-04-22 20:00 | 86.3294 | 86.5888 | 0 | 32.9037
2018-04-22 21:00 | 86.3569 | 86.6728 | 0 | 32.9357
2018-04-22 22:00 | 86.4881 | 86.8086 | 0 | 32.9873
2018-04-22 23:00 | 86.4332 | 86.7353 | 0 | 32.9594
2018-04-23 | 86.4088 | 86.7002 | 86.9352 | 65.9815
2018-04-23 01:00 | 86.0426 | 86.3127 | 86.5278 | 65.6794
2018-04-23 02:00 | 86.392 | 86.6392 | 86.8421 | 65.9229
2018-04-23 03:00 | 86.2776 | 86.5766 | 86.7536 | 65.8655
2018-04-23 04:00 | 86.5034 | 86.8849 | 87.0283 | 66.087
2018-04-23 05:00 | 86.3661 | 86.772 | 87.0054 | 66.0354
2018-04-23 06:00 | 86.2898 | 86.6499 | 86.8147 | 65.9165
2018-04-23 07:00 | 86.2043 | 86.5278 | 86.7079 | 65.8296
2018-04-23 08:00 | 86.3355 | 86.5461 | 86.8025 | 65.8725
2018-04-23 09:00 | 86.3798 | 86.7262 | 86.8711 | 65.967
2018-04-23 10:00 | 86.2272 | 86.5156 | 86.714 | 65.8272
2018-04-23 11:00 | 86.2119 | 86.5141 | 86.7201 | 65.829
2018-04-23 12:00 | 86.389 | 86.6835 | 86.8574 | 65.9455
2018-04-23 13:00 | 86.4027 | 86.6224 | 86.7475 | 65.8806
2018-04-23 14:00 | 86.3783 | 86.6606 | 86.7903 | 65.9113
2018-04-23 15:00 | 86.3355 | 86.5248 | 86.7384 | 65.84
2018-04-23 16:00 | 86.3493 | 86.4912 | 86.685 | 65.807
2018-04-23 17:00 | 86.244 | 86.4683 | 86.6743 | 65.7942
2018-04-23 18:00 | 86.3142 | 86.4378 | 86.5934 | 65.7519
2018-04-23 19:00 | 86.2089 | 86.3508 | 86.5583 | 65.7055
2018-04-23 20:00 | 86.2181 | 86.4836 | 86.6896 | 65.8058
2018-04-23 21:00 | 86.1494 | 86.4759 | 86.63 | 65.7802
2018-04-23 22:00 | 86.2593 | 86.5522 | 86.6468 | 65.8156
2018-04-23 23:00 | 86.4424 | 86.8055 | 86.8864 | 66.0029
2018-04-24 | 86.4637 | 0 | 0 | 0
2018-04-24 01:00 | 86.5629 | 0 | 0 | 0
2018-04-24 02:00 | 86.3706 | 0 | 0 | 0
2018-04-24 03:00 | 86.3523 | 0 | 0 | 0
2018-04-24 04:00 | 86.3676 | 0 | 0 | 0
2018-04-24 05:00 | 86.4027 | 0 | 0 | 0
2018-04-24 06:00 | 86.4652 | 0 | 0 | 0
2018-04-24 07:00 | 86.4012 | 0 | 0 | 0
2018-04-24 08:00 | 86.4515 | 0 | 0 | 0
2018-04-24 09:00 | 86.2028 | 0 | 0 | 0
2018-04-24 10:00 | 86.2715 | 0 | 0 | 0
2018-04-24 11:00 | 86.7567 | 0 | 0 | 0
2018-04-24 12:00 | 86.6194 | 0 | 0 | 0
2018-04-24 13:00 | 86.6377 | 0 | 0 | 0
2018-04-24 14:00 | 86.8757 | 0 | 0 | 0
2018-04-24 15:00 | 86.7994 | 0 | 0 | 0
2018-04-24 16:00 | 86.7674 | 0 | 0 | 0
2018-04-24 17:00 | 86.7384 | 0 | 0 | 0
2018-04-24 18:00 | 86.7124 | 0 | 0 | 0
2018-04-24 19:00 | 86.8376 | 0 | 0 | 0
2018-04-24 20:00 | 86.627 | 0 | 0 | 0
2018-04-24 21:00 | 86.6239 | 0 | 0 | 0
2018-04-24 22:00 | 86.714 | 0 | 0 | 0
2018-04-24 23:00 | 86.8971 | 0 | 0 | 0
2018-04-25 | 0 | 0 | 86.6712 | 32.9351
2018-04-25 01:00 | 0 | 0 | 86.511 | 32.8742
2018-04-25 02:00 | 0 | 0 | 86.7628 | 32.9699
2018-04-25 03:00 | 0 | 0 | 86.7384 | 32.9606
2018-04-25 04:00 | 0 | 0 | 86.8376 | 32.9983
2018-04-25 05:00 | 0 | 0 | 87.0222 | 33.0684
2018-04-25 06:00 | 0 | 0 | 86.9627 | 33.0458
2018-04-25 07:00 | 0 | 0 | 87.1321 | 33.1102
2018-04-25 08:00 | 0 | 0 | 87.1931 | 33.1334
2018-04-25 09:00 | 0 | 0 | 86.7155 | 32.9519
2018-04-25 10:00 | 0 | 0 | 86.6743 | 32.9362
2018-04-25 11:00 | 0 | 0 | 86.8956 | 33.0203
2018-04-25 12:00 | 0 | 0 | 86.9276 | 33.0325
2018-04-25 13:00 | 0 | 0 | 87.2541 | 33.1566
2018-04-25 14:00 | 0 | 0 | 87.4037 | 33.2134
2018-04-25 15:00 | 0 | 0 | 87.2129 | 33.1409
2018-04-25 16:00 | 0 | 0 | 86.9718 | 33.0493
2018-04-25 17:00 | 0 | 0 | 87.1397 | 33.1131
2018-04-25 18:00 | 0 | 0 | 87.2435 | 33.1525
2018-04-25 19:00 | 0 | 0 | 86.8894 | 33.018
2018-04-25 20:00 | 0 | 0 | 87.1839 | 33.1299
2018-04-25 21:00 | 0 | 0 | 87.2419 | 33.1519
2018-04-25 22:00 | 0 | 0 | 87.1733 | 33.1259
2018-04-25 23:00 | 0 | 0 | 87.2557 | 33.1572
2018-04-26 | 86.5492 | 0 | 0 | 0
2018-04-26 01:00 | 86.7201 | 0 | 0 | 0
2018-04-26 02:00 | 86.5095 | 0 | 0 | 0
2018-04-26 03:00 | 86.4576 | 0 | 0 | 0
2018-04-26 04:00 | 86.6316 | 0 | 0 | 0
2018-04-26 05:00 | 86.569 | 0 | 0 | 0
2018-04-26 06:00 | 86.6468 | 0 | 0 | 0
2018-04-26 07:00 | 86.6361 | 0 | 0 | 0
2018-04-26 08:00 | 86.6819 | 0 | 0 | 0
2018-04-26 09:00 | 86.7094 | 0 | 0 | 0
2018-04-26 10:00 | 86.7933 | 0 | 0 | 0
2018-04-26 11:00 | 86.8009 | 0 | 0 | 0
2018-04-26 12:00 | 86.6728 | 0 | 0 | 0
2018-04-26 13:00 | 86.6316 | 0 | 0 | 0
2018-04-26 14:00 | 86.6316 | 0 | 0 | 0
2018-04-26 15:00 | 86.6636 | 0 | 0 | 0
2018-04-26 16:00 | 86.5568 | 0 | 0 | 0
2018-04-26 17:00 | 86.6865 | 0 | 0 | 0
2018-04-26 18:00 | 86.7262 | 0 | 0 | 0
2018-04-26 19:00 | 86.5187 | 0 | 0 | 0
2018-04-26 20:00 | 86.5766 | 0 | 0 | 0
2018-04-26 21:00 | 86.6194 | 0 | 0 | 0
2018-04-26 22:00 | 86.6743 | 0 | 0 | 0
2018-04-26 23:00 | 86.5644 | 0 | 0 | 0
2018-04-27 | 86.2226 | 86.688 | 0 | 32.9414
2018-04-27 01:00 | 86.1128 | 86.5232 | 0 | 32.8788
2018-04-27 02:00 | 86.2791 | 86.6896 | 0 | 32.942
2018-04-27 03:00 | 86.0014 | 86.4485 | 0 | 32.8504
2018-04-27 04:00 | 86.0533 | 86.4347 | 0 | 32.8452
2018-04-27 05:00 | 86.2257 | 86.6117 | 0 | 32.9124
2018-04-27 06:00 | 86.4332 | 86.9352 | 0 | 33.0354
2018-04-27 07:00 | 86.5873 | 87.0619 | 0 | 33.0835
2018-04-27 08:00 | 86.3691 | 86.7811 | 0 | 32.9768
2018-04-27 09:00 | 86.334 | 86.7399 | 0 | 32.9612
2018-04-27 10:00 | 86.5126 | 86.862 | 0 | 33.0076
2018-04-27 11:00 | 86.5003 | 86.9306 | 0 | 33.0336
2018-04-27 12:00 | 86.7002 | 87.1412 | 0 | 33.1137
2018-04-27 13:00 | 86.363 | 86.8009 | 0 | 32.9843
2018-04-27 14:00 | 86.4408 | 86.8635 | 0 | 33.0081
2018-04-27 15:00 | 86.2943 | 86.6743 | 0 | 32.9362
2018-04-27 16:00 | 86.3706 | 86.7491 | 0 | 32.9647
2018-04-27 17:00 | 86.2882 | 86.7445 | 0 | 32.9629
2018-04-27 18:00 | 86.1875 | 86.6667 | 0 | 32.9333
2018-04-27 19:00 | 86.099 | 86.5431 | 0 | 32.8864
2018-04-27 20:00 | 86.1997 | 86.5187 | 0 | 32.8771
2018-04-27 21:00 | 86.3767 | 86.7247 | 0 | 32.9554
2018-04-27 22:00 | 86.3691 | 86.7659 | 0 | 32.971
2018-04-27 23:00 | 86.4012 | 86.7918 | 0 | 32.9809
2018-04-28 | 86.0121 | 0 | 86.5507 | 32.8893
2018-04-28 01:00 | 85.919 | 0 | 86.5324 | 32.8823
2018-04-28 02:00 | 86.0533 | 0 | 86.6453 | 32.9252
2018-04-28 03:00 | 86.1677 | 0 | 86.7002 | 32.9461
2018-04-28 04:00 | 86.3081 | 0 | 86.8513 | 33.0035
2018-04-28 05:00 | 86.2562 | 0 | 86.8605 | 33.007
2018-04-28 06:00 | 86.1234 | 0 | 86.6682 | 32.9339
2018-04-28 07:00 | 86.1906 | 0 | 86.7247 | 32.9554
2018-04-28 08:00 | 86.36 | 0 | 86.952 | 33.0418
2018-04-28 09:00 | 86.4912 | 0 | 87.0588 | 33.0823
2018-04-28 10:00 | 86.1982 | 0 | 86.6392 | 32.9229
2018-04-28 11:00 | 86.1707 | 0 | 86.8849 | 33.0163
2018-04-28 12:00 | 86.5019 | 0 | 87.1504 | 33.1172
2018-04-28 13:00 | 86.6148 | 0 | 87.3167 | 33.1803
2018-04-28 14:00 | 86.4439 | 0 | 87.0832 | 33.0916
2018-04-28 15:00 | 86.5522 | 0 | 87.2938 | 33.1716
2018-04-28 16:00 | 86.5644 | 0 | 87.3579 | 33.196
2018-04-28 17:00 | 86.7445 | 0 | 87.57 | 33.2766
2018-04-28 18:00 | 86.4668 | 0 | 87.3014 | 33.1745
2018-04-28 19:00 | 86.3661 | 0 | 87.0954 | 33.0963
2018-04-28 20:00 | 86.1173 | 0 | 86.891 | 33.0186
2018-04-28 21:00 | 86.1555 | 0 | 86.9245 | 33.0313
2018-04-28 22:00 | 86.2211 | 0 | 87.0054 | 33.0621
2018-04-28 23:00 | 86.2226 | 0 | 87.0787 | 33.0899
2018-04-29 | 86.2364 | 86.7994 | 0 | 32.9838
2018-04-29 01:00 | 86.3188 | 86.952 | 0 | 33.0418
2018-04-29 02:00 | 86.2119 | 86.8177 | 0 | 32.9907
2018-04-29 03:00 | 86.1845 | 86.7857 | 0 | 32.9786
2018-04-29 04:00 | 86.2455 | 86.833 | 0 | 32.9965
2018-04-29 05:00 | 86.2333 | 86.833 | 0 | 32.9965
2018-04-29 06:00 | 86.2776 | 86.8528 | 0 | 33.0041
2018-04-29 07:00 | 86.2867 | 86.8452 | 0 | 33.0012
2018-04-29 08:00 | 86.2989 | 86.9032 | 0 | 33.0232
2018-04-29 09:00 | 86.2867 | 86.8162 | 0 | 32.9902
2018-04-29 10:00 | 86.2882 | 86.8528 | 0 | 33.0041
2018-04-29 11:00 | 86.1845 | 86.743 | 0 | 32.9623
2018-04-29 12:00 | 86.1418 | 86.714 | 0 | 32.9513
2018-04-29 13:00 | 86.1479 | 86.7659 | 0 | 32.971
2018-04-29 14:00 | 86.1112 | 86.7018 | 0 | 32.9467
2018-04-29 15:00 | 86.2455 | 86.8482 | 0 | 33.0023
2018-04-29 16:00 | 86.3447 | 86.9398 | 0 | 33.0371
2018-04-29 17:00 | 86.4805 | 86.9856 | 0 | 33.0545
2018-04-29 18:00 | 86.4332 | 86.92 | 0 | 33.0296
2018-04-29 19:00 | 85.6794 | 85.9266 | 0 | 32.6521
2018-04-29 20:00 | 86.3294 | 86.5888 | 0 | 32.9037
2018-04-29 21:00 | 86.3569 | 86.6728 | 0 | 32.9357
2018-04-29 22:00 | 86.4881 | 86.8086 | 0 | 32.9873
2018-04-29 23:00 | 86.4332 | 86.7353 | 0 | 32.9594
2018-04-30 | 86.4088 | 86.7002 | 86.9352 | 65.9815
2018-04-30 01:00 | 86.0426 | 86.3127 | 86.5278 | 65.6794
2018-04-30 02:00 | 86.392 | 86.6392 | 86.8421 | 65.9229
2018-04-30 03:00 | 86.2776 | 86.5766 | 86.7536 | 65.8655
2018-04-30 04:00 | 86.5034 | 86.8849 | 87.0283 | 66.087
2018-04-30 05:00 | 86.3661 | 86.772 | 87.0054 | 66.0354
2018-04-30 06:00 | 86.2898 | 86.6499 | 86.8147 | 65.9165
2018-04-30 07:00 | 86.2043 | 86.5278 | 86.7079 | 65.8296
2018-04-30 08:00 | 86.3355 | 86.5461 | 86.8025 | 65.8725
2018-04-30 09:00 | 86.3798 | 86.7262 | 86.8711 | 65.967
2018-04-30 10:00 | 86.2272 | 86.5156 | 86.714 | 65.8272
2018-04-30 11:00 | 86.2119 | 86.5141 | 86.7201 | 65.829
2018-04-30 12:00 | 86.389 | 86.6835 | 86.8574 | 65.9455
2018-04-30 13:00 | 86.4027 | 86.6224 | 86.7475 | 65.8806
2018-04-30 14:00 | 86.3783 | 86.6606 | 86.7903 | 65.9113
2018-04-30 15:00 | 86.3355 | 86.5248 | 86.7384 | 65.84
2018-04-30 16:00 | 86.3493 | 86.4912 | 86.685 | 65.807
2018-04-30 17:00 | 86.244 | 86.4683 | 86.6743 | 65.7942
2018-04-30 18:00 | 86.3142 | 86.4378 | 86.5934 | 65.7519
2018-04-30 19:00 | 86.2089 | 86.3508 | 86.5583 | 65.7055
2018-04-30 20:00 | 86.2181 | 86.4836 | 86.6896 | 65.8058
2018-04-30 21:00 | 86.1494 | 86.4759 | 86.63 | 65.7802
2018-04-30 22:00 | 86.2593 | 86.5522 | 86.6468 | 65.8156
2018-04-30 23:00 | 86.4424 | 86.8055 | 86.8864 | 66.0029
2018-05-01 | 86.4637 | 0 | 0 | 0
2018-05-01 01:00 | 86.5629 | 0 | 0 | 0
2018-05-01 02:00 | 86.3706 | 0 | 0 | 0
2018-05-01 03:00 | 86.3523 | 0 | 0 | 0
2018-05-01 04:00 | 86.3676 | 0 | 0 | 0
2018-05-01 05:00 | 86.4027 | 0 | 0 | 0
2018-05-01 06:00 | 86.4652 | 0 | 0 | 0
2018-05-01 07:00 | 86.4012 | 0 | 0 | 0
2018-05-01 08:00 | 86.4515 | 0 | 0 | 0
2018-05-01 09:00 | 86.2028 | 0 | 0 | 0
2018-05-01 10:00 | 86.2715 | 0 | 0 | 0
2018-05-01 11:00 | 86.7567 | 0 | 0 | 0
2018-05-01 12:00 | 86.6194 | 0 | 0 | 0
2018-05-01 13:00 | 86.6377 | 0 | 0 | 0
2018-05-01 14:00 | 86.8757 | 0 | 0 | 0
2018-05-01 15:00 | 86.7994 | 0 | 0 | 0
2018-05-01 16:00 | 86.7674 | 0 | 0 | 0
2018-05-01 17:00 | 86.7384 | 0 | 0 | 0
2018-05-01 18:00 | 86.7124 | 0 | 0 | 0
2018-05-01 19:00 | 86.8376 | 0 | 0 | 0
2018-05-01 20:00 | 86.627 | 0 | 0 | 0
2018-05-01 21:00 | 86.6239 | 0 | 0 | 0
2018-05-01 22:00 | 86.714 | 0 | 0 | 0
2018-05-01 23:00 | 86.8971 | 0 | 0 | 0
2018-05-02 | 0 | 0 | 86.6712 | 32.9351
2018-05-02 01:00 | 0 | 0 | 86.511 | 32.8742
2018-05-02 02:00 | 0 | 0 | 86.7628 | 32.9699
2018-05-02 03:00 | 0 | 0 | 86.7384 | 32.9606
2018-05-02 04:00 | 0 | 0 | 86.8376 | 32.9983
2018-05-02 05:00 | 0 | 0 | 87.0222 | 33.0684
2018-05-02 06:00 | 0 | 0 | 86.9627 | 33.0458
2018-05-02 07:00 | 0 | 0 | 87.1321 | 33.1102
2018-05-02 08:00 | 0 | 0 | 87.1931 | 33.1334
2018-05-02 09:00 | 0 | 0 | 86.7155 | 32.9519
2018-05-02 10:00 | 0 | 0 | 86.6743 | 32.9362
2018-05-02 11:00 | 0 | 0 | 86.8956 | 33.0203
2018-05-02 12:00 | 0 | 0 | 86.9276 | 33.0325
2018-05-02 13:00 | 0 | 0 | 87.2541 | 33.1566
2018-05-02 14:00 | 0 | 0 | 87.4037 | 33.2134
2018-05-02 15:00 | 0 | 0 | 87.2129 | 33.1409
2018-05-02 16:00 | 0 | 0 | 86.9718 | 33.0493
2018-05-02 17:00 | 0 | 0 | 87.1397 | 33.1131
2018-05-02 18:00 | 0 | 0 | 87.2435 | 33.1525
2018-05-02 19:00 | 0 | 0 | 86.8894 | 33.018
2018-05-02 20:00 | 0 | 0 | 87.1839 | 33.1299
2018-05-02 21:00 | 0 | 0 | 87.2419 | 33.1519
2018-05-02 22:00 | 0 | 0 | 87.1733 | 33.1259
2018-05-02 23:00 | 0 | 0 | 87.2557 | 33.1572
2018-05-03 | 86.5492 | 0 | 0 | 0
2018-05-03 01:00 | 86.7201 | 0 | 0 | 0
2018-05-03 02:00 | 86.5095 | 0 | 0 | 0
2018-05-03 03:00 | 86.4576 | 0 | 0 | 0
2018-05-03 04:00 | 86.6316 | 0 | 0 | 0
2018-05-03 05:00 | 86.569 | 0 | 0 | 0
2018-05-03 06:00 | 86.6468 | 0 | 0 | 0
2018-05-03 07:00 | 86.6361 | 0 | 0 | 0
2018-05-03 08:00 | 86.6819 | 0 | 0 | 0
2018-05-03 09:00 | 86.7094 | 0 | 0 | 0
2018-05-03 10:00 | 86.7933 | 0 | 0 | 0
2018-05-03 11:00 | 86.8009 | 0 | 0 | 0
2018-05-03 12:00 | 86.6728 | 0 | 0 | 0
2018-05-03 13:00 | 86.6316 | 0 | 0 | 0
2018-05-03 14:00 | 86.6316 | 0 | 0 | 0
2018-05-03 15:00 | 86.6636 | 0 | 0 | 0
2018-05-03 16:00 | 86.5568 | 0 | 0 | 0
2018-05-03 17:00 | 86.6865 | 0 | 0 | 0
2018-05-03 18:00 | 86.7262 | 0 | 0 | 0
2018-05-03 19:00 | 86.5187 | 0 | 0 | 0
2018-05-03 20:00 | 86.5766 | 0 | 0 | 0
2018-05-03 21:00 | 86.6194 | 0 | 0 | 0
2018-05-03 22:00 | 86.6743 | 0 | 0 | 0
2018-05-03 23:00 | 86.5644 | 0 | 0 | 0
2018-05-04 | 86.2226 | 86.688 | 0 | 32.9414
2018-05-04 01:00 | 86.1128 | 86.5232 | 0 | 32.8788
2018-05-04 02:00 | 86.2791 | 86.6896 | 0 | 32.942
2018-05-04 03:00 | 86.0014 | 86.4485 | 0 | 32.8504
2018-05-04 04:00 | 86.0533 | 86.4347 | 0 | 32.8452
2018-05-04 05:00 | 86.2257 | 86.6117 | 0 | 32.9124
2018-05-04 06:00 | 86.4332 | 86.9352 | 0 | 33.0354
2018-05-04 07:00 | 86.5873 | 87.0619 | 0 | 33.0835
2018-05-04 08:00 | 86.3691 | 86.7811 | 0 | 32.9768
2018-05-04 09:00 | 86.334 | 86.7399 | 0 | 32.9612
2018-05-04 10:00 | 86.5126 | 86.862 | 0 | 33.0076
2018-05-04 11:00 | 86.5003 | 86.9306 | 0 | 33.0336
2018-05-04 12:00 | 86.7002 | 87.1412 | 0 | 33.1137
2018-05-04 13:00 | 86.363 | 86.8009 | 0 | 32.9843
2018-05-04 14:00 | 86.4408 | 86.8635 | 0 | 33.0081
2018-05-04 15:00 | 86.2943 | 86.6743 | 0 | 32.9362
2018-05-04 16:00 | 86.3706 | 86.7491 | 0 | 32.9647
2018-05-04 17:00 | 86.2882 | 86.7445 | 0 | 32.9629
2018-05-04 18:00 | 86.1875 | 86.6667 | 0 | 32.9333
2018-05-04 19:00 | 86.099 | 86.5431 | 0 | 32.8864
2018-05-04 20:00 | 86.1997 | 86.5187 | 0 | 32.8771
2018-05-04 21:00 | 86.3767 | 86.7247 | 0 | 32.9554
2018-05-04 22:00 | 86.3691 | 86.7659 | 0 | 32.971
2018-05-04 23:00 | 86.4012 | 86.7918 | 0 | 32.9809
2018-05-05 | 86.0121 | 0 | 86.5507 | 32.8893
2018-05-05 01:00 | 85.919 | 0 | 86.5324 | 32.8823
2018-05-05 02:00 | 86.0533 | 0 | 86.6453 | 32.9252
2018-05-05 03:00 | 86.1677 | 0 | 86.7002 | 32.9461
2018-05-05 04:00 | 86.3081 | 0 | 86.8513 | 33.0035
2018-05-05 05:00 | 86.2562 | 0 | 86.8605 | 33.007
2018-05-05 06:00 | 86.1234 | 0 | 86.6682 | 32.9339
2018-05-05 07:00 | 86.1906 | 0 | 86.7247 | 32.9554
2018-05-05 08:00 | 86.36 | 0 | 86.952 | 33.0418
2018-05-05 09:00 | 86.4912 | 0 | 87.0588 | 33.0823
2018-05-05 10:00 | 86.1982 | 0 | 86.6392 | 32.9229
2018-05-05 11:00 | 86.1707 | 0 | 86.8849 | 33.0163
2018-05-05 12:00 | 86.5019 | 0 | 87.1504 | 33.1172
2018-05-05 13:00 | 86.6148 | 0 | 87.3167 | 33.1803
2018-05-05 14:00 | 86.4439 | 0 | 87.0832 | 33.0916
2018-05-05 15:00 | 86.5522 | 0 | 87.2938 | 33.1716
2018-05-05 16:00 | 86.5644 | 0 | 87.3579 | 33.196
2018-05-05 17:00 | 86.7445 | 0 | 87.57 | 33.2766
2018-05-05 18:00 | 86.4668 | 0 | 87.3014 | 33.1745
2018-05-05 19:00 | 86.3661 | 0 | 87.0954 | 33.0963
2018-05-05 20:00 | 86.1173 | 0 | 86.891 | 33.0186
2018-05-05 21:00 | 86.1555 | 0 | 86.9245 | 33.0313
2018-05-05 22:00 | 86.2211 | 0 | 87.0054 | 33.0621
2018-05-05 23:00 | 86.2226 | 0 | 87.0787 | 33.0899
2018-05-06 | 86.2364 | 86.7994 | 0 | 32.9838
2018-05-06 01:00 | 86.3188 | 86.952 | 0 | 33.0418
2018-05-06 02:00 | 86.2119 | 86.8177 | 0 | 32.9907
2018-05-06 03:00 | 86.1845 | 86.7857 | 0 | 32.9786
2018-05-06 04:00 | 86.2455 | 86.833 | 0 | 32.9965
2018-05-06 05:00 | 86.2333 | 86.833 | 0 | 32.9965
2018-05-06 06:00 | 86.2776 | 86.8528 | 0 | 33.0041
2018-05-06 07:00 | 86.2867 | 86.8452 | 0 | 33.0012
2018-05-06 08:00 | 86.2989 | 86.9032 | 0 | 33.0232
2018-05-06 09:00 | 86.2867 | 86.8162 | 0 | 32.9902
2018-05-06 10:00 | 86.2882 | 86.8528 | 0 | 33.0041
2018-05-06 11:00 | 86.1845 | 86.743 | 0 | 32.9623
2018-05-06 12:00 | 86.1418 | 86.714 | 0 | 32.9513
2018-05-06 13:00 | 86.1479 | 86.7659 | 0 | 32.971
2018-05-06 14:00 | 86.1112 | 86.7018 | 0 | 32.9467
2018-05-06 15:00 | 86.2455 | 86.8482 | 0 | 33.0023
2018-05-06 16:00 | 86.3447 | 86.9398 | 0 | 33.0371
2018-05-06 17:00 | 86.4805 | 86.9856 | 0 | 33.0545
2018-05-06 18:00 | 86.4332 | 86.92 | 0 | 33.0296
2018-05-06 19:00 | 85.6794 | 85.9266 | 0 | 32.6521
2018-05-06 20:00 | 86.3294 | 86.5888 | 0 | 32.9037
2018-05-06 21:00 | 86.3569 | 86.6728 | 0 | 32.9357
2018-05-06 22:00 | 86.4881 | 86.8086 | 0 | 32.9873
2018-05-06 23:00 | 86.4332 | 86.7353 | 0 | 32.9594
2018-05-07 | 86.4088 | 86.7002 | 86.9352 | 65.9815
2018-05-07 01:00 | 86.0426 | 86.3127 | 86.5278 | 65.6794
2018-05-07 02:00 | 86.392 | 86.6392 | 86.8421 | 65.9229
2018-05-07 03:00 | 86.2776 | 86.5766 | 86.7536 | 65.8655
2018-05-07 04:00 | 86.5034 | 86.8849 | 87.0283 | 66.087
2018-05-07 05:00 | 86.3661 | 86.772 | 87.0054 | 66.0354
2018-05-07 06:00 | 86.2898 | 86.6499 | 86.8147 | 65.9165
2018-05-07 07:00 | 86.2043 | 86.5278 | 86.7079 | 65.8296
2018-05-07 08:00 | 86.3355 | 86.5461 | 86.8025 | 65.8725
2018-05-07 09:00 | 86.3798 | 86.7262 | 86.8711 | 65.967
2018-05-07 10:00 | 86.2272 | 86.5156 | 86.714 | 65.8272
2018-05-07 11:00 | 86.2119 | 86.5141 | 86.7201 | 65.829
2018-05-07 12:00 | 86.389 | 86.6835 | 86.8574 | 65.9455
2018-05-07 13:00 | 86.4027 | 86.6224 | 86.7475 | 65.8806
2018-05-07 14:00 | 86.3783 | 86.6606 | 86.7903 | 65.9113
2018-05-07 15:00 | 86.3355 | 86.5248 | 86.7384 | 65.84
2018-05-07 16:00 | 86.3493 | 86.4912 | 86.685 | 65.807
2018-05-07 17:00 | 86.244 | 86.4683 | 86.6743 | 65.7942
2018-05-07 18:00 | 86.3142 | 86.4378 | 86.5934 | 65.7519
2018-05-07 19:00 | 86.2089 | 86.3508 | 86.5583 | 65.7055
2018-05-07 20:00 | 86.2181 | 86.4836 | 86.6896 | 65.8058
2018-05-07 21:00 | 86.1494 | 86.4759 | 86.63 | 65.7802
2018-05-07 22:00 | 86.2593 | 86.5522 | 86.6468 | 65.8156
2018-05-07 23:00 | 86.4424 | 86.8055 | 86.8864 | 66.0029
2018-05-08 | 86.4637 | 0 | 0 | 0
2018-05-08 01:00 | 86.5629 | 0 | 0 | 0
2018-05-08 02:00 | 86.3706 | 0 | 0 | 0
2018-05-08 03:00 | 86.3523 | 0 | 0 | 0
2018-05-08 04:00 | 86.3676 | 0 | 0 | 0
2018-05-08 05:00 | 86.4027 | 0 | 0 | 0
2018-05-08 06:00 | 86.4652 | 0 | 0 | 0
2018-05-08 07:00 | 86.4012 | 0 | 0 | 0
2018-05-08 08:00 | 86.4515 | 0 | 0 | 0
2018-05-08 09:00 | 86.2028 | 0 | 0 | 0
2018-05-08 10:00 | 86.2715 | 0 | 0 | 0
2018-05-08 11:00 | 86.7567 | 0 | 0 | 0
2018-05-08 12:00 | 86.6194 | 0 | 0 | 0
2018-05-08 13:00 | 86.6377 | 0 | 0 | 0
2018-05-08 14:00 | 86.8757 | 0 | 0 | 0
2018-05-08 15:00 | 86.7994 | 0 | 0 | 0
2018-05-08 16:00 | 86.7674 | 0 | 0 | 0
2018-05-08 17:00 | 86.7384 | 0 | 0 | 0
2018-05-08 18:00 | 86.7124 | 0 | 0 | 0
2018-05-08 19:00 | 86.8376 | 0 | 0 | 0
2018-05-08 20:00 | 86.627 | 0 | 0 | 0
2018-05-08 21:00 | 86.6239 | 0 | 0 | 0
2018-05-08 22:00 | 86.714 | 0 | 0 | 0
2018-05-08 23:00 | 86.8971 | 0 | 0 | 0
2018-05-09 | 0 | 0 | 86.6712 | 32.9351
2018-05-09 01:00 | 0 | 0 | 86.511 | 32.8742
2018-05-09 02:00 | 0 | 0 | 86.7628 | 32.9699
2018-05-09 03:00 | 0 | 0 | 86.7384 | 32.9606
2018-05-09 04:00 | 0 | 0 | 86.8376 | 32.9983
2018-05-09 05:00 | 0 | 0 | 87.0222 | 33.0684
2018-05-09 06:00 | 0 | 0 | 86.9627 | 33.0458
2018-05-09 07:00 | 0 | 0 | 87.1321 | 33.1102
2018-05-09 08:00 | 0 | 0 | 87.1931 | 33.1334
2018-05-09 09:00 | 0 | 0 | 86.7155 | 32.9519
2018-05-09 10:00 | 0 | 0 | 86.6743 | 32.9362
2018-05-09 11:00 | 0 | 0 | 86.8956 | 33.0203
2018-05-09 12:00 | 0 | 0 | 86.9276 | 33.0325
2018-05-09 13:00 | 0 | 0 | 87.2541 | 33.1566
2018-05-09 14:00 | 0 | 0 | 87.4037 | 33.2134
2018-05-09 15:00 | 0 | 0 | 87.2129 | 33.1409
2018-05-09 16:00 | 0 | 0 | 86.9718 | 33.0493
2018-05-09 17:00 | 0 | 0 | 87.1397 | 33.1131
2018-05-09 18:00 | 0 | 0 | 87.2435 | 33.1525
2018-05-09 19:00 | 0 | 0 | 86.8894 | 33.018
2018-05-09 20:00 | 0 | 0 | 87.1839 | 33.1299
2018-05-09 21:00 | 0 | 0 | 87.2419 | 33.1519
2018-05-09 22:00 | 0 | 0 | 87.1733 | 33.1259
2018-05-09 23:00 | 0 | 0 | 87.2557 | 33.1572
2018-05-10 | 86.5492 | 0 | 0 | 0
2018-05-10 01:00 | 86.7201 | 0 | 0 | 0
2018-05-10 02:00 | 86.5095 | 0 | 0 | 0
2018-05-10 03:00 | 86.4576 | 0 | 0 | 0
2018-05-10 04:00 | 86.6316 | 0 | 0 | 0
2018-05-10 05:00 | 86.569 | 0 | 0 | 0
2018-05-10 06:00 | 86.6468 | 0 | 0 | 0
2018-05-10 07:00 | 86.6361 | 0 | 0 | 0
2018-05-10 08:00 | 86.6819 | 0 | 0 | 0
2018-05-10 09:00 | 86.7094 | 0 | 0 | 0
2018-05-10 10:00 | 86.7933 | 0 | 0 | 0
2018-05-10 11:00 | 86.8009 | 0 | 0 | 0
2018-05-10 12:00 | 86.6728 | 0 | 0 | 0
2018-05-10 13:00 | 86.6316 | 0 | 0 | 0
2018-05-10 14:00 | 86.6316 | 0 | 0 | 0
2018-05-10 15:00 | 86.6636 | 0 | 0 | 0
2018-05-10 16:00 | 86.5568 | 0 | 0 | 0
2018-05-10 17:00 | 86.6865 | 0 | 0 | 0
2018-05-10 18:00 | 86.7262 | 0 | 0 | 0
2018-05-10 19:00 | 86.5187 | 0 | 0 | 0
2018-05-10 20:00 | 86.5766 | 0 | 0 | 0
2018-05-10 21:00 | 86.6194 | 0 | 0 | 0
2018-05-10 22:00 | 86.6743 | 0 | 0 | 0
2018-05-10 23:00 | 86.5644 | 0 | 0 | 0
2018-05-11 | 86.2226 | 86.688 | 0 | 32.9414
2018-05-11 01:00 | 86.1128 | 86.5232 | 0 | 32.8788
2018-05-11 02:00 | 86.2791 | 86.6896 | 0 | 32.942
2018-05-11 03:00 | 86.0014 | 86.4485 | 0 | 32.8504
2018-05-11 04:00 | 86.0533 | 86.4347 | 0 | 32.8452
2018-05-11 05:00 | 86.2257 | 86.6117 | 0 | 32.9124
2018-05-11 06:00 | 86.4332 | 86.9352 | 0 | 33.0354
2018-05-11 07:00 | 86.5873 | 87.0619 | 0 | 33.0835
2018-05-11 08:00 | 86.3691 | 86.7811 | 0 | 32.9768
2018-05-11 09:00 | 86.334 | 86.7399 | 0 | 32.9612
2018-05-11 10:00 | 86.5126 | 86.862 | 0 | 33.0076
2018-05-11 11:00 | 86.5003 | 86.9306 | 0 | 33.0336
2018-05-11 12:00 | 86.7002 | 87.1412 | 0 | 33.1137
2018-05-11 13:00 | 86.363 | 86.8009 | 0 | 32.9843
2018-05-11 14:00 | 86.4408 | 86.8635 | 0 | 33.0081
2018-05-11 15:00 | 86.2943 | 86.6743 | 0 | 32.9362
2018-05-11 16:00 | 86.3706 | 86.7491 | 0 | 32.9647
2018-05-11 17:00 | 86.2882 | 86.7445 | 0 | 32.9629
2018-05-11 18:00 | 86.1875 | 86.6667 | 0 | 32.9333
2018-05-11 19:00 | 86.099 | 86.5431 | 0 | 32.8864
2018-05-11 20:00 | 86.1997 | 86.5187 | 0 | 32.8771
2018-05-11 21:00 | 86.3767 | 86.7247 | 0 | 32.9554
2018-05-11 22:00 | 86.3691 | 86.7659 | 0 | 32.971
2018-05-11 23:00 | 86.4012 | 86.7918 | 0 | 32.9809
2018-05-12 | 86.0121 | 0 | 86.5507 | 32.8893
2018-05-12 01:00 | 85.919 | 0 | 86.5324 | 32.8823
2018-05-12 02:00 | 86.0533 | 0 | 86.6453 | 32.9252
2018-05-12 03:00 | 86.1677 | 0 | 86.7002 | 32.9461
2018-05-12 04:00 | 86.3081 | 0 | 86.8513 | 33.0035
2018-05-12 05:00 | 86.2562 | 0 | 86.8605 | 33.007
2018-05-12 06:00 | 86.1234 | 0 | 86.6682 | 32.9339
2018-05-12 07:00 | 86.1906 | 0 | 86.7247 | 32.9554
2018-05-12 08:00 | 86.36 | 0 | 86.952 | 33.0418
2018-05-12 09:00 | 86.4912 | 0 | 87.0588 | 33.0823
2018-05-12 10:00 | 86.1982 | 0 | 86.6392 | 32.9229
2018-05-12 11:00 | 86.1707 | 0 | 86.8849 | 33.0163
2018-05-12 12:00 | 86.5019 | 0 | 87.1504 | 33.1172
2018-05-12 13:00 | 86.6148 | 0 | 87.3167 | 33.1803
2018-05-12 14:00 | 86.4439 | 0 | 87.0832 | 33.0916
2018-05-12 15:00 | 86.5522 | 0 | 87.2938 | 33.1716
2018-05-12 16:00 | 86.5644 | 0 | 87.3579 | 33.196
2018-05-12 17:00 | 86.7445 | 0 | 87.57 | 33.2766
2018-05-12 18:00 | 86.4668 | 0 | 87.3014 | 33.1745
2018-05-12 19:00 | 86.3661 | 0 | 87.0954 | 33.0963
2018-05-12 20:00 | 86.1173 | 0 | 86.891 | 33.0186
2018-05-12 21:00 | 86.1555 | 0 | 86.9245 | 33.0313
2018-05-12 22:00 | 86.2211 | 0 | 87.0054 | 33.0621
2018-05-12 23:00 | 86.2226 | 0 | 87.0787 | 33.0899
2018-05-13 | 86.2364 | 86.7994 | 0 | 32.9838
2018-05-13 01:00 | 86.3188 | 86.952 | 0 | 33.0418
2018-05-13 02:00 | 86.2119 | 86.8177 | 0 | 32.9907
2018-05-13 03:00 | 86.1845 | 86.7857 | 0 | 32.9786
2018-05-13 04:00 | 86.2455 | 86.833 | 0 | 32.9965
2018-05-13 05:00 | 86.2333 | 86.833 | 0 | 32.9965
2018-05-13 06:00 | 86.2776 | 86.8528 | 0 | 33.0041
2018-05-13 07:00 | 86.2867 | 86.8452 | 0 | 33.0012
2018-05-13 08:00 | 86.2989 | 86.9032 | 0 | 33.0232
2018-05-13 09:00 | 86.2867 | 86.8162 | 0 | 32.9902
2018-05-13 10:00 | 86.2882 | 86.8528 | 0 | 33.0041
2018-05-13 11:00 | 86.1845 | 86.743 | 0 | 32.9623
2018-05-13 12:00 | 86.1418 | 86.714 | 0 | 32.9513
2018-05-13 13:00 | 86.1479 | 86.7659 | 0 | 32.971
2018-05-13 14:00 | 86.1112 | 86.7018 | 0 | 32.9467
2018-05-13 15:00 | 86.2455 | 86.8482 | 0 | 33.0023
2018-05-13 16:00 | 86.3447 | 86.9398 | 0 | 33.0371
2018-05-13 17:00 | 86.4805 | 86.9856 | 0 | 33.0545
2018-05-13 18:00 | 86.4332 | 86.92 | 0 | 33.0296
2018-05-13 19:00 | 85.6794 | 85.9266 | 0 | 32.6521
2018-05-13 20:00 | 86.3294 | 86.5888 | 0 | 32.9037
2018-05-13 21:00 | 86.3569 | 86.6728 | 0 | 32.9357
2018-05-13 22:00 | 86.4881 | 86.8086 | 0 | 32.9873
2018-05-13 23:00 | 86.4332 | 86.7353 | 0 | 32.9594
2018-05-14 | 86.4088 | 86.7002 | 86.9352 | 65.9815
2018-05-14 01:00 | 86.0426 | 86.3127 | 86.5278 | 65.6794
2018-05-14 02:00 | 86.392 | 86.6392 | 86.8421 | 65.9229
2018-05-14 03:00 | 86.2776 | 86.5766 | 86.7536 | 65.8655
2018-05-14 04:00 | 86.5034 | 86.8849 | 87.0283 | 66.087
2018-05-14 05:00 | 86.3661 | 86.772 | 87.0054 | 66.0354
2018-05-14 06:00 | 86.2898 | 86.6499 | 86.8147 | 65.9165
2018-05-14 07:00 | 86.2043 | 86.5278 | 86.7079 | 65.8296
2018-05-14 08:00 | 86.3355 | 86.5461 | 86.8025 | 65.8725
2018-05-14 09:00 | 86.3798 | 86.7262 | 86.8711 | 65.967
2018-05-14 10:00 | 86.2272 | 86.5156 | 86.714 | 65.8272
2018-05-14 11:00 | 86.2119 | 86.5141 | 86.7201 | 65.829
2018-05-14 12:00 | 86.389 | 86.6835 | 86.8574 | 65.9455
2018-05-14 13:00 | 86.4027 | 86.6224 | 86.7475 | 65.8806
2018-05-14 14:00 | 86.3783 | 86.6606 | 86.7903 | 65.9113
2018-05-14 15:00 | 86.3355 | 86.5248 | 86.7384 | 65.84
2018-05-14 16:00 | 86.3493 | 86.4912 | 86.685 | 65.807
2018-05-14 17:00 | 86.244 | 86.4683 | 86.6743 | 65.7942
2018-05-14 18:00 | 86.3142 | 86.4378 | 86.5934 | 65.7519
2018-05-14 19:00 | 86.2089 | 86.3508 | 86.5583 | 65.7055
2018-05-14 20:00 | 86.2181 | 86.4836 | 86.6896 | 65.8058
2018-05-14 21:00 | 86.1494 | 86.4759 | 86.63 | 65.7802
2018-05-14 22:00 | 86.2593 | 86.5522 | 86.6468 | 65.8156
2018-05-14 23:00 | 86.4424 | 86.8055 | 86.8864 | 66.0029
2018-05-15 | 86.4637 | 0 | 0 | 0
2018-05-15 01:00 | 86.5629 | 0 | 0 | 0
2018-05-15 02:00 | 86.3706 | 0 | 0 | 0
2018-05-15 03:00 | 86.3523 | 0 | 0 | 0
2018-05-15 04:00 | 86.3676 | 0 | 0 | 0
2018-05-15 05:00 | 86.4027 | 0 | 0 | 0
2018-05-15 06:00 | 86.4652 | 0 | 0 | 0
2018-05-15 07:00 | 86.4012 | 0 | 0 | 0
2018-05-15 08:00 | 86.4515 | 0 | 0 | 0
2018-05-15 09:00 | 86.2028 | 0 | 0 | 0
2018-05-15 10:00 | 86.2715 | 0 | 0 | 0
2018-05-15 11:00 | 86.7567 | 0 | 0 | 0
2018-05-15 12:00 | 86.6194 | 0 | 0 | 0
2018-05-15 13:00 | 86.6377 | 0 | 0 | 0
2018-05-15 14:00 | 86.8757 | 0 | 0 | 0
2018-05-15 15:00 | 86.7994 | 0 | 0 | 0
2018-05-15 16:00 | 86.7674 | 0 | 0 | 0
2018-05-15 17:00 | 86.7384 | 0 | 0 | 0
2018-05-15 18:00 | 86.7124 | 0 | 0 | 0
2018-05-15 19:00 | 86.8376 | 0 | 0 | 0
2018-05-15 20:00 | 86.627 | 0 | 0 | 0
2018-05-15 21:00 | 86.6239 | 0 | 0 | 0
2018-05-15 22:00 | 86.714 | 0 | 0 | 0
2018-05-15 23:00 | 86.8971 | 0 | 0 | 0
2018-05-16 | 0 | 0 | 86.6712 | 32.9351
2018-05-16 01:00 | 0 | 0 | 86.511 | 32.8742
2018-05-16 02:00 | 0 | 0 | 86.7628 | 32.9699
2018-05-16 03:00 | 0 | 0 | 86.7384 | 32.9606
2018-05-16 04:00 | 0 | 0 | 86.8376 | 32.9983
2018-05-16 05:00 | 0 | 0 | 87.0222 | 33.0684
2018-05-16 06:00 | 0 | 0 | 86.9627 | 33.0458
2018-05-16 07:00 | 0 | 0 | 87.1321 | 33.1102
2018-05-16 08:00 | 0 | 0 | 87.1931 | 33.1334
2018-05-16 09:00 | 0 | 0 | 86.7155 | 32.9519
2018-05-16 10:00 | 0 | 0 | 86.6743 | 32.9362
2018-05-16 11:00 | 0 | 0 | 86.8956 | 33.0203
2018-05-16 12:00 | 0 | 0 | 86.9276 | 33.0325
2018-05-16 13:00 | 0 | 0 | 87.2541 | 33.1566
2018-05-16 14:00 | 0 | 0 | 87.4037 | 33.2134
2018-05-16 15:00 | 0 | 0 | 87.2129 | 33.1409
2018-05-16 16:00 | 0 | 0 | 86.9718 | 33.0493
2018-05-16 17:00 | 0 | 0 | 87.1397 | 33.1131
2018-05-16 18:00 | 0 | 0 | 87.2435 | 33.1525
2018-05-16 19:00 | 0 | 0 | 86.8894 | 33.018
2018-05-16 20:00 | 0 | 0 | 87.1839 | 33.1299
2018-05-16 21:00 | 0 | 0 | 87.2419 | 33.1519
2018-05-16 22:00 | 0 | 0 | 87.1733 | 33.1259
2018-05-16 23:00 | 0 | 0 | 87.2557 | 33.1572
2018-05-17 | 86.5492 | 0 | 0 | 0
2018-05-17 01:00 | 86.7201 | 0 | 0 | 0
2018-05-17 02:00 | 86.5095 | 0 | 0 | 0
2018-05-17 03:00 | 86.4576 | 0 | 0 | 0
2018-05-17 04:00 | 86.6316 | 0 | 0 | 0
2018-05-17 05:00 | 86.569 | 0 | 0 | 0
2018-05-17 06:00 | 86.6468 | 0 | 0 | 0
2018-05-17 07:00 | 86.6361 | 0 | 0 | 0
2018-05-17 08:00 | 86.6819 | 0 | 0 | 0
2018-05-17 09:00 | 86.7094 | 0 | 0 | 0
2018-05-17 10:00 | 86.7933 | 0 | 0 | 0
2018-05-17 11:00 | 86.8009 | 0 | 0 | 0
2018-05-17 12:00 | 86.6728 | 0 | 0 | 0
2018-05-17 13:00 | 86.6316 | 0 | 0 | 0
2018-05-17 14:00 | 86.6316 | 0 | 0 | 0
2018-05-17 15:00 | 86.6636 | 0 | 0 | 0
2018-05-17 16:00 | 86.5568 | 0 | 0 | 0
2018-05-17 17:00 | 86.6865 | 0 | 0 | 0
2018-05-17 18:00 | 86.7262 | 0 | 0 | 0
2018-05-17 19:00 | 86.5187 | 0 | 0 | 0
2018-05-17 20:00 | 86.5766 | 0 | 0 | 0
2018-05-17 21:00 | 86.6194 | 0 | 0 | 0
2018-05-17 22:00 | 86.6743 | 0 | 0 | 0
2018-05-17 23:00 | 86.5644 | 0 | 0 | 0
2018-05-18 | 86.2226 | 86.688 | 0 | 32.9414
2018-05-18 01:00 | 86.1128 | 86.5232 | 0 | 32.8788
2018-05-18 02:00 | 86.2791 | 86.6896 | 0 | 32.942
2018-05-18 03:00 | 86.0014 | 86.4485 | 0 | 32.8504
2018-05-18 04:00 | 86.0533 | 86.4347 | 0 | 32.8452
2018-05-18 05:00 | 86.2257 | 86.6117 | 0 | 32.9124
2018-05-18 06:00 | 86.4332 | 86.9352 | 0 | 33.0354
2018-05-18 07:00 | 86.5873 | 87.0619 | 0 | 33.0835
2018-05-18 08:00 | 86.3691 | 86.7811 | 0 | 32.9768
2018-05-18 09:00 | 86.334 | 86.7399 | 0 | 32.9612
2018-05-18 10:00 | 86.5126 | 86.862 | 0 | 33.0076
2018-05-18 11:00 | 86.5003 | 86.9306 | 0 | 33.0336
2018-05-18 12:00 | 86.7002 | 87.1412 | 0 | 33.1137
2018-05-18 13:00 | 86.363 | 86.8009 | 0 | 32.9843
2018-05-18 14:00 | 86.4408 | 86.8635 | 0 | 33.0081
2018-05-18 15:00 | 86.2943 | 86.6743 | 0 | 32.9362
2018-05-18 16:00 | 86.3706 | 86.7491 | 0 | 32.9647
2018-05-18 17:00 | 86.2882 | 86.7445 | 0 | 32.9629
2018-05-18 18:00 | 86.1875 | 86.6667 | 0 | 32.9333
2018-05-18 19:00 | 86.099 | 86.5431 | 0 | 32.8864
2018-05-18 20:00 | 86.1997 | 86.5187 | 0 | 32.8771
2018-05-18 21:00 | 86.3767 | 86.7247 | 0 | 32.9554
2018-05-18 22:00 | 86.3691 | 86.7659 | 0 | 32.971
2018-05-18 23:00 | 86.4012 | 86.7918 | 0 | 32.9809
2018-05-19 | 86.0121 | 0 | 86.5507 | 32.8893
2018-05-19 01:00 | 85.919 | 0 | 86.5324 | 32.8823
2018-05-19 02:00 | 86.0533 | 0 | 86.6453 | 32.9252
2018-05-19 03:00 | 86.1677 | 0 | 86.7002 | 32.9461
2018-05-19 04:00 | 86.3081 | 0 | 86.8513 | 33.0035
2018-05-19 05:00 | 86.2562 | 0 | 86.8605 | 33.007
2018-05-19 06:00 | 86.1234 | 0 | 86.6682 | 32.9339
2018-05-19 07:00 | 86.1906 | 0 | 86.7247 | 32.9554
2018-05-19 08:00 | 86.36 | 0 | 86.952 | 33.0418
2018-05-19 09:00 | 86.4912 | 0 | 87.0588 | 33.0823
2018-05-19 10:00 | 86.1982 | 0 | 86.6392 | 32.9229
2018-05-19 11:00 | 86.1707 | 0 | 86.8849 | 33.0163
2018-05-19 12:00 | 86.5019 | 0 | 87.1504 | 33.1172
2018-05-19 13:00 | 86.6148 | 0 | 87.3167 | 33.1803
2018-05-19 14:00 | 86.4439 | 0 | 87.0832 | 33.0916
2018-05-19 15:00 | 86.5522 | 0 | 87.2938 | 33.1716
2018-05-19 16:00 | 86.5644 | 0 | 87.3579 | 33.196
2018-05-19 17:00 | 86.7445 | 0 | 87.57 | 33.2766
2018-05-19 18:00 | 86.4668 | 0 | 87.3014 | 33.1745
2018-05-19 19:00 | 86.3661 | 0 | 87.0954 | 33.0963
2018-05-19 20:00 | 86.1173 | 0 | 86.891 | 33.0186
2018-05-19 21:00 | 86.1555 | 0 | 86.9245 | 33.0313
2018-05-19 22:00 | 86.2211 | 0 | 87.0054 | 33.0621
2018-05-19 23:00 | 86.2226 | 0 | 87.0787 | 33.0899
2018-05-20 | 86.2364 | 86.7994 | 0 | 32.9838
2018-05-20 01:00 | 86.3188 | 86.952 | 0 | 33.0418
2018-05-20 02:00 | 86.2119 | 86.8177 | 0 | 32.9907
2018-05-20 03:00 | 86.1845 | 86.7857 | 0 | 32.9786
2018-05-20 04:00 | 86.2455 | 86.833 | 0 | 32.9965
2018-05-20 05:00 | 86.2333 | 86.833 | 0 | 32.9965
2018-05-20 06:00 | 86.2776 | 86.8528 | 0 | 33.0041
2018-05-20 07:00 | 86.2867 | 86.8452 | 0 | 33.0012
2018-05-20 08:00 | 86.2989 | 86.9032 | 0 | 33.0232
2018-05-20 09:00 | 86.2867 | 86.8162 | 0 | 32.9902
2018-05-20 10:00 | 86.2882 | 86.8528 | 0 | 33.0041
2018-05-20 11:00 | 86.1845 | 86.743 | 0 | 32.9623
2018-05-20 12:00 | 86.1418 | 86.714 | 0 | 32.9513
2018-05-20 13:00 | 86.1479 | 86.7659 | 0 | 32.971
2018-05-20 14:00 | 86.1112 | 86.7018 | 0 | 32.9467
2018-05-20 15:00 | 86.2455 | 86.8482 | 0 | 33.0023
2018-05-20 16:00 | 86.3447 | 86.9398 | 0 | 33.0371
2018-05-20 17:00 | 86.4805 | 86.9856 | 0 | 33.0545
2018-05-20 18:00 | 86.4332 | 86.92 | 0 | 33.0296
2018-05-20 19:00 | 85.6794 | 85.9266 | 0 | 32.6521
2018-05-20 20:00 | 86.3294 | 86.5888 | 0 | 32.9037
2018-05-20 21:00 | 86.3569 | 86.6728 | 0 | 32.9357
2018-05-20 22:00 | 86.4881 | 86.8086 | 0 | 32.9873
2018-05-20 23:00 | 86.4332 | 86.7353 | 0 | 32.9594
2018-05-21 | 86.4088 | 86.7002 | 86.9352 | 65.9815
2018-05-21 01:00 | 86.0426 | 86.3127 | 86.5278 | 65.6794
2018-05-21 02:00 | 86.392 | 86.6392 | 86.8421 | 65.9229
2018-05-21 03:00 | 86.2776 | 86.5766 | 86.7536 | 65.8655
2018-05-21 04:00 | 86.5034 | 86.8849 | 87.0283 | 66.087
2018-05-21 05:00 | 86.3661 | 86.772 | 87.0054 | 66.0354
2018-05-21 06:00 | 86.2898 | 86.6499 | 86.8147 | 65.9165
2018-05-21 07:00 | 86.2043 | 86.5278 | 86.7079 | 65.8296
2018-05-21 08:00 | 86.3355 | 86.5461 | 86.8025 | 65.8725
2018-05-21 09:00 | 86.3798 | 86.7262 | 86.8711 | 65.967
2018-05-21 10:00 | 86.2272 | 86.5156 | 86.714 | 65.8272
2018-05-21 11:00 | 86.2119 | 86.5141 | 86.7201 | 65.829
2018-05-21 12:00 | 86.389 | 86.6835 | 86.8574 | 65.9455
2018-05-21 13:00 | 86.4027 | 86.6224 | 86.7475 | 65.8806
2018-05-21 14:00 | 86.3783 | 86.6606 | 86.7903 | 65.9113
2018-05-21 15:00 | 86.3355 | 86.5248 | 86.7384 | 65.84
2018-05-21 16:00 | 86.3493 | 86.4912 | 86.685 | 65.807
2018-05-21 17:00 | 86.244 | 86.4683 | 86.6743 | 65.7942
2018-05-21 18:00 | 86.3142 | 86.4378 | 86.5934 | 65.7519
2018-05-21 19:00 | 86.2089 | 86.3508 | 86.5583 | 65.7055
2018-05-21 20:00 | 86.2181 | 86.4836 | 86.6896 | 65.8058
2018-05-21 21:00 | 86.1494 | 86.4759 | 86.63 | 65.7802
2018-05-21 22:00 | 86.2593 | 86.5522 | 86.6468 | 65.8156
2018-05-21 23:00 | 86.4424 | 86.8055 | 86.8864 | 66.0029
2018-05-22 | 86.4637 | 0 | 0 | 0
2018-05-22 01:00 | 86.5629 | 0 | 0 | 0
2018-05-22 02:00 | 86.3706 | 0 | 0 | 0
2018-05-22 03:00 | 86.3523 | 0 | 0 | 0
2018-05-22 04:00 | 86.3676 | 0 | 0 | 0
2018-05-22 05:00 | 86.4027 | 0 | 0 | 0
2018-05-22 06:00 | 86.4652 | 0 | 0 | 0
2018-05-22 07:00 | 86.4012 | 0 | 0 | 0
2018-05-22 08:00 | 86.4515 | 0 | 0 | 0
2018-05-22 09:00 | 86.2028 | 0 | 0 | 0
2018-05-22 10:00 | 86.2715 | 0 | 0 | 0
2018-05-22 11:00 | 86.7567 | 0 | 0 | 0
2018-05-22 12:00 | 86.6194 | 0 | 0 | 0
2018-05-22 13:00 | 86.6377 | 0 | 0 | 0
2018-05-22 14:00 | 86.8757 | 0 | 0 | 0
2018-05-22 15:00 | 86.7994 | 0 | 0 | 0
2018-05-22 16:00 | 86.7674 | 0 | 0 | 0
2018-05-22 17:00 | 86.7384 | 0 | 0 | 0
2018-05-22 18:00 | 86.7124 | 0 | 0 | 0
2018-05-22 19:00 | 86.8376 | 0 | 0 | 0
2018-05-22 20:00 | 86.627 | 0 | 0 | 0
2018-05-22 21:00 | 86.6239 | 0 | 0 | 0
2018-05-22 22:00 | 86.714 | 0 | 0 | 0
2018-05-22 23:00 | 86.8971 | 0 | 0 | 0
2018-05-23 | 0 | 0 | 86.6712 | 32.9351
2018-05-23 01:00 | 0 | 0 | 86.511 | 32.8742
2018-05-23 02:00 | 0 | 0 | 86.7628 | 32.9699
2018-05-23 03:00 | 0 | 0 | 86.7384 | 32.9606
2018-05-23 04:00 | 0 | 0 | 86.8376 | 32.9983
2018-05-23 05:00 | 0 | 0 | 87.0222 | 33.0684
2018-05-23 06:00 | 0 | 0 | 86.9627 | 33.0458
2018-05-23 07:00 | 0 | 0 | 87.1321 | 33.1102
2018-05-23 08:00 | 0 | 0 | 87.1931 | 33.1334
2018-05-23 09:00 | 0 | 0 | 86.7155 | 32.9519
2018-05-23 10:00 | 0 | 0 | 86.6743 | 32.9362
2018-05-23 11:00 | 0 | 0 | 86.8956 | 33.0203
2018-05-23 12:00 | 0 | 0 | 86.9276 | 33.0325
2018-05-23 13:00 | 0 | 0 | 87.2541 | 33.1566
2018-05-23 14:00 | 0 | 0 | 87.4037 | 33.2134
2018-05-23 15:00 | 0 | 0 | 87.2129 | 33.1409
2018-05-23 16:00 | 0 | 0 | 86.9718 | 33.0493
2018-05-23 17:00 | 0 | 0 | 87.1397 | 33.1131
2018-05-23 18:00 | 0 | 0 | 87.2435 | 33.1525
2018-05-23 19:00 | 0 | 0 | 86.8894 | 33.018
2018-05-23 20:00 | 0 | 0 | 87.1839 | 33.1299
2018-05-23 21:00 | 0 | 0 | 87.2419 | 33.1519
2018-05-23 22:00 | 0 | 0 | 87.1733 | 33.1259
2018-05-23 23:00 | 0 | 0 | 87.2557 | 33.1572
2018-05-24 | 86.5492 | 0 | 0 | 0
2018-05-24 01:00 | 86.7201 | 0 | 0 | 0
2018-05-24 02:00 | 86.5095 | 0 | 0 | 0
2018-05-24 03:00 | 86.4576 | 0 | 0 | 0
2018-05-24 04:00 | 86.6316 | 0 | 0 | 0
2018-05-24 05:00 | 86.569 | 0 | 0 | 0
2018-05-24 06:00 | 86.6468 | 0 | 0 | 0
2018-05-24 07:00 | 86.6361 | 0 | 0 | 0
2018-05-24 08:00 | 86.6819 | 0 | 0 | 0
2018-05-24 09:00 | 86.7094 | 0 | 0 | 0
2018-05-24 10:00 | 86.7933 | 0 | 0 | 0
2018-05-24 11:00 | 86.8009 | 0 | 0 | 0

## Step 1.2 Fixture Inventory
Lamp Wattage (W) | Lamp Quantity | Ballast Wattage (W) | Ballast Quantity |  | Total Anticipated Load (kW)
100 | 2000 |  |  | 200 | 200 | If lighting panel is mixed, input existing lamp and ballast wattage and quantity
|  |  |  | 0 |  | If ballast wattage is unknown leave ballast wattage and quantity blank, only input lamp wattage and quantity
0
|  |  |  | 0 |  | The Total Anticipated Load will sum the wattage and quantity of up to 100 fixtures
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0

## Step 2. Power Calcs
Circuit #1 Datetime | Hour of Day | Day of Week | Circuit #1 AC Current (Amps) | Circuit #1 Power (kW) - Balanced Load | Circuit #1 Power (kW) - Unbalanced Load | Circuit #2 Datetime | Hour of Day | Day of Week | Circuit #2 AC Current (Amps) | Circuit #2 Power (kW) - Balanced Load | Circuit #2 Power (kW) - Unbalanced Load | Circuit #3 Datetime | Hour of Day | Day of Week | Circuit #3 AC Current (Amps) | Circuit #3 Power (kW) - Balanced Load | Circuit #3 Power (kW) - Unbalanced Load | Circuit #4 Datetime | Hour of Day | Day of Week | Circuit #4 AC Current (Amps) | Circuit #4 Power (kW) - Balanced Load | Circuit #4 Power (kW) - Unbalanced Load
2018-02-01 10:00 | 10 | 5 | 86.7201 | 18.115 | 0 | 2018-02-01 10:00 | 10 | 5 | 86.7018 | 18.1111 | 0 | 2018-02-01 10:00 | 10 | 5 | 87.0329 | 18.1803 | 0 | 2018-02-01 10:00 | 10 | 5 | 17.3735 | 3.6291 | 0
2018-02-01 11:00 | 11 | 5 | 86.6697 | 18.1044 | 0 | 2018-02-01 11:00 | 11 | 5 | 86.92 | 18.1567 | 0 | 2018-02-01 11:00 | 11 | 5 | 87.0665 | 18.1873 | 0 | 2018-02-01 11:00 | 11 | 5 | 66.1149 | 13.8107 | 0
2018-02-01 12:00 | 12 | 5 | 86.6209 | 18.0942 | 0 | 2018-02-01 12:00 | 12 | 5 | 86.8498 | 18.1421 | 0 | 2018-02-01 12:00 | 12 | 5 | 87.0954 | 18.1934 | 0 | 2018-02-01 12:00 | 12 | 5 | 66.0992 | 13.8075 | 0
2018-02-01 13:00 | 13 | 5 | 86.5003 | 18.069 | 0 | 2018-02-01 13:00 | 13 | 5 | 86.7323 | 18.1175 | 0 | 2018-02-01 13:00 | 13 | 5 | 87.0253 | 18.1787 | 0 | 2018-02-01 13:00 | 13 | 5 | 66.0279 | 13.7926 | 0
2018-02-01 14:00 | 14 | 5 | 86.54 | 18.0773 | 0 | 2018-02-01 14:00 | 14 | 5 | 86.6804 | 18.1067 | 0 | 2018-02-01 14:00 | 14 | 5 | 86.9703 | 18.1672 | 0 | 2018-02-01 14:00 | 14 | 5 | 65.9873 | 13.7841 | 0
2018-02-01 15:00 | 15 | 5 | 86.4958 | 18.0681 | 0 | 2018-02-01 15:00 | 15 | 5 | 86.7079 | 18.1124 | 0 | 2018-02-01 15:00 | 15 | 5 | 87.0542 | 18.1848 | 0 | 2018-02-01 15:00 | 15 | 5 | 66.0296 | 13.7929 | 0
2018-02-01 16:00 | 16 | 5 | 86.5171 | 18.0726 | 0 | 2018-02-01 16:00 | 16 | 5 | 86.7857 | 18.1287 | 0 | 2018-02-01 16:00 | 16 | 5 | 87.0405 | 18.1819 | 0 | 2018-02-01 16:00 | 16 | 5 | 66.054 | 13.798 | 0
2018-02-01 17:00 | 17 | 5 | 86.3813 | 18.0442 | 0 | 2018-02-01 17:00 | 17 | 5 | 86.6392 | 18.0981 | 0 | 2018-02-01 17:00 | 17 | 5 | 87.0085 | 18.1752 | 0 | 2018-02-01 17:00 | 17 | 5 | 65.9861 | 13.7838 | 0
2018-02-01 18:00 | 18 | 5 | 86.537 | 18.0767 | 0 | 2018-02-01 18:00 | 18 | 5 | 86.6407 | 18.0984 | 0 | 2018-02-01 18:00 | 18 | 5 | 87.0695 | 18.1879 | 0 | 2018-02-01 18:00 | 18 | 5 | 66.0099 | 13.7888 | 0
2018-02-01 19:00 | 19 | 5 | 86.6224 | 18.0946 | 0 | 2018-02-01 19:00 | 19 | 5 | 86.8544 | 18.143 | 0 | 2018-02-01 19:00 | 19 | 5 | 87.1382 | 18.2023 | 0 | 2018-02-01 19:00 | 19 | 5 | 66.1172 | 13.8112 | 0
2018-02-01 20:00 | 20 | 5 | 86.537 | 18.0767 | 0 | 2018-02-01 20:00 | 20 | 5 | 86.7628 | 18.1239 | 0 | 2018-02-01 20:00 | 20 | 5 | 87.1458 | 18.2039 | 0 | 2018-02-01 20:00 | 20 | 5 | 66.0853 | 13.8046 | 0
2018-02-01 21:00 | 21 | 5 | 86.5171 | 18.0726 | 0 | 2018-02-01 21:00 | 21 | 5 | 86.746 | 18.1204 | 0 | 2018-02-01 21:00 | 21 | 5 | 86.981 | 18.1695 | 0 | 2018-02-01 21:00 | 21 | 5 | 66.0163 | 13.7901 | 0
2018-02-01 22:00 | 22 | 5 | 86.5278 | 18.0748 | 0 | 2018-02-01 22:00 | 22 | 5 | 86.7292 | 18.1169 | 0 | 2018-02-01 22:00 | 22 | 5 | 86.9444 | 18.1618 | 0 | 2018-02-01 22:00 | 22 | 5 | 65.996 | 13.7859 | 0
2018-02-01 23:00 | 23 | 5 | 86.5461 | 18.0786 | 0 | 2018-02-01 23:00 | 23 | 5 | 86.8818 | 18.1487 | 0 | 2018-02-01 23:00 | 23 | 5 | 87.1351 | 18.2017 | 0 | 2018-02-01 23:00 | 23 | 5 | 66.1264 | 13.8131 | 0
2018-02-02 | 0 | 6 | 0 | 0 | 0 | 2018-02-02 | 0 | 6 | 86.7842 | 18.1284 | 0 | 2018-02-02 | 0 | 6 | 87.1504 | 18.2048 | 0 | 2018-02-02 | 0 | 6 | 66.0951 | 13.8066 | 0
2018-02-02 01:00 | 1 | 6 | 0 | 0 | 0 | 2018-02-02 01:00 | 1 | 6 | 86.8605 | 18.1443 | 0 | 2018-02-02 01:00 | 1 | 6 | 87.0115 | 18.1758 | 0 | 2018-02-02 01:00 | 1 | 6 | 66.0714 | 13.8016 | 0
2018-02-02 02:00 | 2 | 6 | 0 | 0 | 0 | 2018-02-02 02:00 | 2 | 6 | 86.8482 | 18.1417 | 0 | 2018-02-02 02:00 | 2 | 6 | 87.1885 | 18.2128 | 0 | 2018-02-02 02:00 | 2 | 6 | 66.1339 | 13.8147 | 0
2018-02-02 03:00 | 3 | 6 | 0 | 0 | 0 | 2018-02-02 03:00 | 3 | 6 | 86.8681 | 18.1459 | 0 | 2018-02-02 03:00 | 3 | 6 | 87.1641 | 18.2077 | 0 | 2018-02-02 03:00 | 3 | 6 | 66.1322 | 13.8144 | 0
2018-02-02 04:00 | 4 | 6 | 0 | 0 | 0 | 2018-02-02 04:00 | 4 | 6 | 86.7994 | 18.1315 | 0 | 2018-02-02 04:00 | 4 | 6 | 87.1229 | 18.1991 | 0 | 2018-02-02 04:00 | 4 | 6 | 66.0905 | 13.8056 | 0
2018-02-02 05:00 | 5 | 6 | 0 | 0 | 0 | 2018-02-02 05:00 | 5 | 6 | 86.8055 | 18.1328 | 0 | 2018-02-02 05:00 | 5 | 6 | 87.1916 | 18.2135 | 0 | 2018-02-02 05:00 | 5 | 6 | 66.1189 | 13.8116 | 0
2018-02-02 06:00 | 6 | 6 | 0 | 0 | 0 | 2018-02-02 06:00 | 6 | 6 | 86.8086 | 18.1334 | 0 | 2018-02-02 06:00 | 6 | 6 | 87.1778 | 18.2106 | 0 | 2018-02-02 06:00 | 6 | 6 | 66.1148 | 13.8107 | 0
2018-02-02 07:00 | 7 | 6 | 0 | 0 | 0 | 2018-02-02 07:00 | 7 | 6 | 86.865 | 18.1452 | 0 | 2018-02-02 07:00 | 7 | 6 | 87.2572 | 18.2272 | 0 | 2018-02-02 07:00 | 7 | 6 | 66.1664 | 13.8215 | 0
2018-02-02 08:00 | 8 | 6 | 0 | 0 | 0 | 2018-02-02 08:00 | 8 | 6 | 86.7994 | 18.1315 | 0 | 2018-02-02 08:00 | 8 | 6 | 87.1473 | 18.2042 | 0 | 2018-02-02 08:00 | 8 | 6 | 66.0997 | 13.8076 | 0
2018-02-02 09:00 | 9 | 6 | 0 | 0 | 0 | 2018-02-02 09:00 | 9 | 6 | 86.8925 | 18.151 | 0 | 2018-02-02 09:00 | 9 | 6 | 87.1641 | 18.2077 | 0 | 2018-02-02 09:00 | 9 | 6 | 66.1415 | 13.8163 | 0
2018-02-02 10:00 | 10 | 6 | 0 | 0 | 0 | 2018-02-02 10:00 | 10 | 6 | 86.8956 | 18.1516 | 0 | 2018-02-02 10:00 | 10 | 6 | 87.2297 | 18.2214 | 0 | 2018-02-02 10:00 | 10 | 6 | 66.1676 | 13.8218 | 0
2018-02-02 11:00 | 11 | 6 | 0 | 0 | 0 | 2018-02-02 11:00 | 11 | 6 | 86.7704 | 18.1255 | 0 | 2018-02-02 11:00 | 11 | 6 | 87.1031 | 18.195 | 0 | 2018-02-02 11:00 | 11 | 6 | 66.0719 | 13.8018 | 0
2018-02-02 12:00 | 12 | 6 | 0 | 0 | 0 | 2018-02-02 12:00 | 12 | 6 | 86.8101 | 18.1338 | 0 | 2018-02-02 12:00 | 12 | 6 | 87.0329 | 18.1803 | 0 | 2018-02-02 12:00 | 12 | 6 | 66.0603 | 13.7993 | 0
2018-02-02 13:00 | 13 | 6 | 0 | 0 | 0 | 2018-02-02 13:00 | 13 | 6 | 86.8727 | 18.1468 | 0 | 2018-02-02 13:00 | 13 | 6 | 87.1366 | 18.202 | 0 | 2018-02-02 13:00 | 13 | 6 | 66.1235 | 13.8125 | 0
2018-02-02 14:00 | 14 | 6 | 0 | 0 | 0 | 2018-02-02 14:00 | 14 | 6 | 86.7964 | 18.1309 | 0 | 2018-02-02 14:00 | 14 | 6 | 87.0344 | 18.1806 | 0 | 2018-02-02 14:00 | 14 | 6 | 66.0557 | 13.7984 | 0
2018-02-02 15:00 | 15 | 6 | 0 | 0 | 0 | 2018-02-02 15:00 | 15 | 6 | 86.6041 | 18.0907 | 0 | 2018-02-02 15:00 | 15 | 6 | 87.0344 | 18.1806 | 0 | 2018-02-02 15:00 | 15 | 6 | 65.9826 | 13.7831 | 0
2018-02-02 16:00 | 16 | 6 | 0 | 0 | 0 | 2018-02-02 16:00 | 16 | 6 | 86.8391 | 18.1398 | 0 | 2018-02-02 16:00 | 16 | 6 | 87.1321 | 18.201 | 0 | 2018-02-02 16:00 | 16 | 6 | 66.1091 | 13.8095 | 0
2018-02-02 17:00 | 17 | 6 | 0 | 0 | 0 | 2018-02-02 17:00 | 17 | 6 | 86.804 | 18.1325 | 0 | 2018-02-02 17:00 | 17 | 6 | 86.9657 | 18.1663 | 0 | 2018-02-02 17:00 | 17 | 6 | 66.0325 | 13.7935 | 0
2018-02-02 18:00 | 18 | 6 | 0 | 0 | 0 | 2018-02-02 18:00 | 18 | 6 | 86.9017 | 18.1529 | 0 | 2018-02-02 18:00 | 18 | 6 | 87.187 | 18.2125 | 0 | 2018-02-02 18:00 | 18 | 6 | 66.1537 | 13.8188 | 0
2018-02-02 19:00 | 19 | 6 | 0 | 0 | 0 | 2018-02-02 19:00 | 19 | 6 | 86.4302 | 18.0544 | 0 | 2018-02-02 19:00 | 19 | 6 | 86.6423 | 18.0987 | 0 | 2018-02-02 19:00 | 19 | 6 | 65.7675 | 13.7382 | 0
2018-02-02 20:00 | 20 | 6 | 0 | 0 | 0 | 2018-02-02 20:00 | 20 | 6 | 86.6499 | 18.1003 | 0 | 2018-02-02 20:00 | 20 | 6 | 86.8513 | 18.1424 | 0 | 2018-02-02 20:00 | 20 | 6 | 65.9305 | 13.7722 | 0
2018-02-02 21:00 | 21 | 6 | 0 | 0 | 0 | 2018-02-02 21:00 | 21 | 6 | 86.6438 | 18.099 | 0 | 2018-02-02 21:00 | 21 | 6 | 86.9703 | 18.1672 | 0 | 2018-02-02 21:00 | 21 | 6 | 65.9734 | 13.7812 | 0
2018-02-02 22:00 | 22 | 6 | 0 | 0 | 0 | 2018-02-02 22:00 | 22 | 6 | 86.6453 | 18.0993 | 0 | 2018-02-02 22:00 | 22 | 6 | 86.978 | 18.1688 | 0 | 2018-02-02 22:00 | 22 | 6 | 65.9769 | 13.7819 | 0
2018-02-02 23:00 | 23 | 6 | 0 | 0 | 0 | 2018-02-02 23:00 | 23 | 6 | 86.5202 | 18.0732 | 0 | 2018-02-02 23:00 | 23 | 6 | 86.9078 | 18.1542 | 0 | 2018-02-02 23:00 | 23 | 6 | 65.9026 | 13.7664 | 0
2018-02-03 | 0 | 7 | 86.0121 | 17.9671 | 0 | 2018-02-03 | 0 | 7 | 0 | 0 | 0 | 2018-02-03 | 0 | 7 | 86.5507 | 18.0796 | 0 | 2018-02-03 | 0 | 7 | 32.8893 | 6.8702 | 0
2018-02-03 01:00 | 1 | 7 | 85.919 | 17.9476 | 0 | 2018-02-03 01:00 | 1 | 7 | 0 | 0 | 0 | 2018-02-03 01:00 | 1 | 7 | 86.5324 | 18.0758 | 0 | 2018-02-03 01:00 | 1 | 7 | 32.8823 | 6.8688 | 0
2018-02-03 02:00 | 2 | 7 | 86.0533 | 17.9757 | 0 | 2018-02-03 02:00 | 2 | 7 | 0 | 0 | 0 | 2018-02-03 02:00 | 2 | 7 | 86.6453 | 18.0993 | 0 | 2018-02-03 02:00 | 2 | 7 | 32.9252 | 6.8777 | 0
2018-02-03 03:00 | 3 | 7 | 86.1677 | 17.9996 | 0 | 2018-02-03 03:00 | 3 | 7 | 0 | 0 | 0 | 2018-02-03 03:00 | 3 | 7 | 86.7002 | 18.1108 | 0 | 2018-02-03 03:00 | 3 | 7 | 32.9461 | 6.8821 | 0
2018-02-03 04:00 | 4 | 7 | 86.3081 | 18.0289 | 0 | 2018-02-03 04:00 | 4 | 7 | 0 | 0 | 0 | 2018-02-03 04:00 | 4 | 7 | 86.8513 | 18.1424 | 0 | 2018-02-03 04:00 | 4 | 7 | 33.0035 | 6.8941 | 0
2018-02-03 05:00 | 5 | 7 | 86.2562 | 18.0181 | 0 | 2018-02-03 05:00 | 5 | 7 | 0 | 0 | 0 | 2018-02-03 05:00 | 5 | 7 | 86.8605 | 18.1443 | 0 | 2018-02-03 05:00 | 5 | 7 | 33.007 | 6.8948 | 0
2018-02-03 06:00 | 6 | 7 | 86.1234 | 17.9903 | 0 | 2018-02-03 06:00 | 6 | 7 | 0 | 0 | 0 | 2018-02-03 06:00 | 6 | 7 | 86.6682 | 18.1041 | 0 | 2018-02-03 06:00 | 6 | 7 | 32.9339 | 6.8796 | 0
2018-02-03 07:00 | 7 | 7 | 86.1906 | 18.0044 | 0 | 2018-02-03 07:00 | 7 | 7 | 0 | 0 | 0 | 2018-02-03 07:00 | 7 | 7 | 86.7247 | 18.1159 | 0 | 2018-02-03 07:00 | 7 | 7 | 32.9554 | 6.8841 | 0
2018-02-03 08:00 | 8 | 7 | 86.36 | 18.0397 | 0 | 2018-02-03 08:00 | 8 | 7 | 0 | 0 | 0 | 2018-02-03 08:00 | 8 | 7 | 86.952 | 18.1634 | 0 | 2018-02-03 08:00 | 8 | 7 | 33.0418 | 6.9021 | 0
2018-02-03 09:00 | 9 | 7 | 86.4912 | 18.0671 | 0 | 2018-02-03 09:00 | 9 | 7 | 0 | 0 | 0 | 2018-02-03 09:00 | 9 | 7 | 87.0588 | 18.1857 | 0 | 2018-02-03 09:00 | 9 | 7 | 33.0823 | 6.9106 | 0
2018-02-03 10:00 | 10 | 7 | 86.1982 | 18.0059 | 0 | 2018-02-03 10:00 | 10 | 7 | 0 | 0 | 0 | 2018-02-03 10:00 | 10 | 7 | 86.6392 | 18.0981 | 0 | 2018-02-03 10:00 | 10 | 7 | 32.9229 | 6.8773 | 0
2018-02-03 11:00 | 11 | 7 | 86.1707 | 18.0002 | 0 | 2018-02-03 11:00 | 11 | 7 | 0 | 0 | 0 | 2018-02-03 11:00 | 11 | 7 | 86.8849 | 18.1494 | 0 | 2018-02-03 11:00 | 11 | 7 | 33.0163 | 6.8968 | 0
2018-02-03 12:00 | 12 | 7 | 86.5019 | 18.0694 | 0 | 2018-02-03 12:00 | 12 | 7 | 0 | 0 | 0 | 2018-02-03 12:00 | 12 | 7 | 87.1504 | 18.2048 | 0 | 2018-02-03 12:00 | 12 | 7 | 33.1172 | 6.9178 | 0
2018-02-03 13:00 | 13 | 7 | 86.6148 | 18.093 | 0 | 2018-02-03 13:00 | 13 | 7 | 0 | 0 | 0 | 2018-02-03 13:00 | 13 | 7 | 87.3167 | 18.2396 | 0 | 2018-02-03 13:00 | 13 | 7 | 33.1803 | 6.931 | 0
2018-02-03 14:00 | 14 | 7 | 86.4439 | 18.0573 | 0 | 2018-02-03 14:00 | 14 | 7 | 0 | 0 | 0 | 2018-02-03 14:00 | 14 | 7 | 87.0832 | 18.1908 | 0 | 2018-02-03 14:00 | 14 | 7 | 33.0916 | 6.9125 | 0
2018-02-03 15:00 | 15 | 7 | 86.5522 | 18.0799 | 0 | 2018-02-03 15:00 | 15 | 7 | 0 | 0 | 0 | 2018-02-03 15:00 | 15 | 7 | 87.2938 | 18.2348 | 0 | 2018-02-03 15:00 | 15 | 7 | 33.1716 | 6.9292 | 0
2018-02-03 16:00 | 16 | 7 | 86.5644 | 18.0824 | 0 | 2018-02-03 16:00 | 16 | 7 | 0 | 0 | 0 | 2018-02-03 16:00 | 16 | 7 | 87.3579 | 18.2482 | 0 | 2018-02-03 16:00 | 16 | 7 | 33.196 | 6.9343 | 0
2018-02-03 17:00 | 17 | 7 | 86.7445 | 18.1201 | 0 | 2018-02-03 17:00 | 17 | 7 | 0 | 0 | 0 | 2018-02-03 17:00 | 17 | 7 | 87.57 | 18.2925 | 0 | 2018-02-03 17:00 | 17 | 7 | 33.2766 | 6.9511 | 0
2018-02-03 18:00 | 18 | 7 | 86.4668 | 18.062 | 0 | 2018-02-03 18:00 | 18 | 7 | 0 | 0 | 0 | 2018-02-03 18:00 | 18 | 7 | 87.3014 | 18.2364 | 0 | 2018-02-03 18:00 | 18 | 7 | 33.1745 | 6.9298 | 0
2018-02-03 19:00 | 19 | 7 | 86.3661 | 18.041 | 0 | 2018-02-03 19:00 | 19 | 7 | 0 | 0 | 0 | 2018-02-03 19:00 | 19 | 7 | 87.0954 | 18.1934 | 0 | 2018-02-03 19:00 | 19 | 7 | 33.0963 | 6.9135 | 0
2018-02-03 20:00 | 20 | 7 | 86.1173 | 17.989 | 0 | 2018-02-03 20:00 | 20 | 7 | 0 | 0 | 0 | 2018-02-03 20:00 | 20 | 7 | 86.891 | 18.1507 | 0 | 2018-02-03 20:00 | 20 | 7 | 33.0186 | 6.8973 | 0
2018-02-03 21:00 | 21 | 7 | 86.1555 | 17.997 | 0 | 2018-02-03 21:00 | 21 | 7 | 0 | 0 | 0 | 2018-02-03 21:00 | 21 | 7 | 86.9245 | 18.1577 | 0 | 2018-02-03 21:00 | 21 | 7 | 33.0313 | 6.8999 | 0
2018-02-03 22:00 | 22 | 7 | 86.2211 | 18.0107 | 0 | 2018-02-03 22:00 | 22 | 7 | 0 | 0 | 0 | 2018-02-03 22:00 | 22 | 7 | 87.0054 | 18.1746 | 0 | 2018-02-03 22:00 | 22 | 7 | 33.0621 | 6.9063 | 0
2018-02-03 23:00 | 23 | 7 | 86.2226 | 18.011 | 0 | 2018-02-03 23:00 | 23 | 7 | 0 | 0 | 0 | 2018-02-03 23:00 | 23 | 7 | 87.0787 | 18.1899 | 0 | 2018-02-03 23:00 | 23 | 7 | 33.0899 | 6.9122 | 0
2018-02-04 | 0 | 1 | 86.2364 | 18.0139 | 0 | 2018-02-04 | 0 | 1 | 86.7994 | 18.1315 | 0 | 2018-02-04 | 0 | 1 | 0 | 0 | 0 | 2018-02-04 | 0 | 1 | 32.9838 | 6.89 | 0
2018-02-04 01:00 | 1 | 1 | 86.3188 | 18.0311 | 0 | 2018-02-04 01:00 | 1 | 1 | 86.952 | 18.1634 | 0 | 2018-02-04 01:00 | 1 | 1 | 0 | 0 | 0 | 2018-02-04 01:00 | 1 | 1 | 33.0418 | 6.9021 | 0
2018-02-04 02:00 | 2 | 1 | 86.2119 | 18.0088 | 0 | 2018-02-04 02:00 | 2 | 1 | 86.8177 | 18.1353 | 0 | 2018-02-04 02:00 | 2 | 1 | 0 | 0 | 0 | 2018-02-04 02:00 | 2 | 1 | 32.9907 | 6.8914 | 0
2018-02-04 03:00 | 3 | 1 | 86.1845 | 18.0031 | 0 | 2018-02-04 03:00 | 3 | 1 | 86.7857 | 18.1287 | 0 | 2018-02-04 03:00 | 3 | 1 | 0 | 0 | 0 | 2018-02-04 03:00 | 3 | 1 | 32.9786 | 6.8889 | 0
2018-02-04 04:00 | 4 | 1 | 86.2455 | 18.0158 | 0 | 2018-02-04 04:00 | 4 | 1 | 86.833 | 18.1385 | 0 | 2018-02-04 04:00 | 4 | 1 | 0 | 0 | 0 | 2018-02-04 04:00 | 4 | 1 | 32.9965 | 6.8926 | 0
2018-02-04 05:00 | 5 | 1 | 86.2333 | 18.0133 | 0 | 2018-02-04 05:00 | 5 | 1 | 86.833 | 18.1385 | 0 | 2018-02-04 05:00 | 5 | 1 | 0 | 0 | 0 | 2018-02-04 05:00 | 5 | 1 | 32.9965 | 6.8926 | 0
2018-02-04 06:00 | 6 | 1 | 86.2776 | 18.0225 | 0 | 2018-02-04 06:00 | 6 | 1 | 86.8528 | 18.1427 | 0 | 2018-02-04 06:00 | 6 | 1 | 0 | 0 | 0 | 2018-02-04 06:00 | 6 | 1 | 33.0041 | 6.8942 | 0
2018-02-04 07:00 | 7 | 1 | 86.2867 | 18.0244 | 0 | 2018-02-04 07:00 | 7 | 1 | 86.8452 | 18.1411 | 0 | 2018-02-04 07:00 | 7 | 1 | 0 | 0 | 0 | 2018-02-04 07:00 | 7 | 1 | 33.0012 | 6.8936 | 0
2018-02-04 08:00 | 8 | 1 | 86.2989 | 18.027 | 0 | 2018-02-04 08:00 | 8 | 1 | 86.9032 | 18.1532 | 0 | 2018-02-04 08:00 | 8 | 1 | 0 | 0 | 0 | 2018-02-04 08:00 | 8 | 1 | 33.0232 | 6.8982 | 0
2018-02-04 09:00 | 9 | 1 | 86.2867 | 18.0244 | 0 | 2018-02-04 09:00 | 9 | 1 | 86.8162 | 18.135 | 0 | 2018-02-04 09:00 | 9 | 1 | 0 | 0 | 0 | 2018-02-04 09:00 | 9 | 1 | 32.9902 | 6.8913 | 0
2018-02-04 10:00 | 10 | 1 | 86.2882 | 18.0247 | 0 | 2018-02-04 10:00 | 10 | 1 | 86.8528 | 18.1427 | 0 | 2018-02-04 10:00 | 10 | 1 | 0 | 0 | 0 | 2018-02-04 10:00 | 10 | 1 | 33.0041 | 6.8942 | 0
2018-02-04 11:00 | 11 | 1 | 86.1845 | 18.0031 | 0 | 2018-02-04 11:00 | 11 | 1 | 86.743 | 18.1197 | 0 | 2018-02-04 11:00 | 11 | 1 | 0 | 0 | 0 | 2018-02-04 11:00 | 11 | 1 | 32.9623 | 6.8855 | 0
2018-02-04 12:00 | 12 | 1 | 86.1418 | 17.9942 | 0 | 2018-02-04 12:00 | 12 | 1 | 86.714 | 18.1137 | 0 | 2018-02-04 12:00 | 12 | 1 | 0 | 0 | 0 | 2018-02-04 12:00 | 12 | 1 | 32.9513 | 6.8832 | 0
2018-02-04 13:00 | 13 | 1 | 86.1479 | 17.9954 | 0 | 2018-02-04 13:00 | 13 | 1 | 86.7659 | 18.1245 | 0 | 2018-02-04 13:00 | 13 | 1 | 0 | 0 | 0 | 2018-02-04 13:00 | 13 | 1 | 32.971 | 6.8873 | 0
2018-02-04 14:00 | 14 | 1 | 86.1112 | 17.9878 | 0 | 2018-02-04 14:00 | 14 | 1 | 86.7018 | 18.1111 | 0 | 2018-02-04 14:00 | 14 | 1 | 0 | 0 | 0 | 2018-02-04 14:00 | 14 | 1 | 32.9467 | 6.8822 | 0
2018-02-04 15:00 | 15 | 1 | 86.2455 | 18.0158 | 0 | 2018-02-04 15:00 | 15 | 1 | 86.8482 | 18.1417 | 0 | 2018-02-04 15:00 | 15 | 1 | 0 | 0 | 0 | 2018-02-04 15:00 | 15 | 1 | 33.0023 | 6.8939 | 0
2018-02-04 16:00 | 16 | 1 | 86.3447 | 18.0365 | 0 | 2018-02-04 16:00 | 16 | 1 | 86.9398 | 18.1609 | 0 | 2018-02-04 16:00 | 16 | 1 | 0 | 0 | 0 | 2018-02-04 16:00 | 16 | 1 | 33.0371 | 6.9011 | 0
2018-02-04 17:00 | 17 | 1 | 86.4805 | 18.0649 | 0 | 2018-02-04 17:00 | 17 | 1 | 86.9856 | 18.1704 | 0 | 2018-02-04 17:00 | 17 | 1 | 0 | 0 | 0 | 2018-02-04 17:00 | 17 | 1 | 33.0545 | 6.9048 | 0
2018-02-04 18:00 | 18 | 1 | 86.4332 | 18.055 | 0 | 2018-02-04 18:00 | 18 | 1 | 86.92 | 18.1567 | 0 | 2018-02-04 18:00 | 18 | 1 | 0 | 0 | 0 | 2018-02-04 18:00 | 18 | 1 | 33.0296 | 6.8996 | 0
2018-02-04 19:00 | 19 | 1 | 85.6794 | 17.8976 | 0 | 2018-02-04 19:00 | 19 | 1 | 85.9266 | 17.9492 | 0 | 2018-02-04 19:00 | 19 | 1 | 0 | 0 | 0 | 2018-02-04 19:00 | 19 | 1 | 32.6521 | 6.8207 | 0
2018-02-04 20:00 | 20 | 1 | 86.3294 | 18.0333 | 0 | 2018-02-04 20:00 | 20 | 1 | 86.5888 | 18.0875 | 0 | 2018-02-04 20:00 | 20 | 1 | 0 | 0 | 0 | 2018-02-04 20:00 | 20 | 1 | 32.9037 | 6.8733 | 0
2018-02-04 21:00 | 21 | 1 | 86.3569 | 18.0391 | 0 | 2018-02-04 21:00 | 21 | 1 | 86.6728 | 18.1051 | 0 | 2018-02-04 21:00 | 21 | 1 | 0 | 0 | 0 | 2018-02-04 21:00 | 21 | 1 | 32.9357 | 6.8799 | 0
2018-02-04 22:00 | 22 | 1 | 86.4881 | 18.0665 | 0 | 2018-02-04 22:00 | 22 | 1 | 86.8086 | 18.1334 | 0 | 2018-02-04 22:00 | 22 | 1 | 0 | 0 | 0 | 2018-02-04 22:00 | 22 | 1 | 32.9873 | 6.8907 | 0
2018-02-04 23:00 | 23 | 1 | 86.4332 | 18.055 | 0 | 2018-02-04 23:00 | 23 | 1 | 86.7353 | 18.1181 | 0 | 2018-02-04 23:00 | 23 | 1 | 0 | 0 | 0 | 2018-02-04 23:00 | 23 | 1 | 32.9594 | 6.8849 | 0
2018-02-05 | 0 | 2 | 86.4088 | 18.0499 | 0 | 2018-02-05 | 0 | 2 | 86.7002 | 18.1108 | 0 | 2018-02-05 | 0 | 2 | 86.9352 | 18.1599 | 0 | 2018-02-05 | 0 | 2 | 65.9815 | 13.7829 | 0
2018-02-05 01:00 | 1 | 2 | 86.0426 | 17.9734 | 0 | 2018-02-05 01:00 | 1 | 2 | 86.3127 | 18.0299 | 0 | 2018-02-05 01:00 | 1 | 2 | 86.5278 | 18.0748 | 0 | 2018-02-05 01:00 | 1 | 2 | 65.6794 | 13.7198 | 0
2018-02-05 02:00 | 2 | 2 | 86.392 | 18.0464 | 0 | 2018-02-05 02:00 | 2 | 2 | 86.6392 | 18.0981 | 0 | 2018-02-05 02:00 | 2 | 2 | 86.8421 | 18.1404 | 0 | 2018-02-05 02:00 | 2 | 2 | 65.9229 | 13.7706 | 0
2018-02-05 03:00 | 3 | 2 | 86.2776 | 18.0225 | 0 | 2018-02-05 03:00 | 3 | 2 | 86.5766 | 18.085 | 0 | 2018-02-05 03:00 | 3 | 2 | 86.7536 | 18.122 | 0 | 2018-02-05 03:00 | 3 | 2 | 65.8655 | 13.7586 | 0
2018-02-05 04:00 | 4 | 2 | 86.5034 | 18.0697 | 0 | 2018-02-05 04:00 | 4 | 2 | 86.8849 | 18.1494 | 0 | 2018-02-05 04:00 | 4 | 2 | 87.0283 | 18.1793 | 0 | 2018-02-05 04:00 | 4 | 2 | 66.087 | 13.8049 | 0
2018-02-05 05:00 | 5 | 2 | 86.3661 | 18.041 | 0 | 2018-02-05 05:00 | 5 | 2 | 86.772 | 18.1258 | 0 | 2018-02-05 05:00 | 5 | 2 | 87.0054 | 18.1746 | 0 | 2018-02-05 05:00 | 5 | 2 | 66.0354 | 13.7941 | 0
2018-02-05 06:00 | 6 | 2 | 86.2898 | 18.0251 | 0 | 2018-02-05 06:00 | 6 | 2 | 86.6499 | 18.1003 | 0 | 2018-02-05 06:00 | 6 | 2 | 86.8147 | 18.1347 | 0 | 2018-02-05 06:00 | 6 | 2 | 65.9165 | 13.7693 | 0
2018-02-05 07:00 | 7 | 2 | 86.2043 | 18.0072 | 0 | 2018-02-05 07:00 | 7 | 2 | 86.5278 | 18.0748 | 0 | 2018-02-05 07:00 | 7 | 2 | 86.7079 | 18.1124 | 0 | 2018-02-05 07:00 | 7 | 2 | 65.8296 | 13.7511 | 0
2018-02-05 08:00 | 8 | 2 | 86.3355 | 18.0346 | 0 | 2018-02-05 08:00 | 8 | 2 | 86.5461 | 18.0786 | 0 | 2018-02-05 08:00 | 8 | 2 | 86.8025 | 18.1322 | 0 | 2018-02-05 08:00 | 8 | 2 | 65.8725 | 13.7601 | 0
2018-02-05 09:00 | 9 | 2 | 86.3798 | 18.0439 | 0 | 2018-02-05 09:00 | 9 | 2 | 86.7262 | 18.1162 | 0 | 2018-02-05 09:00 | 9 | 2 | 86.8711 | 18.1465 | 0 | 2018-02-05 09:00 | 9 | 2 | 65.967 | 13.7798 | 0
2018-02-05 10:00 | 10 | 2 | 86.2272 | 18.012 | 0 | 2018-02-05 10:00 | 10 | 2 | 86.5156 | 18.0722 | 0 | 2018-02-05 10:00 | 10 | 2 | 86.714 | 18.1137 | 0 | 2018-02-05 10:00 | 10 | 2 | 65.8272 | 13.7507 | 0
2018-02-05 11:00 | 11 | 2 | 86.2119 | 18.0088 | 0 | 2018-02-05 11:00 | 11 | 2 | 86.5141 | 18.0719 | 0 | 2018-02-05 11:00 | 11 | 2 | 86.7201 | 18.115 | 0 | 2018-02-05 11:00 | 11 | 2 | 65.829 | 13.751 | 0
2018-02-05 12:00 | 12 | 2 | 86.389 | 18.0458 | 0 | 2018-02-05 12:00 | 12 | 2 | 86.6835 | 18.1073 | 0 | 2018-02-05 12:00 | 12 | 2 | 86.8574 | 18.1436 | 0 | 2018-02-05 12:00 | 12 | 2 | 65.9455 | 13.7754 | 0
2018-02-05 13:00 | 13 | 2 | 86.4027 | 18.0487 | 0 | 2018-02-05 13:00 | 13 | 2 | 86.6224 | 18.0946 | 0 | 2018-02-05 13:00 | 13 | 2 | 86.7475 | 18.1207 | 0 | 2018-02-05 13:00 | 13 | 2 | 65.8806 | 13.7618 | 0
2018-02-05 14:00 | 14 | 2 | 86.3783 | 18.0436 | 0 | 2018-02-05 14:00 | 14 | 2 | 86.6606 | 18.1025 | 0 | 2018-02-05 14:00 | 14 | 2 | 86.7903 | 18.1296 | 0 | 2018-02-05 14:00 | 14 | 2 | 65.9113 | 13.7682 | 0
2018-02-05 15:00 | 15 | 2 | 86.3355 | 18.0346 | 0 | 2018-02-05 15:00 | 15 | 2 | 86.5248 | 18.0742 | 0 | 2018-02-05 15:00 | 15 | 2 | 86.7384 | 18.1188 | 0 | 2018-02-05 15:00 | 15 | 2 | 65.84 | 13.7533 | 0
2018-02-05 16:00 | 16 | 2 | 86.3493 | 18.0375 | 0 | 2018-02-05 16:00 | 16 | 2 | 86.4912 | 18.0671 | 0 | 2018-02-05 16:00 | 16 | 2 | 86.685 | 18.1076 | 0 | 2018-02-05 16:00 | 16 | 2 | 65.807 | 13.7464 | 0
2018-02-05 17:00 | 17 | 2 | 86.244 | 18.0155 | 0 | 2018-02-05 17:00 | 17 | 2 | 86.4683 | 18.0624 | 0 | 2018-02-05 17:00 | 17 | 2 | 86.6743 | 18.1054 | 0 | 2018-02-05 17:00 | 17 | 2 | 65.7942 | 13.7437 | 0
2018-02-05 18:00 | 18 | 2 | 86.3142 | 18.0302 | 0 | 2018-02-05 18:00 | 18 | 2 | 86.4378 | 18.056 | 0 | 2018-02-05 18:00 | 18 | 2 | 86.5934 | 18.0885 | 0 | 2018-02-05 18:00 | 18 | 2 | 65.7519 | 13.7349 | 0
2018-02-05 19:00 | 19 | 2 | 86.2089 | 18.0082 | 0 | 2018-02-05 19:00 | 19 | 2 | 86.3508 | 18.0378 | 0 | 2018-02-05 19:00 | 19 | 2 | 86.5583 | 18.0812 | 0 | 2018-02-05 19:00 | 19 | 2 | 65.7055 | 13.7252 | 0
2018-02-05 20:00 | 20 | 2 | 86.2181 | 18.0101 | 0 | 2018-02-05 20:00 | 20 | 2 | 86.4836 | 18.0656 | 0 | 2018-02-05 20:00 | 20 | 2 | 86.6896 | 18.1086 | 0 | 2018-02-05 20:00 | 20 | 2 | 65.8058 | 13.7462 | 0
2018-02-05 21:00 | 21 | 2 | 86.1494 | 17.9957 | 0 | 2018-02-05 21:00 | 21 | 2 | 86.4759 | 18.064 | 0 | 2018-02-05 21:00 | 21 | 2 | 86.63 | 18.0961 | 0 | 2018-02-05 21:00 | 21 | 2 | 65.7802 | 13.7408 | 0
2018-02-05 22:00 | 22 | 2 | 86.2593 | 18.0187 | 0 | 2018-02-05 22:00 | 22 | 2 | 86.5522 | 18.0799 | 0 | 2018-02-05 22:00 | 22 | 2 | 86.6468 | 18.0997 | 0 | 2018-02-05 22:00 | 22 | 2 | 65.8156 | 13.7482 | 0
2018-02-05 23:00 | 23 | 2 | 86.4424 | 18.057 | 0 | 2018-02-05 23:00 | 23 | 2 | 86.8055 | 18.1328 | 0 | 2018-02-05 23:00 | 23 | 2 | 86.8864 | 18.1497 | 0 | 2018-02-05 23:00 | 23 | 2 | 66.0029 | 13.7874 | 0
2018-02-06 | 0 | 3 | 86.4637 | 18.0614 | 0 | 2018-02-06 | 0 | 3 | 0 | 0 | 0 | 2018-02-06 | 0 | 3 | 0 | 0 | 0 | 2018-02-06 | 0 | 3 | 0 | 0 | 0
2018-02-06 01:00 | 1 | 3 | 86.5629 | 18.0821 | 0 | 2018-02-06 01:00 | 1 | 3 | 0 | 0 | 0 | 2018-02-06 01:00 | 1 | 3 | 0 | 0 | 0 | 2018-02-06 01:00 | 1 | 3 | 0 | 0 | 0
2018-02-06 02:00 | 2 | 3 | 86.3706 | 18.042 | 0 | 2018-02-06 02:00 | 2 | 3 | 0 | 0 | 0 | 2018-02-06 02:00 | 2 | 3 | 0 | 0 | 0 | 2018-02-06 02:00 | 2 | 3 | 0 | 0 | 0
2018-02-06 03:00 | 3 | 3 | 86.3523 | 18.0381 | 0 | 2018-02-06 03:00 | 3 | 3 | 0 | 0 | 0 | 2018-02-06 03:00 | 3 | 3 | 0 | 0 | 0 | 2018-02-06 03:00 | 3 | 3 | 0 | 0 | 0
2018-02-06 04:00 | 4 | 3 | 86.3676 | 18.0413 | 0 | 2018-02-06 04:00 | 4 | 3 | 0 | 0 | 0 | 2018-02-06 04:00 | 4 | 3 | 0 | 0 | 0 | 2018-02-06 04:00 | 4 | 3 | 0 | 0 | 0
2018-02-06 05:00 | 5 | 3 | 86.4027 | 18.0487 | 0 | 2018-02-06 05:00 | 5 | 3 | 0 | 0 | 0 | 2018-02-06 05:00 | 5 | 3 | 0 | 0 | 0 | 2018-02-06 05:00 | 5 | 3 | 0 | 0 | 0
2018-02-06 06:00 | 6 | 3 | 86.4652 | 18.0617 | 0 | 2018-02-06 06:00 | 6 | 3 | 0 | 0 | 0 | 2018-02-06 06:00 | 6 | 3 | 0 | 0 | 0 | 2018-02-06 06:00 | 6 | 3 | 0 | 0 | 0
2018-02-06 07:00 | 7 | 3 | 86.4012 | 18.0483 | 0 | 2018-02-06 07:00 | 7 | 3 | 0 | 0 | 0 | 2018-02-06 07:00 | 7 | 3 | 0 | 0 | 0 | 2018-02-06 07:00 | 7 | 3 | 0 | 0 | 0
2018-02-06 08:00 | 8 | 3 | 86.4515 | 18.0589 | 0 | 2018-02-06 08:00 | 8 | 3 | 0 | 0 | 0 | 2018-02-06 08:00 | 8 | 3 | 0 | 0 | 0 | 2018-02-06 08:00 | 8 | 3 | 0 | 0 | 0
2018-02-06 09:00 | 9 | 3 | 86.2028 | 18.0069 | 0 | 2018-02-06 09:00 | 9 | 3 | 0 | 0 | 0 | 2018-02-06 09:00 | 9 | 3 | 0 | 0 | 0 | 2018-02-06 09:00 | 9 | 3 | 0 | 0 | 0
2018-02-06 10:00 | 10 | 3 | 86.2715 | 18.0213 | 0 | 2018-02-06 10:00 | 10 | 3 | 0 | 0 | 0 | 2018-02-06 10:00 | 10 | 3 | 0 | 0 | 0 | 2018-02-06 10:00 | 10 | 3 | 0 | 0 | 0
2018-02-06 11:00 | 11 | 3 | 86.7567 | 18.1226 | 0 | 2018-02-06 11:00 | 11 | 3 | 0 | 0 | 0 | 2018-02-06 11:00 | 11 | 3 | 0 | 0 | 0 | 2018-02-06 11:00 | 11 | 3 | 0 | 0 | 0
2018-02-06 12:00 | 12 | 3 | 86.6194 | 18.0939 | 0 | 2018-02-06 12:00 | 12 | 3 | 0 | 0 | 0 | 2018-02-06 12:00 | 12 | 3 | 0 | 0 | 0 | 2018-02-06 12:00 | 12 | 3 | 0 | 0 | 0
2018-02-06 13:00 | 13 | 3 | 86.6377 | 18.0977 | 0 | 2018-02-06 13:00 | 13 | 3 | 0 | 0 | 0 | 2018-02-06 13:00 | 13 | 3 | 0 | 0 | 0 | 2018-02-06 13:00 | 13 | 3 | 0 | 0 | 0
2018-02-06 14:00 | 14 | 3 | 86.8757 | 18.1475 | 0 | 2018-02-06 14:00 | 14 | 3 | 0 | 0 | 0 | 2018-02-06 14:00 | 14 | 3 | 0 | 0 | 0 | 2018-02-06 14:00 | 14 | 3 | 0 | 0 | 0
2018-02-06 15:00 | 15 | 3 | 86.7994 | 18.1315 | 0 | 2018-02-06 15:00 | 15 | 3 | 0 | 0 | 0 | 2018-02-06 15:00 | 15 | 3 | 0 | 0 | 0 | 2018-02-06 15:00 | 15 | 3 | 0 | 0 | 0
2018-02-06 16:00 | 16 | 3 | 86.7674 | 18.1248 | 0 | 2018-02-06 16:00 | 16 | 3 | 0 | 0 | 0 | 2018-02-06 16:00 | 16 | 3 | 0 | 0 | 0 | 2018-02-06 16:00 | 16 | 3 | 0 | 0 | 0
2018-02-06 17:00 | 17 | 3 | 86.7384 | 18.1188 | 0 | 2018-02-06 17:00 | 17 | 3 | 0 | 0 | 0 | 2018-02-06 17:00 | 17 | 3 | 0 | 0 | 0 | 2018-02-06 17:00 | 17 | 3 | 0 | 0 | 0
2018-02-06 18:00 | 18 | 3 | 86.7124 | 18.1134 | 0 | 2018-02-06 18:00 | 18 | 3 | 0 | 0 | 0 | 2018-02-06 18:00 | 18 | 3 | 0 | 0 | 0 | 2018-02-06 18:00 | 18 | 3 | 0 | 0 | 0
2018-02-06 19:00 | 19 | 3 | 86.8376 | 18.1395 | 0 | 2018-02-06 19:00 | 19 | 3 | 0 | 0 | 0 | 2018-02-06 19:00 | 19 | 3 | 0 | 0 | 0 | 2018-02-06 19:00 | 19 | 3 | 0 | 0 | 0
2018-02-06 20:00 | 20 | 3 | 86.627 | 18.0955 | 0 | 2018-02-06 20:00 | 20 | 3 | 0 | 0 | 0 | 2018-02-06 20:00 | 20 | 3 | 0 | 0 | 0 | 2018-02-06 20:00 | 20 | 3 | 0 | 0 | 0
2018-02-06 21:00 | 21 | 3 | 86.6239 | 18.0949 | 0 | 2018-02-06 21:00 | 21 | 3 | 0 | 0 | 0 | 2018-02-06 21:00 | 21 | 3 | 0 | 0 | 0 | 2018-02-06 21:00 | 21 | 3 | 0 | 0 | 0
2018-02-06 22:00 | 22 | 3 | 86.714 | 18.1137 | 0 | 2018-02-06 22:00 | 22 | 3 | 0 | 0 | 0 | 2018-02-06 22:00 | 22 | 3 | 0 | 0 | 0 | 2018-02-06 22:00 | 22 | 3 | 0 | 0 | 0
2018-02-06 23:00 | 23 | 3 | 86.8971 | 18.1519 | 0 | 2018-02-06 23:00 | 23 | 3 | 0 | 0 | 0 | 2018-02-06 23:00 | 23 | 3 | 0 | 0 | 0 | 2018-02-06 23:00 | 23 | 3 | 0 | 0 | 0
2018-02-07 | 0 | 4 | 0 | 0 | 0 | 2018-02-07 | 0 | 4 | 0 | 0 | 0 | 2018-02-07 | 0 | 4 | 86.6712 | 18.1047 | 0 | 2018-02-07 | 0 | 4 | 32.9351 | 6.8798 | 0
2018-02-07 01:00 | 1 | 4 | 0 | 0 | 0 | 2018-02-07 01:00 | 1 | 4 | 0 | 0 | 0 | 2018-02-07 01:00 | 1 | 4 | 86.511 | 18.0713 | 0 | 2018-02-07 01:00 | 1 | 4 | 32.8742 | 6.8671 | 0
2018-02-07 02:00 | 2 | 4 | 0 | 0 | 0 | 2018-02-07 02:00 | 2 | 4 | 0 | 0 | 0 | 2018-02-07 02:00 | 2 | 4 | 86.7628 | 18.1239 | 0 | 2018-02-07 02:00 | 2 | 4 | 32.9699 | 6.8871 | 0
2018-02-07 03:00 | 3 | 4 | 0 | 0 | 0 | 2018-02-07 03:00 | 3 | 4 | 0 | 0 | 0 | 2018-02-07 03:00 | 3 | 4 | 86.7384 | 18.1188 | 0 | 2018-02-07 03:00 | 3 | 4 | 32.9606 | 6.8851 | 0
2018-02-07 04:00 | 4 | 4 | 0 | 0 | 0 | 2018-02-07 04:00 | 4 | 4 | 0 | 0 | 0 | 2018-02-07 04:00 | 4 | 4 | 86.8376 | 18.1395 | 0 | 2018-02-07 04:00 | 4 | 4 | 32.9983 | 6.893 | 0
2018-02-07 05:00 | 5 | 4 | 0 | 0 | 0 | 2018-02-07 05:00 | 5 | 4 | 0 | 0 | 0 | 2018-02-07 05:00 | 5 | 4 | 87.0222 | 18.1781 | 0 | 2018-02-07 05:00 | 5 | 4 | 33.0684 | 6.9077 | 0
2018-02-07 06:00 | 6 | 4 | 0 | 0 | 0 | 2018-02-07 06:00 | 6 | 4 | 0 | 0 | 0 | 2018-02-07 06:00 | 6 | 4 | 86.9627 | 18.1656 | 0 | 2018-02-07 06:00 | 6 | 4 | 33.0458 | 6.9029 | 0
2018-02-07 07:00 | 7 | 4 | 0 | 0 | 0 | 2018-02-07 07:00 | 7 | 4 | 0 | 0 | 0 | 2018-02-07 07:00 | 7 | 4 | 87.1321 | 18.201 | 0 | 2018-02-07 07:00 | 7 | 4 | 33.1102 | 6.9164 | 0
2018-02-07 08:00 | 8 | 4 | 0 | 0 | 0 | 2018-02-07 08:00 | 8 | 4 | 0 | 0 | 0 | 2018-02-07 08:00 | 8 | 4 | 87.1931 | 18.2138 | 0 | 2018-02-07 08:00 | 8 | 4 | 33.1334 | 6.9212 | 0
2018-02-07 09:00 | 9 | 4 | 0 | 0 | 0 | 2018-02-07 09:00 | 9 | 4 | 0 | 0 | 0 | 2018-02-07 09:00 | 9 | 4 | 86.7155 | 18.114 | 0 | 2018-02-07 09:00 | 9 | 4 | 32.9519 | 6.8833 | 0
2018-02-07 10:00 | 10 | 4 | 0 | 0 | 0 | 2018-02-07 10:00 | 10 | 4 | 0 | 0 | 0 | 2018-02-07 10:00 | 10 | 4 | 86.6743 | 18.1054 | 0 | 2018-02-07 10:00 | 10 | 4 | 32.9362 | 6.88 | 0
2018-02-07 11:00 | 11 | 4 | 0 | 0 | 0 | 2018-02-07 11:00 | 11 | 4 | 0 | 0 | 0 | 2018-02-07 11:00 | 11 | 4 | 86.8956 | 18.1516 | 0 | 2018-02-07 11:00 | 11 | 4 | 33.0203 | 6.8976 | 0
2018-02-07 12:00 | 12 | 4 | 0 | 0 | 0 | 2018-02-07 12:00 | 12 | 4 | 0 | 0 | 0 | 2018-02-07 12:00 | 12 | 4 | 86.9276 | 18.1583 | 0 | 2018-02-07 12:00 | 12 | 4 | 33.0325 | 6.9002 | 0
2018-02-07 13:00 | 13 | 4 | 0 | 0 | 0 | 2018-02-07 13:00 | 13 | 4 | 0 | 0 | 0 | 2018-02-07 13:00 | 13 | 4 | 87.2541 | 18.2265 | 0 | 2018-02-07 13:00 | 13 | 4 | 33.1566 | 6.9261 | 0
2018-02-07 14:00 | 14 | 4 | 0 | 0 | 0 | 2018-02-07 14:00 | 14 | 4 | 0 | 0 | 0 | 2018-02-07 14:00 | 14 | 4 | 87.4037 | 18.2578 | 0 | 2018-02-07 14:00 | 14 | 4 | 33.2134 | 6.9379 | 0
2018-02-07 15:00 | 15 | 4 | 0 | 0 | 0 | 2018-02-07 15:00 | 15 | 4 | 0 | 0 | 0 | 2018-02-07 15:00 | 15 | 4 | 87.2129 | 18.2179 | 0 | 2018-02-07 15:00 | 15 | 4 | 33.1409 | 6.9228 | 0
2018-02-07 16:00 | 16 | 4 | 0 | 0 | 0 | 2018-02-07 16:00 | 16 | 4 | 0 | 0 | 0 | 2018-02-07 16:00 | 16 | 4 | 86.9718 | 18.1675 | 0 | 2018-02-07 16:00 | 16 | 4 | 33.0493 | 6.9037 | 0
2018-02-07 17:00 | 17 | 4 | 0 | 0 | 0 | 2018-02-07 17:00 | 17 | 4 | 0 | 0 | 0 | 2018-02-07 17:00 | 17 | 4 | 87.1397 | 18.2026 | 0 | 2018-02-07 17:00 | 17 | 4 | 33.1131 | 6.917 | 0
2018-02-07 18:00 | 18 | 4 | 0 | 0 | 0 | 2018-02-07 18:00 | 18 | 4 | 0 | 0 | 0 | 2018-02-07 18:00 | 18 | 4 | 87.2435 | 18.2243 | 0 | 2018-02-07 18:00 | 18 | 4 | 33.1525 | 6.9252 | 0
2018-02-07 19:00 | 19 | 4 | 0 | 0 | 0 | 2018-02-07 19:00 | 19 | 4 | 0 | 0 | 0 | 2018-02-07 19:00 | 19 | 4 | 86.8894 | 18.1503 | 0 | 2018-02-07 19:00 | 19 | 4 | 33.018 | 6.8971 | 0
2018-02-07 20:00 | 20 | 4 | 0 | 0 | 0 | 2018-02-07 20:00 | 20 | 4 | 0 | 0 | 0 | 2018-02-07 20:00 | 20 | 4 | 87.1839 | 18.2118 | 0 | 2018-02-07 20:00 | 20 | 4 | 33.1299 | 6.9205 | 0
2018-02-07 21:00 | 21 | 4 | 0 | 0 | 0 | 2018-02-07 21:00 | 21 | 4 | 0 | 0 | 0 | 2018-02-07 21:00 | 21 | 4 | 87.2419 | 18.224 | 0 | 2018-02-07 21:00 | 21 | 4 | 33.1519 | 6.9251 | 0
2018-02-07 22:00 | 22 | 4 | 0 | 0 | 0 | 2018-02-07 22:00 | 22 | 4 | 0 | 0 | 0 | 2018-02-07 22:00 | 22 | 4 | 87.1733 | 18.2096 | 0 | 2018-02-07 22:00 | 22 | 4 | 33.1259 | 6.9197 | 0
2018-02-07 23:00 | 23 | 4 | 0 | 0 | 0 | 2018-02-07 23:00 | 23 | 4 | 0 | 0 | 0 | 2018-02-07 23:00 | 23 | 4 | 87.2557 | 18.2268 | 0 | 2018-02-07 23:00 | 23 | 4 | 33.1572 | 6.9262 | 0
2018-02-08 | 0 | 5 | 86.5492 | 18.0793 | 0 | 2018-02-08 | 0 | 5 | 0 | 0 | 0 | 2018-02-08 | 0 | 5 | 0 | 0 | 0 | 2018-02-08 | 0 | 5 | 0 | 0 | 0
2018-02-08 01:00 | 1 | 5 | 86.7201 | 18.115 | 0 | 2018-02-08 01:00 | 1 | 5 | 0 | 0 | 0 | 2018-02-08 01:00 | 1 | 5 | 0 | 0 | 0 | 2018-02-08 01:00 | 1 | 5 | 0 | 0 | 0
2018-02-08 02:00 | 2 | 5 | 86.5095 | 18.071 | 0 | 2018-02-08 02:00 | 2 | 5 | 0 | 0 | 0 | 2018-02-08 02:00 | 2 | 5 | 0 | 0 | 0 | 2018-02-08 02:00 | 2 | 5 | 0 | 0 | 0
2018-02-08 03:00 | 3 | 5 | 86.4576 | 18.0601 | 0 | 2018-02-08 03:00 | 3 | 5 | 0 | 0 | 0 | 2018-02-08 03:00 | 3 | 5 | 0 | 0 | 0 | 2018-02-08 03:00 | 3 | 5 | 0 | 0 | 0
2018-02-08 04:00 | 4 | 5 | 86.6316 | 18.0965 | 0 | 2018-02-08 04:00 | 4 | 5 | 0 | 0 | 0 | 2018-02-08 04:00 | 4 | 5 | 0 | 0 | 0 | 2018-02-08 04:00 | 4 | 5 | 0 | 0 | 0
2018-02-08 05:00 | 5 | 5 | 86.569 | 18.0834 | 0 | 2018-02-08 05:00 | 5 | 5 | 0 | 0 | 0 | 2018-02-08 05:00 | 5 | 5 | 0 | 0 | 0 | 2018-02-08 05:00 | 5 | 5 | 0 | 0 | 0
2018-02-08 06:00 | 6 | 5 | 86.6468 | 18.0997 | 0 | 2018-02-08 06:00 | 6 | 5 | 0 | 0 | 0 | 2018-02-08 06:00 | 6 | 5 | 0 | 0 | 0 | 2018-02-08 06:00 | 6 | 5 | 0 | 0 | 0
2018-02-08 07:00 | 7 | 5 | 86.6361 | 18.0974 | 0 | 2018-02-08 07:00 | 7 | 5 | 0 | 0 | 0 | 2018-02-08 07:00 | 7 | 5 | 0 | 0 | 0 | 2018-02-08 07:00 | 7 | 5 | 0 | 0 | 0
2018-02-08 08:00 | 8 | 5 | 86.6819 | 18.107 | 0 | 2018-02-08 08:00 | 8 | 5 | 0 | 0 | 0 | 2018-02-08 08:00 | 8 | 5 | 0 | 0 | 0 | 2018-02-08 08:00 | 8 | 5 | 0 | 0 | 0
2018-02-08 09:00 | 9 | 5 | 86.7094 | 18.1127 | 0 | 2018-02-08 09:00 | 9 | 5 | 0 | 0 | 0 | 2018-02-08 09:00 | 9 | 5 | 0 | 0 | 0 | 2018-02-08 09:00 | 9 | 5 | 0 | 0 | 0
2018-02-08 10:00 | 10 | 5 | 86.7933 | 18.1303 | 0 | 2018-02-08 10:00 | 10 | 5 | 0 | 0 | 0 | 2018-02-08 10:00 | 10 | 5 | 0 | 0 | 0 | 2018-02-08 10:00 | 10 | 5 | 0 | 0 | 0
2018-02-08 11:00 | 11 | 5 | 86.8009 | 18.1318 | 0 | 2018-02-08 11:00 | 11 | 5 | 0 | 0 | 0 | 2018-02-08 11:00 | 11 | 5 | 0 | 0 | 0 | 2018-02-08 11:00 | 11 | 5 | 0 | 0 | 0
2018-02-08 12:00 | 12 | 5 | 86.6728 | 18.1051 | 0 | 2018-02-08 12:00 | 12 | 5 | 0 | 0 | 0 | 2018-02-08 12:00 | 12 | 5 | 0 | 0 | 0 | 2018-02-08 12:00 | 12 | 5 | 0 | 0 | 0
2018-02-08 13:00 | 13 | 5 | 86.6316 | 18.0965 | 0 | 2018-02-08 13:00 | 13 | 5 | 0 | 0 | 0 | 2018-02-08 13:00 | 13 | 5 | 0 | 0 | 0 | 2018-02-08 13:00 | 13 | 5 | 0 | 0 | 0
2018-02-08 14:00 | 14 | 5 | 86.6316 | 18.0965 | 0 | 2018-02-08 14:00 | 14 | 5 | 0 | 0 | 0 | 2018-02-08 14:00 | 14 | 5 | 0 | 0 | 0 | 2018-02-08 14:00 | 14 | 5 | 0 | 0 | 0
2018-02-08 15:00 | 15 | 5 | 86.6636 | 18.1032 | 0 | 2018-02-08 15:00 | 15 | 5 | 0 | 0 | 0 | 2018-02-08 15:00 | 15 | 5 | 0 | 0 | 0 | 2018-02-08 15:00 | 15 | 5 | 0 | 0 | 0
2018-02-08 16:00 | 16 | 5 | 86.5568 | 18.0808 | 0 | 2018-02-08 16:00 | 16 | 5 | 0 | 0 | 0 | 2018-02-08 16:00 | 16 | 5 | 0 | 0 | 0 | 2018-02-08 16:00 | 16 | 5 | 0 | 0 | 0
2018-02-08 17:00 | 17 | 5 | 86.6865 | 18.1079 | 0 | 2018-02-08 17:00 | 17 | 5 | 0 | 0 | 0 | 2018-02-08 17:00 | 17 | 5 | 0 | 0 | 0 | 2018-02-08 17:00 | 17 | 5 | 0 | 0 | 0
2018-02-08 18:00 | 18 | 5 | 86.7262 | 18.1162 | 0 | 2018-02-08 18:00 | 18 | 5 | 0 | 0 | 0 | 2018-02-08 18:00 | 18 | 5 | 0 | 0 | 0 | 2018-02-08 18:00 | 18 | 5 | 0 | 0 | 0
2018-02-08 19:00 | 19 | 5 | 86.5187 | 18.0729 | 0 | 2018-02-08 19:00 | 19 | 5 | 0 | 0 | 0 | 2018-02-08 19:00 | 19 | 5 | 0 | 0 | 0 | 2018-02-08 19:00 | 19 | 5 | 0 | 0 | 0
2018-02-08 20:00 | 20 | 5 | 86.5766 | 18.085 | 0 | 2018-02-08 20:00 | 20 | 5 | 0 | 0 | 0 | 2018-02-08 20:00 | 20 | 5 | 0 | 0 | 0 | 2018-02-08 20:00 | 20 | 5 | 0 | 0 | 0
2018-02-08 21:00 | 21 | 5 | 86.6194 | 18.0939 | 0 | 2018-02-08 21:00 | 21 | 5 | 0 | 0 | 0 | 2018-02-08 21:00 | 21 | 5 | 0 | 0 | 0 | 2018-02-08 21:00 | 21 | 5 | 0 | 0 | 0
2018-02-08 22:00 | 22 | 5 | 86.6743 | 18.1054 | 0 | 2018-02-08 22:00 | 22 | 5 | 0 | 0 | 0 | 2018-02-08 22:00 | 22 | 5 | 0 | 0 | 0 | 2018-02-08 22:00 | 22 | 5 | 0 | 0 | 0
2018-02-08 23:00 | 23 | 5 | 86.5644 | 18.0824 | 0 | 2018-02-08 23:00 | 23 | 5 | 0 | 0 | 0 | 2018-02-08 23:00 | 23 | 5 | 0 | 0 | 0 | 2018-02-08 23:00 | 23 | 5 | 0 | 0 | 0
2018-02-09 | 0 | 6 | 86.2226 | 18.011 | 0 | 2018-02-09 | 0 | 6 | 86.688 | 18.1083 | 0 | 2018-02-09 | 0 | 6 | 0 | 0 | 0 | 2018-02-09 | 0 | 6 | 32.9414 | 6.8811 | 0
2018-02-09 01:00 | 1 | 6 | 86.1128 | 17.9881 | 0 | 2018-02-09 01:00 | 1 | 6 | 86.5232 | 18.0738 | 0 | 2018-02-09 01:00 | 1 | 6 | 0 | 0 | 0 | 2018-02-09 01:00 | 1 | 6 | 32.8788 | 6.8681 | 0
2018-02-09 02:00 | 2 | 6 | 86.2791 | 18.0228 | 0 | 2018-02-09 02:00 | 2 | 6 | 86.6896 | 18.1086 | 0 | 2018-02-09 02:00 | 2 | 6 | 0 | 0 | 0 | 2018-02-09 02:00 | 2 | 6 | 32.942 | 6.8813 | 0
2018-02-09 03:00 | 3 | 6 | 86.0014 | 17.9648 | 0 | 2018-02-09 03:00 | 3 | 6 | 86.4485 | 18.0582 | 0 | 2018-02-09 03:00 | 3 | 6 | 0 | 0 | 0 | 2018-02-09 03:00 | 3 | 6 | 32.8504 | 6.8621 | 0
2018-02-09 04:00 | 4 | 6 | 86.0533 | 17.9757 | 0 | 2018-02-09 04:00 | 4 | 6 | 86.4347 | 18.0553 | 0 | 2018-02-09 04:00 | 4 | 6 | 0 | 0 | 0 | 2018-02-09 04:00 | 4 | 6 | 32.8452 | 6.861 | 0
2018-02-09 05:00 | 5 | 6 | 86.2257 | 18.0117 | 0 | 2018-02-09 05:00 | 5 | 6 | 86.6117 | 18.0923 | 0 | 2018-02-09 05:00 | 5 | 6 | 0 | 0 | 0 | 2018-02-09 05:00 | 5 | 6 | 32.9124 | 6.8751 | 0
2018-02-09 06:00 | 6 | 6 | 86.4332 | 18.055 | 0 | 2018-02-09 06:00 | 6 | 6 | 86.9352 | 18.1599 | 0 | 2018-02-09 06:00 | 6 | 6 | 0 | 0 | 0 | 2018-02-09 06:00 | 6 | 6 | 33.0354 | 6.9008 | 0
2018-02-09 07:00 | 7 | 6 | 86.5873 | 18.0872 | 0 | 2018-02-09 07:00 | 7 | 6 | 87.0619 | 18.1864 | 0 | 2018-02-09 07:00 | 7 | 6 | 0 | 0 | 0 | 2018-02-09 07:00 | 7 | 6 | 33.0835 | 6.9108 | 0
2018-02-09 08:00 | 8 | 6 | 86.3691 | 18.0416 | 0 | 2018-02-09 08:00 | 8 | 6 | 86.7811 | 18.1277 | 0 | 2018-02-09 08:00 | 8 | 6 | 0 | 0 | 0 | 2018-02-09 08:00 | 8 | 6 | 32.9768 | 6.8885 | 0
2018-02-09 09:00 | 9 | 6 | 86.334 | 18.0343 | 0 | 2018-02-09 09:00 | 9 | 6 | 86.7399 | 18.1191 | 0 | 2018-02-09 09:00 | 9 | 6 | 0 | 0 | 0 | 2018-02-09 09:00 | 9 | 6 | 32.9612 | 6.8853 | 0
2018-02-09 10:00 | 10 | 6 | 86.5126 | 18.0716 | 0 | 2018-02-09 10:00 | 10 | 6 | 86.862 | 18.1446 | 0 | 2018-02-09 10:00 | 10 | 6 | 0 | 0 | 0 | 2018-02-09 10:00 | 10 | 6 | 33.0076 | 6.8949 | 0
2018-02-09 11:00 | 11 | 6 | 86.5003 | 18.069 | 0 | 2018-02-09 11:00 | 11 | 6 | 86.9306 | 18.1589 | 0 | 2018-02-09 11:00 | 11 | 6 | 0 | 0 | 0 | 2018-02-09 11:00 | 11 | 6 | 33.0336 | 6.9004 | 0
2018-02-09 12:00 | 12 | 6 | 86.7002 | 18.1108 | 0 | 2018-02-09 12:00 | 12 | 6 | 87.1412 | 18.2029 | 0 | 2018-02-09 12:00 | 12 | 6 | 0 | 0 | 0 | 2018-02-09 12:00 | 12 | 6 | 33.1137 | 6.9171 | 0
2018-02-09 13:00 | 13 | 6 | 86.363 | 18.0404 | 0 | 2018-02-09 13:00 | 13 | 6 | 86.8009 | 18.1318 | 0 | 2018-02-09 13:00 | 13 | 6 | 0 | 0 | 0 | 2018-02-09 13:00 | 13 | 6 | 32.9843 | 6.8901 | 0
2018-02-09 14:00 | 14 | 6 | 86.4408 | 18.0566 | 0 | 2018-02-09 14:00 | 14 | 6 | 86.8635 | 18.1449 | 0 | 2018-02-09 14:00 | 14 | 6 | 0 | 0 | 0 | 2018-02-09 14:00 | 14 | 6 | 33.0081 | 6.8951 | 0
2018-02-09 15:00 | 15 | 6 | 86.2943 | 18.026 | 0 | 2018-02-09 15:00 | 15 | 6 | 86.6743 | 18.1054 | 0 | 2018-02-09 15:00 | 15 | 6 | 0 | 0 | 0 | 2018-02-09 15:00 | 15 | 6 | 32.9362 | 6.88 | 0
2018-02-09 16:00 | 16 | 6 | 86.3706 | 18.042 | 0 | 2018-02-09 16:00 | 16 | 6 | 86.7491 | 18.121 | 0 | 2018-02-09 16:00 | 16 | 6 | 0 | 0 | 0 | 2018-02-09 16:00 | 16 | 6 | 32.9647 | 6.886 | 0
2018-02-09 17:00 | 17 | 6 | 86.2882 | 18.0247 | 0 | 2018-02-09 17:00 | 17 | 6 | 86.7445 | 18.1201 | 0 | 2018-02-09 17:00 | 17 | 6 | 0 | 0 | 0 | 2018-02-09 17:00 | 17 | 6 | 32.9629 | 6.8856 | 0
2018-02-09 18:00 | 18 | 6 | 86.1875 | 18.0037 | 0 | 2018-02-09 18:00 | 18 | 6 | 86.6667 | 18.1038 | 0 | 2018-02-09 18:00 | 18 | 6 | 0 | 0 | 0 | 2018-02-09 18:00 | 18 | 6 | 32.9333 | 6.8794 | 0
2018-02-09 19:00 | 19 | 6 | 86.099 | 17.9852 | 0 | 2018-02-09 19:00 | 19 | 6 | 86.5431 | 18.078 | 0 | 2018-02-09 19:00 | 19 | 6 | 0 | 0 | 0 | 2018-02-09 19:00 | 19 | 6 | 32.8864 | 6.8696 | 0
2018-02-09 20:00 | 20 | 6 | 86.1997 | 18.0063 | 0 | 2018-02-09 20:00 | 20 | 6 | 86.5187 | 18.0729 | 0 | 2018-02-09 20:00 | 20 | 6 | 0 | 0 | 0 | 2018-02-09 20:00 | 20 | 6 | 32.8771 | 6.8677 | 0
2018-02-09 21:00 | 21 | 6 | 86.3767 | 18.0432 | 0 | 2018-02-09 21:00 | 21 | 6 | 86.7247 | 18.1159 | 0 | 2018-02-09 21:00 | 21 | 6 | 0 | 0 | 0 | 2018-02-09 21:00 | 21 | 6 | 32.9554 | 6.8841 | 0
2018-02-09 22:00 | 22 | 6 | 86.3691 | 18.0416 | 0 | 2018-02-09 22:00 | 22 | 6 | 86.7659 | 18.1245 | 0 | 2018-02-09 22:00 | 22 | 6 | 0 | 0 | 0 | 2018-02-09 22:00 | 22 | 6 | 32.971 | 6.8873 | 0
2018-02-09 23:00 | 23 | 6 | 86.4012 | 18.0483 | 0 | 2018-02-09 23:00 | 23 | 6 | 86.7918 | 18.1299 | 0 | 2018-02-09 23:00 | 23 | 6 | 0 | 0 | 0 | 2018-02-09 23:00 | 23 | 6 | 32.9809 | 6.8894 | 0
2018-02-10 | 0 | 7 | 86.0121 | 17.9671 | 0 | 2018-02-10 | 0 | 7 | 0 | 0 | 0 | 2018-02-10 | 0 | 7 | 86.5507 | 18.0796 | 0 | 2018-02-10 | 0 | 7 | 32.8893 | 6.8702 | 0
2018-02-10 01:00 | 1 | 7 | 85.919 | 17.9476 | 0 | 2018-02-10 01:00 | 1 | 7 | 0 | 0 | 0 | 2018-02-10 01:00 | 1 | 7 | 86.5324 | 18.0758 | 0 | 2018-02-10 01:00 | 1 | 7 | 32.8823 | 6.8688 | 0
2018-02-10 02:00 | 2 | 7 | 86.0533 | 17.9757 | 0 | 2018-02-10 02:00 | 2 | 7 | 0 | 0 | 0 | 2018-02-10 02:00 | 2 | 7 | 86.6453 | 18.0993 | 0 | 2018-02-10 02:00 | 2 | 7 | 32.9252 | 6.8777 | 0
2018-02-10 03:00 | 3 | 7 | 86.1677 | 17.9996 | 0 | 2018-02-10 03:00 | 3 | 7 | 0 | 0 | 0 | 2018-02-10 03:00 | 3 | 7 | 86.7002 | 18.1108 | 0 | 2018-02-10 03:00 | 3 | 7 | 32.9461 | 6.8821 | 0
2018-02-10 04:00 | 4 | 7 | 86.3081 | 18.0289 | 0 | 2018-02-10 04:00 | 4 | 7 | 0 | 0 | 0 | 2018-02-10 04:00 | 4 | 7 | 86.8513 | 18.1424 | 0 | 2018-02-10 04:00 | 4 | 7 | 33.0035 | 6.8941 | 0
2018-02-10 05:00 | 5 | 7 | 86.2562 | 18.0181 | 0 | 2018-02-10 05:00 | 5 | 7 | 0 | 0 | 0 | 2018-02-10 05:00 | 5 | 7 | 86.8605 | 18.1443 | 0 | 2018-02-10 05:00 | 5 | 7 | 33.007 | 6.8948 | 0
2018-02-10 06:00 | 6 | 7 | 86.1234 | 17.9903 | 0 | 2018-02-10 06:00 | 6 | 7 | 0 | 0 | 0 | 2018-02-10 06:00 | 6 | 7 | 86.6682 | 18.1041 | 0 | 2018-02-10 06:00 | 6 | 7 | 32.9339 | 6.8796 | 0
2018-02-10 07:00 | 7 | 7 | 86.1906 | 18.0044 | 0 | 2018-02-10 07:00 | 7 | 7 | 0 | 0 | 0 | 2018-02-10 07:00 | 7 | 7 | 86.7247 | 18.1159 | 0 | 2018-02-10 07:00 | 7 | 7 | 32.9554 | 6.8841 | 0
2018-02-10 08:00 | 8 | 7 | 86.36 | 18.0397 | 0 | 2018-02-10 08:00 | 8 | 7 | 0 | 0 | 0 | 2018-02-10 08:00 | 8 | 7 | 86.952 | 18.1634 | 0 | 2018-02-10 08:00 | 8 | 7 | 33.0418 | 6.9021 | 0
2018-02-10 09:00 | 9 | 7 | 86.4912 | 18.0671 | 0 | 2018-02-10 09:00 | 9 | 7 | 0 | 0 | 0 | 2018-02-10 09:00 | 9 | 7 | 87.0588 | 18.1857 | 0 | 2018-02-10 09:00 | 9 | 7 | 33.0823 | 6.9106 | 0
2018-02-10 10:00 | 10 | 7 | 86.1982 | 18.0059 | 0 | 2018-02-10 10:00 | 10 | 7 | 0 | 0 | 0 | 2018-02-10 10:00 | 10 | 7 | 86.6392 | 18.0981 | 0 | 2018-02-10 10:00 | 10 | 7 | 32.9229 | 6.8773 | 0
2018-02-10 11:00 | 11 | 7 | 86.1707 | 18.0002 | 0 | 2018-02-10 11:00 | 11 | 7 | 0 | 0 | 0 | 2018-02-10 11:00 | 11 | 7 | 86.8849 | 18.1494 | 0 | 2018-02-10 11:00 | 11 | 7 | 33.0163 | 6.8968 | 0
2018-02-10 12:00 | 12 | 7 | 86.5019 | 18.0694 | 0 | 2018-02-10 12:00 | 12 | 7 | 0 | 0 | 0 | 2018-02-10 12:00 | 12 | 7 | 87.1504 | 18.2048 | 0 | 2018-02-10 12:00 | 12 | 7 | 33.1172 | 6.9178 | 0
2018-02-10 13:00 | 13 | 7 | 86.6148 | 18.093 | 0 | 2018-02-10 13:00 | 13 | 7 | 0 | 0 | 0 | 2018-02-10 13:00 | 13 | 7 | 87.3167 | 18.2396 | 0 | 2018-02-10 13:00 | 13 | 7 | 33.1803 | 6.931 | 0
2018-02-10 14:00 | 14 | 7 | 86.4439 | 18.0573 | 0 | 2018-02-10 14:00 | 14 | 7 | 0 | 0 | 0 | 2018-02-10 14:00 | 14 | 7 | 87.0832 | 18.1908 | 0 | 2018-02-10 14:00 | 14 | 7 | 33.0916 | 6.9125 | 0
2018-02-10 15:00 | 15 | 7 | 86.5522 | 18.0799 | 0 | 2018-02-10 15:00 | 15 | 7 | 0 | 0 | 0 | 2018-02-10 15:00 | 15 | 7 | 87.2938 | 18.2348 | 0 | 2018-02-10 15:00 | 15 | 7 | 33.1716 | 6.9292 | 0
2018-02-10 16:00 | 16 | 7 | 86.5644 | 18.0824 | 0 | 2018-02-10 16:00 | 16 | 7 | 0 | 0 | 0 | 2018-02-10 16:00 | 16 | 7 | 87.3579 | 18.2482 | 0 | 2018-02-10 16:00 | 16 | 7 | 33.196 | 6.9343 | 0
2018-02-10 17:00 | 17 | 7 | 86.7445 | 18.1201 | 0 | 2018-02-10 17:00 | 17 | 7 | 0 | 0 | 0 | 2018-02-10 17:00 | 17 | 7 | 87.57 | 18.2925 | 0 | 2018-02-10 17:00 | 17 | 7 | 33.2766 | 6.9511 | 0
2018-02-10 18:00 | 18 | 7 | 86.4668 | 18.062 | 0 | 2018-02-10 18:00 | 18 | 7 | 0 | 0 | 0 | 2018-02-10 18:00 | 18 | 7 | 87.3014 | 18.2364 | 0 | 2018-02-10 18:00 | 18 | 7 | 33.1745 | 6.9298 | 0
2018-02-10 19:00 | 19 | 7 | 86.3661 | 18.041 | 0 | 2018-02-10 19:00 | 19 | 7 | 0 | 0 | 0 | 2018-02-10 19:00 | 19 | 7 | 87.0954 | 18.1934 | 0 | 2018-02-10 19:00 | 19 | 7 | 33.0963 | 6.9135 | 0
2018-02-10 20:00 | 20 | 7 | 86.1173 | 17.989 | 0 | 2018-02-10 20:00 | 20 | 7 | 0 | 0 | 0 | 2018-02-10 20:00 | 20 | 7 | 86.891 | 18.1507 | 0 | 2018-02-10 20:00 | 20 | 7 | 33.0186 | 6.8973 | 0
2018-02-10 21:00 | 21 | 7 | 86.1555 | 17.997 | 0 | 2018-02-10 21:00 | 21 | 7 | 0 | 0 | 0 | 2018-02-10 21:00 | 21 | 7 | 86.9245 | 18.1577 | 0 | 2018-02-10 21:00 | 21 | 7 | 33.0313 | 6.8999 | 0
2018-02-10 22:00 | 22 | 7 | 86.2211 | 18.0107 | 0 | 2018-02-10 22:00 | 22 | 7 | 0 | 0 | 0 | 2018-02-10 22:00 | 22 | 7 | 87.0054 | 18.1746 | 0 | 2018-02-10 22:00 | 22 | 7 | 33.0621 | 6.9063 | 0
2018-02-10 23:00 | 23 | 7 | 86.2226 | 18.011 | 0 | 2018-02-10 23:00 | 23 | 7 | 0 | 0 | 0 | 2018-02-10 23:00 | 23 | 7 | 87.0787 | 18.1899 | 0 | 2018-02-10 23:00 | 23 | 7 | 33.0899 | 6.9122 | 0
2018-02-11 | 0 | 1 | 86.2364 | 18.0139 | 0 | 2018-02-11 | 0 | 1 | 86.7994 | 18.1315 | 0 | 2018-02-11 | 0 | 1 | 0 | 0 | 0 | 2018-02-11 | 0 | 1 | 32.9838 | 6.89 | 0
2018-02-11 01:00 | 1 | 1 | 86.3188 | 18.0311 | 0 | 2018-02-11 01:00 | 1 | 1 | 86.952 | 18.1634 | 0 | 2018-02-11 01:00 | 1 | 1 | 0 | 0 | 0 | 2018-02-11 01:00 | 1 | 1 | 33.0418 | 6.9021 | 0
2018-02-11 02:00 | 2 | 1 | 86.2119 | 18.0088 | 0 | 2018-02-11 02:00 | 2 | 1 | 86.8177 | 18.1353 | 0 | 2018-02-11 02:00 | 2 | 1 | 0 | 0 | 0 | 2018-02-11 02:00 | 2 | 1 | 32.9907 | 6.8914 | 0
2018-02-11 03:00 | 3 | 1 | 86.1845 | 18.0031 | 0 | 2018-02-11 03:00 | 3 | 1 | 86.7857 | 18.1287 | 0 | 2018-02-11 03:00 | 3 | 1 | 0 | 0 | 0 | 2018-02-11 03:00 | 3 | 1 | 32.9786 | 6.8889 | 0
2018-02-11 04:00 | 4 | 1 | 86.2455 | 18.0158 | 0 | 2018-02-11 04:00 | 4 | 1 | 86.833 | 18.1385 | 0 | 2018-02-11 04:00 | 4 | 1 | 0 | 0 | 0 | 2018-02-11 04:00 | 4 | 1 | 32.9965 | 6.8926 | 0
2018-02-11 05:00 | 5 | 1 | 86.2333 | 18.0133 | 0 | 2018-02-11 05:00 | 5 | 1 | 86.833 | 18.1385 | 0 | 2018-02-11 05:00 | 5 | 1 | 0 | 0 | 0 | 2018-02-11 05:00 | 5 | 1 | 32.9965 | 6.8926 | 0
2018-02-11 06:00 | 6 | 1 | 86.2776 | 18.0225 | 0 | 2018-02-11 06:00 | 6 | 1 | 86.8528 | 18.1427 | 0 | 2018-02-11 06:00 | 6 | 1 | 0 | 0 | 0 | 2018-02-11 06:00 | 6 | 1 | 33.0041 | 6.8942 | 0
2018-02-11 07:00 | 7 | 1 | 86.2867 | 18.0244 | 0 | 2018-02-11 07:00 | 7 | 1 | 86.8452 | 18.1411 | 0 | 2018-02-11 07:00 | 7 | 1 | 0 | 0 | 0 | 2018-02-11 07:00 | 7 | 1 | 33.0012 | 6.8936 | 0
2018-02-11 08:00 | 8 | 1 | 86.2989 | 18.027 | 0 | 2018-02-11 08:00 | 8 | 1 | 86.9032 | 18.1532 | 0 | 2018-02-11 08:00 | 8 | 1 | 0 | 0 | 0 | 2018-02-11 08:00 | 8 | 1 | 33.0232 | 6.8982 | 0
2018-02-11 09:00 | 9 | 1 | 86.2867 | 18.0244 | 0 | 2018-02-11 09:00 | 9 | 1 | 86.8162 | 18.135 | 0 | 2018-02-11 09:00 | 9 | 1 | 0 | 0 | 0 | 2018-02-11 09:00 | 9 | 1 | 32.9902 | 6.8913 | 0
2018-02-11 10:00 | 10 | 1 | 86.2882 | 18.0247 | 0 | 2018-02-11 10:00 | 10 | 1 | 86.8528 | 18.1427 | 0 | 2018-02-11 10:00 | 10 | 1 | 0 | 0 | 0 | 2018-02-11 10:00 | 10 | 1 | 33.0041 | 6.8942 | 0
2018-02-11 11:00 | 11 | 1 | 86.1845 | 18.0031 | 0 | 2018-02-11 11:00 | 11 | 1 | 86.743 | 18.1197 | 0 | 2018-02-11 11:00 | 11 | 1 | 0 | 0 | 0 | 2018-02-11 11:00 | 11 | 1 | 32.9623 | 6.8855 | 0
2018-02-11 12:00 | 12 | 1 | 86.1418 | 17.9942 | 0 | 2018-02-11 12:00 | 12 | 1 | 86.714 | 18.1137 | 0 | 2018-02-11 12:00 | 12 | 1 | 0 | 0 | 0 | 2018-02-11 12:00 | 12 | 1 | 32.9513 | 6.8832 | 0
2018-02-11 13:00 | 13 | 1 | 86.1479 | 17.9954 | 0 | 2018-02-11 13:00 | 13 | 1 | 86.7659 | 18.1245 | 0 | 2018-02-11 13:00 | 13 | 1 | 0 | 0 | 0 | 2018-02-11 13:00 | 13 | 1 | 32.971 | 6.8873 | 0
2018-02-11 14:00 | 14 | 1 | 86.1112 | 17.9878 | 0 | 2018-02-11 14:00 | 14 | 1 | 86.7018 | 18.1111 | 0 | 2018-02-11 14:00 | 14 | 1 | 0 | 0 | 0 | 2018-02-11 14:00 | 14 | 1 | 32.9467 | 6.8822 | 0
2018-02-11 15:00 | 15 | 1 | 86.2455 | 18.0158 | 0 | 2018-02-11 15:00 | 15 | 1 | 86.8482 | 18.1417 | 0 | 2018-02-11 15:00 | 15 | 1 | 0 | 0 | 0 | 2018-02-11 15:00 | 15 | 1 | 33.0023 | 6.8939 | 0
2018-02-11 16:00 | 16 | 1 | 86.3447 | 18.0365 | 0 | 2018-02-11 16:00 | 16 | 1 | 86.9398 | 18.1609 | 0 | 2018-02-11 16:00 | 16 | 1 | 0 | 0 | 0 | 2018-02-11 16:00 | 16 | 1 | 33.0371 | 6.9011 | 0
2018-02-11 17:00 | 17 | 1 | 86.4805 | 18.0649 | 0 | 2018-02-11 17:00 | 17 | 1 | 86.9856 | 18.1704 | 0 | 2018-02-11 17:00 | 17 | 1 | 0 | 0 | 0 | 2018-02-11 17:00 | 17 | 1 | 33.0545 | 6.9048 | 0
2018-02-11 18:00 | 18 | 1 | 86.4332 | 18.055 | 0 | 2018-02-11 18:00 | 18 | 1 | 86.92 | 18.1567 | 0 | 2018-02-11 18:00 | 18 | 1 | 0 | 0 | 0 | 2018-02-11 18:00 | 18 | 1 | 33.0296 | 6.8996 | 0
2018-02-11 19:00 | 19 | 1 | 85.6794 | 17.8976 | 0 | 2018-02-11 19:00 | 19 | 1 | 85.9266 | 17.9492 | 0 | 2018-02-11 19:00 | 19 | 1 | 0 | 0 | 0 | 2018-02-11 19:00 | 19 | 1 | 32.6521 | 6.8207 | 0
2018-02-11 20:00 | 20 | 1 | 86.3294 | 18.0333 | 0 | 2018-02-11 20:00 | 20 | 1 | 86.5888 | 18.0875 | 0 | 2018-02-11 20:00 | 20 | 1 | 0 | 0 | 0 | 2018-02-11 20:00 | 20 | 1 | 32.9037 | 6.8733 | 0
2018-02-11 21:00 | 21 | 1 | 86.3569 | 18.0391 | 0 | 2018-02-11 21:00 | 21 | 1 | 86.6728 | 18.1051 | 0 | 2018-02-11 21:00 | 21 | 1 | 0 | 0 | 0 | 2018-02-11 21:00 | 21 | 1 | 32.9357 | 6.8799 | 0
2018-02-11 22:00 | 22 | 1 | 86.4881 | 18.0665 | 0 | 2018-02-11 22:00 | 22 | 1 | 86.8086 | 18.1334 | 0 | 2018-02-11 22:00 | 22 | 1 | 0 | 0 | 0 | 2018-02-11 22:00 | 22 | 1 | 32.9873 | 6.8907 | 0
2018-02-11 23:00 | 23 | 1 | 86.4332 | 18.055 | 0 | 2018-02-11 23:00 | 23 | 1 | 86.7353 | 18.1181 | 0 | 2018-02-11 23:00 | 23 | 1 | 0 | 0 | 0 | 2018-02-11 23:00 | 23 | 1 | 32.9594 | 6.8849 | 0
2018-02-12 | 0 | 2 | 86.4088 | 18.0499 | 0 | 2018-02-12 | 0 | 2 | 86.7002 | 18.1108 | 0 | 2018-02-12 | 0 | 2 | 86.9352 | 18.1599 | 0 | 2018-02-12 | 0 | 2 | 65.9815 | 13.7829 | 0
2018-02-12 01:00 | 1 | 2 | 86.0426 | 17.9734 | 0 | 2018-02-12 01:00 | 1 | 2 | 86.3127 | 18.0299 | 0 | 2018-02-12 01:00 | 1 | 2 | 86.5278 | 18.0748 | 0 | 2018-02-12 01:00 | 1 | 2 | 65.6794 | 13.7198 | 0
2018-02-12 02:00 | 2 | 2 | 86.392 | 18.0464 | 0 | 2018-02-12 02:00 | 2 | 2 | 86.6392 | 18.0981 | 0 | 2018-02-12 02:00 | 2 | 2 | 86.8421 | 18.1404 | 0 | 2018-02-12 02:00 | 2 | 2 | 65.9229 | 13.7706 | 0
2018-02-12 03:00 | 3 | 2 | 86.2776 | 18.0225 | 0 | 2018-02-12 03:00 | 3 | 2 | 86.5766 | 18.085 | 0 | 2018-02-12 03:00 | 3 | 2 | 86.7536 | 18.122 | 0 | 2018-02-12 03:00 | 3 | 2 | 65.8655 | 13.7586 | 0
2018-02-12 04:00 | 4 | 2 | 86.5034 | 18.0697 | 0 | 2018-02-12 04:00 | 4 | 2 | 86.8849 | 18.1494 | 0 | 2018-02-12 04:00 | 4 | 2 | 87.0283 | 18.1793 | 0 | 2018-02-12 04:00 | 4 | 2 | 66.087 | 13.8049 | 0
2018-02-12 05:00 | 5 | 2 | 86.3661 | 18.041 | 0 | 2018-02-12 05:00 | 5 | 2 | 86.772 | 18.1258 | 0 | 2018-02-12 05:00 | 5 | 2 | 87.0054 | 18.1746 | 0 | 2018-02-12 05:00 | 5 | 2 | 66.0354 | 13.7941 | 0
2018-02-12 06:00 | 6 | 2 | 86.2898 | 18.0251 | 0 | 2018-02-12 06:00 | 6 | 2 | 86.6499 | 18.1003 | 0 | 2018-02-12 06:00 | 6 | 2 | 86.8147 | 18.1347 | 0 | 2018-02-12 06:00 | 6 | 2 | 65.9165 | 13.7693 | 0
2018-02-12 07:00 | 7 | 2 | 86.2043 | 18.0072 | 0 | 2018-02-12 07:00 | 7 | 2 | 86.5278 | 18.0748 | 0 | 2018-02-12 07:00 | 7 | 2 | 86.7079 | 18.1124 | 0 | 2018-02-12 07:00 | 7 | 2 | 65.8296 | 13.7511 | 0
2018-02-12 08:00 | 8 | 2 | 86.3355 | 18.0346 | 0 | 2018-02-12 08:00 | 8 | 2 | 86.5461 | 18.0786 | 0 | 2018-02-12 08:00 | 8 | 2 | 86.8025 | 18.1322 | 0 | 2018-02-12 08:00 | 8 | 2 | 65.8725 | 13.7601 | 0
2018-02-12 09:00 | 9 | 2 | 86.3798 | 18.0439 | 0 | 2018-02-12 09:00 | 9 | 2 | 86.7262 | 18.1162 | 0 | 2018-02-12 09:00 | 9 | 2 | 86.8711 | 18.1465 | 0 | 2018-02-12 09:00 | 9 | 2 | 65.967 | 13.7798 | 0
2018-02-12 10:00 | 10 | 2 | 86.2272 | 18.012 | 0 | 2018-02-12 10:00 | 10 | 2 | 86.5156 | 18.0722 | 0 | 2018-02-12 10:00 | 10 | 2 | 86.714 | 18.1137 | 0 | 2018-02-12 10:00 | 10 | 2 | 65.8272 | 13.7507 | 0
2018-02-12 11:00 | 11 | 2 | 86.2119 | 18.0088 | 0 | 2018-02-12 11:00 | 11 | 2 | 86.5141 | 18.0719 | 0 | 2018-02-12 11:00 | 11 | 2 | 86.7201 | 18.115 | 0 | 2018-02-12 11:00 | 11 | 2 | 65.829 | 13.751 | 0
2018-02-12 12:00 | 12 | 2 | 86.389 | 18.0458 | 0 | 2018-02-12 12:00 | 12 | 2 | 86.6835 | 18.1073 | 0 | 2018-02-12 12:00 | 12 | 2 | 86.8574 | 18.1436 | 0 | 2018-02-12 12:00 | 12 | 2 | 65.9455 | 13.7754 | 0
2018-02-12 13:00 | 13 | 2 | 86.4027 | 18.0487 | 0 | 2018-02-12 13:00 | 13 | 2 | 86.6224 | 18.0946 | 0 | 2018-02-12 13:00 | 13 | 2 | 86.7475 | 18.1207 | 0 | 2018-02-12 13:00 | 13 | 2 | 65.8806 | 13.7618 | 0
2018-02-12 14:00 | 14 | 2 | 86.3783 | 18.0436 | 0 | 2018-02-12 14:00 | 14 | 2 | 86.6606 | 18.1025 | 0 | 2018-02-12 14:00 | 14 | 2 | 86.7903 | 18.1296 | 0 | 2018-02-12 14:00 | 14 | 2 | 65.9113 | 13.7682 | 0
2018-02-12 15:00 | 15 | 2 | 86.3355 | 18.0346 | 0 | 2018-02-12 15:00 | 15 | 2 | 86.5248 | 18.0742 | 0 | 2018-02-12 15:00 | 15 | 2 | 86.7384 | 18.1188 | 0 | 2018-02-12 15:00 | 15 | 2 | 65.84 | 13.7533 | 0
2018-02-12 16:00 | 16 | 2 | 86.3493 | 18.0375 | 0 | 2018-02-12 16:00 | 16 | 2 | 86.4912 | 18.0671 | 0 | 2018-02-12 16:00 | 16 | 2 | 86.685 | 18.1076 | 0 | 2018-02-12 16:00 | 16 | 2 | 65.807 | 13.7464 | 0
2018-02-12 17:00 | 17 | 2 | 86.244 | 18.0155 | 0 | 2018-02-12 17:00 | 17 | 2 | 86.4683 | 18.0624 | 0 | 2018-02-12 17:00 | 17 | 2 | 86.6743 | 18.1054 | 0 | 2018-02-12 17:00 | 17 | 2 | 65.7942 | 13.7437 | 0
2018-02-12 18:00 | 18 | 2 | 86.3142 | 18.0302 | 0 | 2018-02-12 18:00 | 18 | 2 | 86.4378 | 18.056 | 0 | 2018-02-12 18:00 | 18 | 2 | 86.5934 | 18.0885 | 0 | 2018-02-12 18:00 | 18 | 2 | 65.7519 | 13.7349 | 0
2018-02-12 19:00 | 19 | 2 | 86.2089 | 18.0082 | 0 | 2018-02-12 19:00 | 19 | 2 | 86.3508 | 18.0378 | 0 | 2018-02-12 19:00 | 19 | 2 | 86.5583 | 18.0812 | 0 | 2018-02-12 19:00 | 19 | 2 | 65.7055 | 13.7252 | 0
2018-02-12 20:00 | 20 | 2 | 86.2181 | 18.0101 | 0 | 2018-02-12 20:00 | 20 | 2 | 86.4836 | 18.0656 | 0 | 2018-02-12 20:00 | 20 | 2 | 86.6896 | 18.1086 | 0 | 2018-02-12 20:00 | 20 | 2 | 65.8058 | 13.7462 | 0
2018-02-12 21:00 | 21 | 2 | 86.1494 | 17.9957 | 0 | 2018-02-12 21:00 | 21 | 2 | 86.4759 | 18.064 | 0 | 2018-02-12 21:00 | 21 | 2 | 86.63 | 18.0961 | 0 | 2018-02-12 21:00 | 21 | 2 | 65.7802 | 13.7408 | 0
2018-02-12 22:00 | 22 | 2 | 86.2593 | 18.0187 | 0 | 2018-02-12 22:00 | 22 | 2 | 86.5522 | 18.0799 | 0 | 2018-02-12 22:00 | 22 | 2 | 86.6468 | 18.0997 | 0 | 2018-02-12 22:00 | 22 | 2 | 65.8156 | 13.7482 | 0
2018-02-12 23:00 | 23 | 2 | 86.4424 | 18.057 | 0 | 2018-02-12 23:00 | 23 | 2 | 86.8055 | 18.1328 | 0 | 2018-02-12 23:00 | 23 | 2 | 86.8864 | 18.1497 | 0 | 2018-02-12 23:00 | 23 | 2 | 66.0029 | 13.7874 | 0
2018-02-13 | 0 | 3 | 86.4637 | 18.0614 | 0 | 2018-02-13 | 0 | 3 | 0 | 0 | 0 | 2018-02-13 | 0 | 3 | 0 | 0 | 0 | 2018-02-13 | 0 | 3 | 0 | 0 | 0
2018-02-13 01:00 | 1 | 3 | 86.5629 | 18.0821 | 0 | 2018-02-13 01:00 | 1 | 3 | 0 | 0 | 0 | 2018-02-13 01:00 | 1 | 3 | 0 | 0 | 0 | 2018-02-13 01:00 | 1 | 3 | 0 | 0 | 0
2018-02-13 02:00 | 2 | 3 | 86.3706 | 18.042 | 0 | 2018-02-13 02:00 | 2 | 3 | 0 | 0 | 0 | 2018-02-13 02:00 | 2 | 3 | 0 | 0 | 0 | 2018-02-13 02:00 | 2 | 3 | 0 | 0 | 0
2018-02-13 03:00 | 3 | 3 | 86.3523 | 18.0381 | 0 | 2018-02-13 03:00 | 3 | 3 | 0 | 0 | 0 | 2018-02-13 03:00 | 3 | 3 | 0 | 0 | 0 | 2018-02-13 03:00 | 3 | 3 | 0 | 0 | 0
2018-02-13 04:00 | 4 | 3 | 86.3676 | 18.0413 | 0 | 2018-02-13 04:00 | 4 | 3 | 0 | 0 | 0 | 2018-02-13 04:00 | 4 | 3 | 0 | 0 | 0 | 2018-02-13 04:00 | 4 | 3 | 0 | 0 | 0
2018-02-13 05:00 | 5 | 3 | 86.4027 | 18.0487 | 0 | 2018-02-13 05:00 | 5 | 3 | 0 | 0 | 0 | 2018-02-13 05:00 | 5 | 3 | 0 | 0 | 0 | 2018-02-13 05:00 | 5 | 3 | 0 | 0 | 0
2018-02-13 06:00 | 6 | 3 | 86.4652 | 18.0617 | 0 | 2018-02-13 06:00 | 6 | 3 | 0 | 0 | 0 | 2018-02-13 06:00 | 6 | 3 | 0 | 0 | 0 | 2018-02-13 06:00 | 6 | 3 | 0 | 0 | 0
2018-02-13 07:00 | 7 | 3 | 86.4012 | 18.0483 | 0 | 2018-02-13 07:00 | 7 | 3 | 0 | 0 | 0 | 2018-02-13 07:00 | 7 | 3 | 0 | 0 | 0 | 2018-02-13 07:00 | 7 | 3 | 0 | 0 | 0
2018-02-13 08:00 | 8 | 3 | 86.4515 | 18.0589 | 0 | 2018-02-13 08:00 | 8 | 3 | 0 | 0 | 0 | 2018-02-13 08:00 | 8 | 3 | 0 | 0 | 0 | 2018-02-13 08:00 | 8 | 3 | 0 | 0 | 0
2018-02-13 09:00 | 9 | 3 | 86.2028 | 18.0069 | 0 | 2018-02-13 09:00 | 9 | 3 | 0 | 0 | 0 | 2018-02-13 09:00 | 9 | 3 | 0 | 0 | 0 | 2018-02-13 09:00 | 9 | 3 | 0 | 0 | 0
2018-02-13 10:00 | 10 | 3 | 86.2715 | 18.0213 | 0 | 2018-02-13 10:00 | 10 | 3 | 0 | 0 | 0 | 2018-02-13 10:00 | 10 | 3 | 0 | 0 | 0 | 2018-02-13 10:00 | 10 | 3 | 0 | 0 | 0
2018-02-13 11:00 | 11 | 3 | 86.7567 | 18.1226 | 0 | 2018-02-13 11:00 | 11 | 3 | 0 | 0 | 0 | 2018-02-13 11:00 | 11 | 3 | 0 | 0 | 0 | 2018-02-13 11:00 | 11 | 3 | 0 | 0 | 0
2018-02-13 12:00 | 12 | 3 | 86.6194 | 18.0939 | 0 | 2018-02-13 12:00 | 12 | 3 | 0 | 0 | 0 | 2018-02-13 12:00 | 12 | 3 | 0 | 0 | 0 | 2018-02-13 12:00 | 12 | 3 | 0 | 0 | 0
2018-02-13 13:00 | 13 | 3 | 86.6377 | 18.0977 | 0 | 2018-02-13 13:00 | 13 | 3 | 0 | 0 | 0 | 2018-02-13 13:00 | 13 | 3 | 0 | 0 | 0 | 2018-02-13 13:00 | 13 | 3 | 0 | 0 | 0
2018-02-13 14:00 | 14 | 3 | 86.8757 | 18.1475 | 0 | 2018-02-13 14:00 | 14 | 3 | 0 | 0 | 0 | 2018-02-13 14:00 | 14 | 3 | 0 | 0 | 0 | 2018-02-13 14:00 | 14 | 3 | 0 | 0 | 0
2018-02-13 15:00 | 15 | 3 | 86.7994 | 18.1315 | 0 | 2018-02-13 15:00 | 15 | 3 | 0 | 0 | 0 | 2018-02-13 15:00 | 15 | 3 | 0 | 0 | 0 | 2018-02-13 15:00 | 15 | 3 | 0 | 0 | 0
2018-02-13 16:00 | 16 | 3 | 86.7674 | 18.1248 | 0 | 2018-02-13 16:00 | 16 | 3 | 0 | 0 | 0 | 2018-02-13 16:00 | 16 | 3 | 0 | 0 | 0 | 2018-02-13 16:00 | 16 | 3 | 0 | 0 | 0
2018-02-13 17:00 | 17 | 3 | 86.7384 | 18.1188 | 0 | 2018-02-13 17:00 | 17 | 3 | 0 | 0 | 0 | 2018-02-13 17:00 | 17 | 3 | 0 | 0 | 0 | 2018-02-13 17:00 | 17 | 3 | 0 | 0 | 0
2018-02-13 18:00 | 18 | 3 | 86.7124 | 18.1134 | 0 | 2018-02-13 18:00 | 18 | 3 | 0 | 0 | 0 | 2018-02-13 18:00 | 18 | 3 | 0 | 0 | 0 | 2018-02-13 18:00 | 18 | 3 | 0 | 0 | 0
2018-02-13 19:00 | 19 | 3 | 86.8376 | 18.1395 | 0 | 2018-02-13 19:00 | 19 | 3 | 0 | 0 | 0 | 2018-02-13 19:00 | 19 | 3 | 0 | 0 | 0 | 2018-02-13 19:00 | 19 | 3 | 0 | 0 | 0
2018-02-13 20:00 | 20 | 3 | 86.627 | 18.0955 | 0 | 2018-02-13 20:00 | 20 | 3 | 0 | 0 | 0 | 2018-02-13 20:00 | 20 | 3 | 0 | 0 | 0 | 2018-02-13 20:00 | 20 | 3 | 0 | 0 | 0
2018-02-13 21:00 | 21 | 3 | 86.6239 | 18.0949 | 0 | 2018-02-13 21:00 | 21 | 3 | 0 | 0 | 0 | 2018-02-13 21:00 | 21 | 3 | 0 | 0 | 0 | 2018-02-13 21:00 | 21 | 3 | 0 | 0 | 0
2018-02-13 22:00 | 22 | 3 | 86.714 | 18.1137 | 0 | 2018-02-13 22:00 | 22 | 3 | 0 | 0 | 0 | 2018-02-13 22:00 | 22 | 3 | 0 | 0 | 0 | 2018-02-13 22:00 | 22 | 3 | 0 | 0 | 0
2018-02-13 23:00 | 23 | 3 | 86.8971 | 18.1519 | 0 | 2018-02-13 23:00 | 23 | 3 | 0 | 0 | 0 | 2018-02-13 23:00 | 23 | 3 | 0 | 0 | 0 | 2018-02-13 23:00 | 23 | 3 | 0 | 0 | 0
2018-02-14 | 0 | 4 | 0 | 0 | 0 | 2018-02-14 | 0 | 4 | 0 | 0 | 0 | 2018-02-14 | 0 | 4 | 86.6712 | 18.1047 | 0 | 2018-02-14 | 0 | 4 | 32.9351 | 6.8798 | 0
2018-02-14 01:00 | 1 | 4 | 0 | 0 | 0 | 2018-02-14 01:00 | 1 | 4 | 0 | 0 | 0 | 2018-02-14 01:00 | 1 | 4 | 86.511 | 18.0713 | 0 | 2018-02-14 01:00 | 1 | 4 | 32.8742 | 6.8671 | 0
2018-02-14 02:00 | 2 | 4 | 0 | 0 | 0 | 2018-02-14 02:00 | 2 | 4 | 0 | 0 | 0 | 2018-02-14 02:00 | 2 | 4 | 86.7628 | 18.1239 | 0 | 2018-02-14 02:00 | 2 | 4 | 32.9699 | 6.8871 | 0
2018-02-14 03:00 | 3 | 4 | 0 | 0 | 0 | 2018-02-14 03:00 | 3 | 4 | 0 | 0 | 0 | 2018-02-14 03:00 | 3 | 4 | 86.7384 | 18.1188 | 0 | 2018-02-14 03:00 | 3 | 4 | 32.9606 | 6.8851 | 0
2018-02-14 04:00 | 4 | 4 | 0 | 0 | 0 | 2018-02-14 04:00 | 4 | 4 | 0 | 0 | 0 | 2018-02-14 04:00 | 4 | 4 | 86.8376 | 18.1395 | 0 | 2018-02-14 04:00 | 4 | 4 | 32.9983 | 6.893 | 0
2018-02-14 05:00 | 5 | 4 | 0 | 0 | 0 | 2018-02-14 05:00 | 5 | 4 | 0 | 0 | 0 | 2018-02-14 05:00 | 5 | 4 | 87.0222 | 18.1781 | 0 | 2018-02-14 05:00 | 5 | 4 | 33.0684 | 6.9077 | 0
2018-02-14 06:00 | 6 | 4 | 0 | 0 | 0 | 2018-02-14 06:00 | 6 | 4 | 0 | 0 | 0 | 2018-02-14 06:00 | 6 | 4 | 86.9627 | 18.1656 | 0 | 2018-02-14 06:00 | 6 | 4 | 33.0458 | 6.9029 | 0
2018-02-14 07:00 | 7 | 4 | 0 | 0 | 0 | 2018-02-14 07:00 | 7 | 4 | 0 | 0 | 0 | 2018-02-14 07:00 | 7 | 4 | 87.1321 | 18.201 | 0 | 2018-02-14 07:00 | 7 | 4 | 33.1102 | 6.9164 | 0
2018-02-14 08:00 | 8 | 4 | 0 | 0 | 0 | 2018-02-14 08:00 | 8 | 4 | 0 | 0 | 0 | 2018-02-14 08:00 | 8 | 4 | 87.1931 | 18.2138 | 0 | 2018-02-14 08:00 | 8 | 4 | 33.1334 | 6.9212 | 0
2018-02-14 09:00 | 9 | 4 | 0 | 0 | 0 | 2018-02-14 09:00 | 9 | 4 | 0 | 0 | 0 | 2018-02-14 09:00 | 9 | 4 | 86.7155 | 18.114 | 0 | 2018-02-14 09:00 | 9 | 4 | 32.9519 | 6.8833 | 0
2018-02-14 10:00 | 10 | 4 | 0 | 0 | 0 | 2018-02-14 10:00 | 10 | 4 | 0 | 0 | 0 | 2018-02-14 10:00 | 10 | 4 | 86.6743 | 18.1054 | 0 | 2018-02-14 10:00 | 10 | 4 | 32.9362 | 6.88 | 0
2018-02-14 11:00 | 11 | 4 | 0 | 0 | 0 | 2018-02-14 11:00 | 11 | 4 | 0 | 0 | 0 | 2018-02-14 11:00 | 11 | 4 | 86.8956 | 18.1516 | 0 | 2018-02-14 11:00 | 11 | 4 | 33.0203 | 6.8976 | 0
2018-02-14 12:00 | 12 | 4 | 0 | 0 | 0 | 2018-02-14 12:00 | 12 | 4 | 0 | 0 | 0 | 2018-02-14 12:00 | 12 | 4 | 86.9276 | 18.1583 | 0 | 2018-02-14 12:00 | 12 | 4 | 33.0325 | 6.9002 | 0
2018-02-14 13:00 | 13 | 4 | 0 | 0 | 0 | 2018-02-14 13:00 | 13 | 4 | 0 | 0 | 0 | 2018-02-14 13:00 | 13 | 4 | 87.2541 | 18.2265 | 0 | 2018-02-14 13:00 | 13 | 4 | 33.1566 | 6.9261 | 0
2018-02-14 14:00 | 14 | 4 | 0 | 0 | 0 | 2018-02-14 14:00 | 14 | 4 | 0 | 0 | 0 | 2018-02-14 14:00 | 14 | 4 | 87.4037 | 18.2578 | 0 | 2018-02-14 14:00 | 14 | 4 | 33.2134 | 6.9379 | 0
2018-02-14 15:00 | 15 | 4 | 0 | 0 | 0 | 2018-02-14 15:00 | 15 | 4 | 0 | 0 | 0 | 2018-02-14 15:00 | 15 | 4 | 87.2129 | 18.2179 | 0 | 2018-02-14 15:00 | 15 | 4 | 33.1409 | 6.9228 | 0
2018-02-14 16:00 | 16 | 4 | 0 | 0 | 0 | 2018-02-14 16:00 | 16 | 4 | 0 | 0 | 0 | 2018-02-14 16:00 | 16 | 4 | 86.9718 | 18.1675 | 0 | 2018-02-14 16:00 | 16 | 4 | 33.0493 | 6.9037 | 0
2018-02-14 17:00 | 17 | 4 | 0 | 0 | 0 | 2018-02-14 17:00 | 17 | 4 | 0 | 0 | 0 | 2018-02-14 17:00 | 17 | 4 | 87.1397 | 18.2026 | 0 | 2018-02-14 17:00 | 17 | 4 | 33.1131 | 6.917 | 0
2018-02-14 18:00 | 18 | 4 | 0 | 0 | 0 | 2018-02-14 18:00 | 18 | 4 | 0 | 0 | 0 | 2018-02-14 18:00 | 18 | 4 | 87.2435 | 18.2243 | 0 | 2018-02-14 18:00 | 18 | 4 | 33.1525 | 6.9252 | 0
2018-02-14 19:00 | 19 | 4 | 0 | 0 | 0 | 2018-02-14 19:00 | 19 | 4 | 0 | 0 | 0 | 2018-02-14 19:00 | 19 | 4 | 86.8894 | 18.1503 | 0 | 2018-02-14 19:00 | 19 | 4 | 33.018 | 6.8971 | 0
2018-02-14 20:00 | 20 | 4 | 0 | 0 | 0 | 2018-02-14 20:00 | 20 | 4 | 0 | 0 | 0 | 2018-02-14 20:00 | 20 | 4 | 87.1839 | 18.2118 | 0 | 2018-02-14 20:00 | 20 | 4 | 33.1299 | 6.9205 | 0
2018-02-14 21:00 | 21 | 4 | 0 | 0 | 0 | 2018-02-14 21:00 | 21 | 4 | 0 | 0 | 0 | 2018-02-14 21:00 | 21 | 4 | 87.2419 | 18.224 | 0 | 2018-02-14 21:00 | 21 | 4 | 33.1519 | 6.9251 | 0
2018-02-14 22:00 | 22 | 4 | 0 | 0 | 0 | 2018-02-14 22:00 | 22 | 4 | 0 | 0 | 0 | 2018-02-14 22:00 | 22 | 4 | 87.1733 | 18.2096 | 0 | 2018-02-14 22:00 | 22 | 4 | 33.1259 | 6.9197 | 0
2018-02-14 23:00 | 23 | 4 | 0 | 0 | 0 | 2018-02-14 23:00 | 23 | 4 | 0 | 0 | 0 | 2018-02-14 23:00 | 23 | 4 | 87.2557 | 18.2268 | 0 | 2018-02-14 23:00 | 23 | 4 | 33.1572 | 6.9262 | 0
2018-02-15 | 0 | 5 | 86.5492 | 18.0793 | 0 | 2018-02-15 | 0 | 5 | 0 | 0 | 0 | 2018-02-15 | 0 | 5 | 0 | 0 | 0 | 2018-02-15 | 0 | 5 | 0 | 0 | 0
2018-02-15 01:00 | 1 | 5 | 86.7201 | 18.115 | 0 | 2018-02-15 01:00 | 1 | 5 | 0 | 0 | 0 | 2018-02-15 01:00 | 1 | 5 | 0 | 0 | 0 | 2018-02-15 01:00 | 1 | 5 | 0 | 0 | 0
2018-02-15 02:00 | 2 | 5 | 86.5095 | 18.071 | 0 | 2018-02-15 02:00 | 2 | 5 | 0 | 0 | 0 | 2018-02-15 02:00 | 2 | 5 | 0 | 0 | 0 | 2018-02-15 02:00 | 2 | 5 | 0 | 0 | 0
2018-02-15 03:00 | 3 | 5 | 86.4576 | 18.0601 | 0 | 2018-02-15 03:00 | 3 | 5 | 0 | 0 | 0 | 2018-02-15 03:00 | 3 | 5 | 0 | 0 | 0 | 2018-02-15 03:00 | 3 | 5 | 0 | 0 | 0
2018-02-15 04:00 | 4 | 5 | 86.6316 | 18.0965 | 0 | 2018-02-15 04:00 | 4 | 5 | 0 | 0 | 0 | 2018-02-15 04:00 | 4 | 5 | 0 | 0 | 0 | 2018-02-15 04:00 | 4 | 5 | 0 | 0 | 0
2018-02-15 05:00 | 5 | 5 | 86.569 | 18.0834 | 0 | 2018-02-15 05:00 | 5 | 5 | 0 | 0 | 0 | 2018-02-15 05:00 | 5 | 5 | 0 | 0 | 0 | 2018-02-15 05:00 | 5 | 5 | 0 | 0 | 0
2018-02-15 06:00 | 6 | 5 | 86.6468 | 18.0997 | 0 | 2018-02-15 06:00 | 6 | 5 | 0 | 0 | 0 | 2018-02-15 06:00 | 6 | 5 | 0 | 0 | 0 | 2018-02-15 06:00 | 6 | 5 | 0 | 0 | 0
2018-02-15 07:00 | 7 | 5 | 86.6361 | 18.0974 | 0 | 2018-02-15 07:00 | 7 | 5 | 0 | 0 | 0 | 2018-02-15 07:00 | 7 | 5 | 0 | 0 | 0 | 2018-02-15 07:00 | 7 | 5 | 0 | 0 | 0
2018-02-15 08:00 | 8 | 5 | 86.6819 | 18.107 | 0 | 2018-02-15 08:00 | 8 | 5 | 0 | 0 | 0 | 2018-02-15 08:00 | 8 | 5 | 0 | 0 | 0 | 2018-02-15 08:00 | 8 | 5 | 0 | 0 | 0
2018-02-15 09:00 | 9 | 5 | 86.7094 | 18.1127 | 0 | 2018-02-15 09:00 | 9 | 5 | 0 | 0 | 0 | 2018-02-15 09:00 | 9 | 5 | 0 | 0 | 0 | 2018-02-15 09:00 | 9 | 5 | 0 | 0 | 0
2018-02-15 10:00 | 10 | 5 | 86.7933 | 18.1303 | 0 | 2018-02-15 10:00 | 10 | 5 | 0 | 0 | 0 | 2018-02-15 10:00 | 10 | 5 | 0 | 0 | 0 | 2018-02-15 10:00 | 10 | 5 | 0 | 0 | 0
2018-02-15 11:00 | 11 | 5 | 86.8009 | 18.1318 | 0 | 2018-02-15 11:00 | 11 | 5 | 0 | 0 | 0 | 2018-02-15 11:00 | 11 | 5 | 0 | 0 | 0 | 2018-02-15 11:00 | 11 | 5 | 0 | 0 | 0
2018-02-15 12:00 | 12 | 5 | 86.6728 | 18.1051 | 0 | 2018-02-15 12:00 | 12 | 5 | 0 | 0 | 0 | 2018-02-15 12:00 | 12 | 5 | 0 | 0 | 0 | 2018-02-15 12:00 | 12 | 5 | 0 | 0 | 0
2018-02-15 13:00 | 13 | 5 | 86.6316 | 18.0965 | 0 | 2018-02-15 13:00 | 13 | 5 | 0 | 0 | 0 | 2018-02-15 13:00 | 13 | 5 | 0 | 0 | 0 | 2018-02-15 13:00 | 13 | 5 | 0 | 0 | 0
2018-02-15 14:00 | 14 | 5 | 86.6316 | 18.0965 | 0 | 2018-02-15 14:00 | 14 | 5 | 0 | 0 | 0 | 2018-02-15 14:00 | 14 | 5 | 0 | 0 | 0 | 2018-02-15 14:00 | 14 | 5 | 0 | 0 | 0
2018-02-15 15:00 | 15 | 5 | 86.6636 | 18.1032 | 0 | 2018-02-15 15:00 | 15 | 5 | 0 | 0 | 0 | 2018-02-15 15:00 | 15 | 5 | 0 | 0 | 0 | 2018-02-15 15:00 | 15 | 5 | 0 | 0 | 0
2018-02-15 16:00 | 16 | 5 | 86.5568 | 18.0808 | 0 | 2018-02-15 16:00 | 16 | 5 | 0 | 0 | 0 | 2018-02-15 16:00 | 16 | 5 | 0 | 0 | 0 | 2018-02-15 16:00 | 16 | 5 | 0 | 0 | 0
2018-02-15 17:00 | 17 | 5 | 86.6865 | 18.1079 | 0 | 2018-02-15 17:00 | 17 | 5 | 0 | 0 | 0 | 2018-02-15 17:00 | 17 | 5 | 0 | 0 | 0 | 2018-02-15 17:00 | 17 | 5 | 0 | 0 | 0
2018-02-15 18:00 | 18 | 5 | 86.7262 | 18.1162 | 0 | 2018-02-15 18:00 | 18 | 5 | 0 | 0 | 0 | 2018-02-15 18:00 | 18 | 5 | 0 | 0 | 0 | 2018-02-15 18:00 | 18 | 5 | 0 | 0 | 0
2018-02-15 19:00 | 19 | 5 | 86.5187 | 18.0729 | 0 | 2018-02-15 19:00 | 19 | 5 | 0 | 0 | 0 | 2018-02-15 19:00 | 19 | 5 | 0 | 0 | 0 | 2018-02-15 19:00 | 19 | 5 | 0 | 0 | 0
2018-02-15 20:00 | 20 | 5 | 86.5766 | 18.085 | 0 | 2018-02-15 20:00 | 20 | 5 | 0 | 0 | 0 | 2018-02-15 20:00 | 20 | 5 | 0 | 0 | 0 | 2018-02-15 20:00 | 20 | 5 | 0 | 0 | 0
2018-02-15 21:00 | 21 | 5 | 86.6194 | 18.0939 | 0 | 2018-02-15 21:00 | 21 | 5 | 0 | 0 | 0 | 2018-02-15 21:00 | 21 | 5 | 0 | 0 | 0 | 2018-02-15 21:00 | 21 | 5 | 0 | 0 | 0
2018-02-15 22:00 | 22 | 5 | 86.6743 | 18.1054 | 0 | 2018-02-15 22:00 | 22 | 5 | 0 | 0 | 0 | 2018-02-15 22:00 | 22 | 5 | 0 | 0 | 0 | 2018-02-15 22:00 | 22 | 5 | 0 | 0 | 0
2018-02-15 23:00 | 23 | 5 | 86.5644 | 18.0824 | 0 | 2018-02-15 23:00 | 23 | 5 | 0 | 0 | 0 | 2018-02-15 23:00 | 23 | 5 | 0 | 0 | 0 | 2018-02-15 23:00 | 23 | 5 | 0 | 0 | 0
2018-02-16 | 0 | 6 | 86.2226 | 18.011 | 0 | 2018-02-16 | 0 | 6 | 86.688 | 18.1083 | 0 | 2018-02-16 | 0 | 6 | 0 | 0 | 0 | 2018-02-16 | 0 | 6 | 32.9414 | 6.8811 | 0
2018-02-16 01:00 | 1 | 6 | 86.1128 | 17.9881 | 0 | 2018-02-16 01:00 | 1 | 6 | 86.5232 | 18.0738 | 0 | 2018-02-16 01:00 | 1 | 6 | 0 | 0 | 0 | 2018-02-16 01:00 | 1 | 6 | 32.8788 | 6.8681 | 0
2018-02-16 02:00 | 2 | 6 | 86.2791 | 18.0228 | 0 | 2018-02-16 02:00 | 2 | 6 | 86.6896 | 18.1086 | 0 | 2018-02-16 02:00 | 2 | 6 | 0 | 0 | 0 | 2018-02-16 02:00 | 2 | 6 | 32.942 | 6.8813 | 0
2018-02-16 03:00 | 3 | 6 | 86.0014 | 17.9648 | 0 | 2018-02-16 03:00 | 3 | 6 | 86.4485 | 18.0582 | 0 | 2018-02-16 03:00 | 3 | 6 | 0 | 0 | 0 | 2018-02-16 03:00 | 3 | 6 | 32.8504 | 6.8621 | 0
2018-02-16 04:00 | 4 | 6 | 86.0533 | 17.9757 | 0 | 2018-02-16 04:00 | 4 | 6 | 86.4347 | 18.0553 | 0 | 2018-02-16 04:00 | 4 | 6 | 0 | 0 | 0 | 2018-02-16 04:00 | 4 | 6 | 32.8452 | 6.861 | 0
2018-02-16 05:00 | 5 | 6 | 86.2257 | 18.0117 | 0 | 2018-02-16 05:00 | 5 | 6 | 86.6117 | 18.0923 | 0 | 2018-02-16 05:00 | 5 | 6 | 0 | 0 | 0 | 2018-02-16 05:00 | 5 | 6 | 32.9124 | 6.8751 | 0
2018-02-16 06:00 | 6 | 6 | 86.4332 | 18.055 | 0 | 2018-02-16 06:00 | 6 | 6 | 86.9352 | 18.1599 | 0 | 2018-02-16 06:00 | 6 | 6 | 0 | 0 | 0 | 2018-02-16 06:00 | 6 | 6 | 33.0354 | 6.9008 | 0
2018-02-16 07:00 | 7 | 6 | 86.5873 | 18.0872 | 0 | 2018-02-16 07:00 | 7 | 6 | 87.0619 | 18.1864 | 0 | 2018-02-16 07:00 | 7 | 6 | 0 | 0 | 0 | 2018-02-16 07:00 | 7 | 6 | 33.0835 | 6.9108 | 0
2018-02-16 08:00 | 8 | 6 | 86.3691 | 18.0416 | 0 | 2018-02-16 08:00 | 8 | 6 | 86.7811 | 18.1277 | 0 | 2018-02-16 08:00 | 8 | 6 | 0 | 0 | 0 | 2018-02-16 08:00 | 8 | 6 | 32.9768 | 6.8885 | 0
2018-02-16 09:00 | 9 | 6 | 86.334 | 18.0343 | 0 | 2018-02-16 09:00 | 9 | 6 | 86.7399 | 18.1191 | 0 | 2018-02-16 09:00 | 9 | 6 | 0 | 0 | 0 | 2018-02-16 09:00 | 9 | 6 | 32.9612 | 6.8853 | 0
2018-02-16 10:00 | 10 | 6 | 86.5126 | 18.0716 | 0 | 2018-02-16 10:00 | 10 | 6 | 86.862 | 18.1446 | 0 | 2018-02-16 10:00 | 10 | 6 | 0 | 0 | 0 | 2018-02-16 10:00 | 10 | 6 | 33.0076 | 6.8949 | 0
2018-02-16 11:00 | 11 | 6 | 86.5003 | 18.069 | 0 | 2018-02-16 11:00 | 11 | 6 | 86.9306 | 18.1589 | 0 | 2018-02-16 11:00 | 11 | 6 | 0 | 0 | 0 | 2018-02-16 11:00 | 11 | 6 | 33.0336 | 6.9004 | 0
2018-02-16 12:00 | 12 | 6 | 86.7002 | 18.1108 | 0 | 2018-02-16 12:00 | 12 | 6 | 87.1412 | 18.2029 | 0 | 2018-02-16 12:00 | 12 | 6 | 0 | 0 | 0 | 2018-02-16 12:00 | 12 | 6 | 33.1137 | 6.9171 | 0
2018-02-16 13:00 | 13 | 6 | 86.363 | 18.0404 | 0 | 2018-02-16 13:00 | 13 | 6 | 86.8009 | 18.1318 | 0 | 2018-02-16 13:00 | 13 | 6 | 0 | 0 | 0 | 2018-02-16 13:00 | 13 | 6 | 32.9843 | 6.8901 | 0
2018-02-16 14:00 | 14 | 6 | 86.4408 | 18.0566 | 0 | 2018-02-16 14:00 | 14 | 6 | 86.8635 | 18.1449 | 0 | 2018-02-16 14:00 | 14 | 6 | 0 | 0 | 0 | 2018-02-16 14:00 | 14 | 6 | 33.0081 | 6.8951 | 0
2018-02-16 15:00 | 15 | 6 | 86.2943 | 18.026 | 0 | 2018-02-16 15:00 | 15 | 6 | 86.6743 | 18.1054 | 0 | 2018-02-16 15:00 | 15 | 6 | 0 | 0 | 0 | 2018-02-16 15:00 | 15 | 6 | 32.9362 | 6.88 | 0
2018-02-16 16:00 | 16 | 6 | 86.3706 | 18.042 | 0 | 2018-02-16 16:00 | 16 | 6 | 86.7491 | 18.121 | 0 | 2018-02-16 16:00 | 16 | 6 | 0 | 0 | 0 | 2018-02-16 16:00 | 16 | 6 | 32.9647 | 6.886 | 0
2018-02-16 17:00 | 17 | 6 | 86.2882 | 18.0247 | 0 | 2018-02-16 17:00 | 17 | 6 | 86.7445 | 18.1201 | 0 | 2018-02-16 17:00 | 17 | 6 | 0 | 0 | 0 | 2018-02-16 17:00 | 17 | 6 | 32.9629 | 6.8856 | 0
2018-02-16 18:00 | 18 | 6 | 86.1875 | 18.0037 | 0 | 2018-02-16 18:00 | 18 | 6 | 86.6667 | 18.1038 | 0 | 2018-02-16 18:00 | 18 | 6 | 0 | 0 | 0 | 2018-02-16 18:00 | 18 | 6 | 32.9333 | 6.8794 | 0
2018-02-16 19:00 | 19 | 6 | 86.099 | 17.9852 | 0 | 2018-02-16 19:00 | 19 | 6 | 86.5431 | 18.078 | 0 | 2018-02-16 19:00 | 19 | 6 | 0 | 0 | 0 | 2018-02-16 19:00 | 19 | 6 | 32.8864 | 6.8696 | 0
2018-02-16 20:00 | 20 | 6 | 86.1997 | 18.0063 | 0 | 2018-02-16 20:00 | 20 | 6 | 86.5187 | 18.0729 | 0 | 2018-02-16 20:00 | 20 | 6 | 0 | 0 | 0 | 2018-02-16 20:00 | 20 | 6 | 32.8771 | 6.8677 | 0
2018-02-16 21:00 | 21 | 6 | 86.3767 | 18.0432 | 0 | 2018-02-16 21:00 | 21 | 6 | 86.7247 | 18.1159 | 0 | 2018-02-16 21:00 | 21 | 6 | 0 | 0 | 0 | 2018-02-16 21:00 | 21 | 6 | 32.9554 | 6.8841 | 0
2018-02-16 22:00 | 22 | 6 | 86.3691 | 18.0416 | 0 | 2018-02-16 22:00 | 22 | 6 | 86.7659 | 18.1245 | 0 | 2018-02-16 22:00 | 22 | 6 | 0 | 0 | 0 | 2018-02-16 22:00 | 22 | 6 | 32.971 | 6.8873 | 0
2018-02-16 23:00 | 23 | 6 | 86.4012 | 18.0483 | 0 | 2018-02-16 23:00 | 23 | 6 | 86.7918 | 18.1299 | 0 | 2018-02-16 23:00 | 23 | 6 | 0 | 0 | 0 | 2018-02-16 23:00 | 23 | 6 | 32.9809 | 6.8894 | 0
2018-02-17 | 0 | 7 | 86.0121 | 17.9671 | 0 | 2018-02-17 | 0 | 7 | 0 | 0 | 0 | 2018-02-17 | 0 | 7 | 86.5507 | 18.0796 | 0 | 2018-02-17 | 0 | 7 | 32.8893 | 6.8702 | 0
2018-02-17 01:00 | 1 | 7 | 85.919 | 17.9476 | 0 | 2018-02-17 01:00 | 1 | 7 | 0 | 0 | 0 | 2018-02-17 01:00 | 1 | 7 | 86.5324 | 18.0758 | 0 | 2018-02-17 01:00 | 1 | 7 | 32.8823 | 6.8688 | 0
2018-02-17 02:00 | 2 | 7 | 86.0533 | 17.9757 | 0 | 2018-02-17 02:00 | 2 | 7 | 0 | 0 | 0 | 2018-02-17 02:00 | 2 | 7 | 86.6453 | 18.0993 | 0 | 2018-02-17 02:00 | 2 | 7 | 32.9252 | 6.8777 | 0
2018-02-17 03:00 | 3 | 7 | 86.1677 | 17.9996 | 0 | 2018-02-17 03:00 | 3 | 7 | 0 | 0 | 0 | 2018-02-17 03:00 | 3 | 7 | 86.7002 | 18.1108 | 0 | 2018-02-17 03:00 | 3 | 7 | 32.9461 | 6.8821 | 0
2018-02-17 04:00 | 4 | 7 | 86.3081 | 18.0289 | 0 | 2018-02-17 04:00 | 4 | 7 | 0 | 0 | 0 | 2018-02-17 04:00 | 4 | 7 | 86.8513 | 18.1424 | 0 | 2018-02-17 04:00 | 4 | 7 | 33.0035 | 6.8941 | 0
2018-02-17 05:00 | 5 | 7 | 86.2562 | 18.0181 | 0 | 2018-02-17 05:00 | 5 | 7 | 0 | 0 | 0 | 2018-02-17 05:00 | 5 | 7 | 86.8605 | 18.1443 | 0 | 2018-02-17 05:00 | 5 | 7 | 33.007 | 6.8948 | 0
2018-02-17 06:00 | 6 | 7 | 86.1234 | 17.9903 | 0 | 2018-02-17 06:00 | 6 | 7 | 0 | 0 | 0 | 2018-02-17 06:00 | 6 | 7 | 86.6682 | 18.1041 | 0 | 2018-02-17 06:00 | 6 | 7 | 32.9339 | 6.8796 | 0
2018-02-17 07:00 | 7 | 7 | 86.1906 | 18.0044 | 0 | 2018-02-17 07:00 | 7 | 7 | 0 | 0 | 0 | 2018-02-17 07:00 | 7 | 7 | 86.7247 | 18.1159 | 0 | 2018-02-17 07:00 | 7 | 7 | 32.9554 | 6.8841 | 0
2018-02-17 08:00 | 8 | 7 | 86.36 | 18.0397 | 0 | 2018-02-17 08:00 | 8 | 7 | 0 | 0 | 0 | 2018-02-17 08:00 | 8 | 7 | 86.952 | 18.1634 | 0 | 2018-02-17 08:00 | 8 | 7 | 33.0418 | 6.9021 | 0
2018-02-17 09:00 | 9 | 7 | 86.4912 | 18.0671 | 0 | 2018-02-17 09:00 | 9 | 7 | 0 | 0 | 0 | 2018-02-17 09:00 | 9 | 7 | 87.0588 | 18.1857 | 0 | 2018-02-17 09:00 | 9 | 7 | 33.0823 | 6.9106 | 0
2018-02-17 10:00 | 10 | 7 | 86.1982 | 18.0059 | 0 | 2018-02-17 10:00 | 10 | 7 | 0 | 0 | 0 | 2018-02-17 10:00 | 10 | 7 | 86.6392 | 18.0981 | 0 | 2018-02-17 10:00 | 10 | 7 | 32.9229 | 6.8773 | 0
2018-02-17 11:00 | 11 | 7 | 86.1707 | 18.0002 | 0 | 2018-02-17 11:00 | 11 | 7 | 0 | 0 | 0 | 2018-02-17 11:00 | 11 | 7 | 86.8849 | 18.1494 | 0 | 2018-02-17 11:00 | 11 | 7 | 33.0163 | 6.8968 | 0
2018-02-17 12:00 | 12 | 7 | 86.5019 | 18.0694 | 0 | 2018-02-17 12:00 | 12 | 7 | 0 | 0 | 0 | 2018-02-17 12:00 | 12 | 7 | 87.1504 | 18.2048 | 0 | 2018-02-17 12:00 | 12 | 7 | 33.1172 | 6.9178 | 0
2018-02-17 13:00 | 13 | 7 | 86.6148 | 18.093 | 0 | 2018-02-17 13:00 | 13 | 7 | 0 | 0 | 0 | 2018-02-17 13:00 | 13 | 7 | 87.3167 | 18.2396 | 0 | 2018-02-17 13:00 | 13 | 7 | 33.1803 | 6.931 | 0
2018-02-17 14:00 | 14 | 7 | 86.4439 | 18.0573 | 0 | 2018-02-17 14:00 | 14 | 7 | 0 | 0 | 0 | 2018-02-17 14:00 | 14 | 7 | 87.0832 | 18.1908 | 0 | 2018-02-17 14:00 | 14 | 7 | 33.0916 | 6.9125 | 0
2018-02-17 15:00 | 15 | 7 | 86.5522 | 18.0799 | 0 | 2018-02-17 15:00 | 15 | 7 | 0 | 0 | 0 | 2018-02-17 15:00 | 15 | 7 | 87.2938 | 18.2348 | 0 | 2018-02-17 15:00 | 15 | 7 | 33.1716 | 6.9292 | 0
2018-02-17 16:00 | 16 | 7 | 86.5644 | 18.0824 | 0 | 2018-02-17 16:00 | 16 | 7 | 0 | 0 | 0 | 2018-02-17 16:00 | 16 | 7 | 87.3579 | 18.2482 | 0 | 2018-02-17 16:00 | 16 | 7 | 33.196 | 6.9343 | 0
2018-02-17 17:00 | 17 | 7 | 86.7445 | 18.1201 | 0 | 2018-02-17 17:00 | 17 | 7 | 0 | 0 | 0 | 2018-02-17 17:00 | 17 | 7 | 87.57 | 18.2925 | 0 | 2018-02-17 17:00 | 17 | 7 | 33.2766 | 6.9511 | 0
2018-02-17 18:00 | 18 | 7 | 86.4668 | 18.062 | 0 | 2018-02-17 18:00 | 18 | 7 | 0 | 0 | 0 | 2018-02-17 18:00 | 18 | 7 | 87.3014 | 18.2364 | 0 | 2018-02-17 18:00 | 18 | 7 | 33.1745 | 6.9298 | 0
2018-02-17 19:00 | 19 | 7 | 86.3661 | 18.041 | 0 | 2018-02-17 19:00 | 19 | 7 | 0 | 0 | 0 | 2018-02-17 19:00 | 19 | 7 | 87.0954 | 18.1934 | 0 | 2018-02-17 19:00 | 19 | 7 | 33.0963 | 6.9135 | 0
2018-02-17 20:00 | 20 | 7 | 86.1173 | 17.989 | 0 | 2018-02-17 20:00 | 20 | 7 | 0 | 0 | 0 | 2018-02-17 20:00 | 20 | 7 | 86.891 | 18.1507 | 0 | 2018-02-17 20:00 | 20 | 7 | 33.0186 | 6.8973 | 0
2018-02-17 21:00 | 21 | 7 | 86.1555 | 17.997 | 0 | 2018-02-17 21:00 | 21 | 7 | 0 | 0 | 0 | 2018-02-17 21:00 | 21 | 7 | 86.9245 | 18.1577 | 0 | 2018-02-17 21:00 | 21 | 7 | 33.0313 | 6.8999 | 0
2018-02-17 22:00 | 22 | 7 | 86.2211 | 18.0107 | 0 | 2018-02-17 22:00 | 22 | 7 | 0 | 0 | 0 | 2018-02-17 22:00 | 22 | 7 | 87.0054 | 18.1746 | 0 | 2018-02-17 22:00 | 22 | 7 | 33.0621 | 6.9063 | 0
2018-02-17 23:00 | 23 | 7 | 86.2226 | 18.011 | 0 | 2018-02-17 23:00 | 23 | 7 | 0 | 0 | 0 | 2018-02-17 23:00 | 23 | 7 | 87.0787 | 18.1899 | 0 | 2018-02-17 23:00 | 23 | 7 | 33.0899 | 6.9122 | 0
2018-02-18 | 0 | 1 | 86.2364 | 18.0139 | 0 | 2018-02-18 | 0 | 1 | 86.7994 | 18.1315 | 0 | 2018-02-18 | 0 | 1 | 0 | 0 | 0 | 2018-02-18 | 0 | 1 | 32.9838 | 6.89 | 0
2018-02-18 01:00 | 1 | 1 | 86.3188 | 18.0311 | 0 | 2018-02-18 01:00 | 1 | 1 | 86.952 | 18.1634 | 0 | 2018-02-18 01:00 | 1 | 1 | 0 | 0 | 0 | 2018-02-18 01:00 | 1 | 1 | 33.0418 | 6.9021 | 0
2018-02-18 02:00 | 2 | 1 | 86.2119 | 18.0088 | 0 | 2018-02-18 02:00 | 2 | 1 | 86.8177 | 18.1353 | 0 | 2018-02-18 02:00 | 2 | 1 | 0 | 0 | 0 | 2018-02-18 02:00 | 2 | 1 | 32.9907 | 6.8914 | 0
2018-02-18 03:00 | 3 | 1 | 86.1845 | 18.0031 | 0 | 2018-02-18 03:00 | 3 | 1 | 86.7857 | 18.1287 | 0 | 2018-02-18 03:00 | 3 | 1 | 0 | 0 | 0 | 2018-02-18 03:00 | 3 | 1 | 32.9786 | 6.8889 | 0
2018-02-18 04:00 | 4 | 1 | 86.2455 | 18.0158 | 0 | 2018-02-18 04:00 | 4 | 1 | 86.833 | 18.1385 | 0 | 2018-02-18 04:00 | 4 | 1 | 0 | 0 | 0 | 2018-02-18 04:00 | 4 | 1 | 32.9965 | 6.8926 | 0
2018-02-18 05:00 | 5 | 1 | 86.2333 | 18.0133 | 0 | 2018-02-18 05:00 | 5 | 1 | 86.833 | 18.1385 | 0 | 2018-02-18 05:00 | 5 | 1 | 0 | 0 | 0 | 2018-02-18 05:00 | 5 | 1 | 32.9965 | 6.8926 | 0
2018-02-18 06:00 | 6 | 1 | 86.2776 | 18.0225 | 0 | 2018-02-18 06:00 | 6 | 1 | 86.8528 | 18.1427 | 0 | 2018-02-18 06:00 | 6 | 1 | 0 | 0 | 0 | 2018-02-18 06:00 | 6 | 1 | 33.0041 | 6.8942 | 0
2018-02-18 07:00 | 7 | 1 | 86.2867 | 18.0244 | 0 | 2018-02-18 07:00 | 7 | 1 | 86.8452 | 18.1411 | 0 | 2018-02-18 07:00 | 7 | 1 | 0 | 0 | 0 | 2018-02-18 07:00 | 7 | 1 | 33.0012 | 6.8936 | 0
2018-02-18 08:00 | 8 | 1 | 86.2989 | 18.027 | 0 | 2018-02-18 08:00 | 8 | 1 | 86.9032 | 18.1532 | 0 | 2018-02-18 08:00 | 8 | 1 | 0 | 0 | 0 | 2018-02-18 08:00 | 8 | 1 | 33.0232 | 6.8982 | 0
2018-02-18 09:00 | 9 | 1 | 86.2867 | 18.0244 | 0 | 2018-02-18 09:00 | 9 | 1 | 86.8162 | 18.135 | 0 | 2018-02-18 09:00 | 9 | 1 | 0 | 0 | 0 | 2018-02-18 09:00 | 9 | 1 | 32.9902 | 6.8913 | 0
2018-02-18 10:00 | 10 | 1 | 86.2882 | 18.0247 | 0 | 2018-02-18 10:00 | 10 | 1 | 86.8528 | 18.1427 | 0 | 2018-02-18 10:00 | 10 | 1 | 0 | 0 | 0 | 2018-02-18 10:00 | 10 | 1 | 33.0041 | 6.8942 | 0
2018-02-18 11:00 | 11 | 1 | 86.1845 | 18.0031 | 0 | 2018-02-18 11:00 | 11 | 1 | 86.743 | 18.1197 | 0 | 2018-02-18 11:00 | 11 | 1 | 0 | 0 | 0 | 2018-02-18 11:00 | 11 | 1 | 32.9623 | 6.8855 | 0
2018-02-18 12:00 | 12 | 1 | 86.1418 | 17.9942 | 0 | 2018-02-18 12:00 | 12 | 1 | 86.714 | 18.1137 | 0 | 2018-02-18 12:00 | 12 | 1 | 0 | 0 | 0 | 2018-02-18 12:00 | 12 | 1 | 32.9513 | 6.8832 | 0
2018-02-18 13:00 | 13 | 1 | 86.1479 | 17.9954 | 0 | 2018-02-18 13:00 | 13 | 1 | 86.7659 | 18.1245 | 0 | 2018-02-18 13:00 | 13 | 1 | 0 | 0 | 0 | 2018-02-18 13:00 | 13 | 1 | 32.971 | 6.8873 | 0
2018-02-18 14:00 | 14 | 1 | 86.1112 | 17.9878 | 0 | 2018-02-18 14:00 | 14 | 1 | 86.7018 | 18.1111 | 0 | 2018-02-18 14:00 | 14 | 1 | 0 | 0 | 0 | 2018-02-18 14:00 | 14 | 1 | 32.9467 | 6.8822 | 0
2018-02-18 15:00 | 15 | 1 | 86.2455 | 18.0158 | 0 | 2018-02-18 15:00 | 15 | 1 | 86.8482 | 18.1417 | 0 | 2018-02-18 15:00 | 15 | 1 | 0 | 0 | 0 | 2018-02-18 15:00 | 15 | 1 | 33.0023 | 6.8939 | 0
2018-02-18 16:00 | 16 | 1 | 86.3447 | 18.0365 | 0 | 2018-02-18 16:00 | 16 | 1 | 86.9398 | 18.1609 | 0 | 2018-02-18 16:00 | 16 | 1 | 0 | 0 | 0 | 2018-02-18 16:00 | 16 | 1 | 33.0371 | 6.9011 | 0
2018-02-18 17:00 | 17 | 1 | 86.4805 | 18.0649 | 0 | 2018-02-18 17:00 | 17 | 1 | 86.9856 | 18.1704 | 0 | 2018-02-18 17:00 | 17 | 1 | 0 | 0 | 0 | 2018-02-18 17:00 | 17 | 1 | 33.0545 | 6.9048 | 0
2018-02-18 18:00 | 18 | 1 | 86.4332 | 18.055 | 0 | 2018-02-18 18:00 | 18 | 1 | 86.92 | 18.1567 | 0 | 2018-02-18 18:00 | 18 | 1 | 0 | 0 | 0 | 2018-02-18 18:00 | 18 | 1 | 33.0296 | 6.8996 | 0
2018-02-18 19:00 | 19 | 1 | 85.6794 | 17.8976 | 0 | 2018-02-18 19:00 | 19 | 1 | 85.9266 | 17.9492 | 0 | 2018-02-18 19:00 | 19 | 1 | 0 | 0 | 0 | 2018-02-18 19:00 | 19 | 1 | 32.6521 | 6.8207 | 0
2018-02-18 20:00 | 20 | 1 | 86.3294 | 18.0333 | 0 | 2018-02-18 20:00 | 20 | 1 | 86.5888 | 18.0875 | 0 | 2018-02-18 20:00 | 20 | 1 | 0 | 0 | 0 | 2018-02-18 20:00 | 20 | 1 | 32.9037 | 6.8733 | 0
2018-02-18 21:00 | 21 | 1 | 86.3569 | 18.0391 | 0 | 2018-02-18 21:00 | 21 | 1 | 86.6728 | 18.1051 | 0 | 2018-02-18 21:00 | 21 | 1 | 0 | 0 | 0 | 2018-02-18 21:00 | 21 | 1 | 32.9357 | 6.8799 | 0
2018-02-18 22:00 | 22 | 1 | 86.4881 | 18.0665 | 0 | 2018-02-18 22:00 | 22 | 1 | 86.8086 | 18.1334 | 0 | 2018-02-18 22:00 | 22 | 1 | 0 | 0 | 0 | 2018-02-18 22:00 | 22 | 1 | 32.9873 | 6.8907 | 0
2018-02-18 23:00 | 23 | 1 | 86.4332 | 18.055 | 0 | 2018-02-18 23:00 | 23 | 1 | 86.7353 | 18.1181 | 0 | 2018-02-18 23:00 | 23 | 1 | 0 | 0 | 0 | 2018-02-18 23:00 | 23 | 1 | 32.9594 | 6.8849 | 0
2018-02-19 | 0 | 2 | 86.4088 | 18.0499 | 0 | 2018-02-19 | 0 | 2 | 86.7002 | 18.1108 | 0 | 2018-02-19 | 0 | 2 | 86.9352 | 18.1599 | 0 | 2018-02-19 | 0 | 2 | 65.9815 | 13.7829 | 0
2018-02-19 01:00 | 1 | 2 | 86.0426 | 17.9734 | 0 | 2018-02-19 01:00 | 1 | 2 | 86.3127 | 18.0299 | 0 | 2018-02-19 01:00 | 1 | 2 | 86.5278 | 18.0748 | 0 | 2018-02-19 01:00 | 1 | 2 | 65.6794 | 13.7198 | 0
2018-02-19 02:00 | 2 | 2 | 86.392 | 18.0464 | 0 | 2018-02-19 02:00 | 2 | 2 | 86.6392 | 18.0981 | 0 | 2018-02-19 02:00 | 2 | 2 | 86.8421 | 18.1404 | 0 | 2018-02-19 02:00 | 2 | 2 | 65.9229 | 13.7706 | 0
2018-02-19 03:00 | 3 | 2 | 86.2776 | 18.0225 | 0 | 2018-02-19 03:00 | 3 | 2 | 86.5766 | 18.085 | 0 | 2018-02-19 03:00 | 3 | 2 | 86.7536 | 18.122 | 0 | 2018-02-19 03:00 | 3 | 2 | 65.8655 | 13.7586 | 0
2018-02-19 04:00 | 4 | 2 | 86.5034 | 18.0697 | 0 | 2018-02-19 04:00 | 4 | 2 | 86.8849 | 18.1494 | 0 | 2018-02-19 04:00 | 4 | 2 | 87.0283 | 18.1793 | 0 | 2018-02-19 04:00 | 4 | 2 | 66.087 | 13.8049 | 0
2018-02-19 05:00 | 5 | 2 | 86.3661 | 18.041 | 0 | 2018-02-19 05:00 | 5 | 2 | 86.772 | 18.1258 | 0 | 2018-02-19 05:00 | 5 | 2 | 87.0054 | 18.1746 | 0 | 2018-02-19 05:00 | 5 | 2 | 66.0354 | 13.7941 | 0
2018-02-19 06:00 | 6 | 2 | 86.2898 | 18.0251 | 0 | 2018-02-19 06:00 | 6 | 2 | 86.6499 | 18.1003 | 0 | 2018-02-19 06:00 | 6 | 2 | 86.8147 | 18.1347 | 0 | 2018-02-19 06:00 | 6 | 2 | 65.9165 | 13.7693 | 0
2018-02-19 07:00 | 7 | 2 | 86.2043 | 18.0072 | 0 | 2018-02-19 07:00 | 7 | 2 | 86.5278 | 18.0748 | 0 | 2018-02-19 07:00 | 7 | 2 | 86.7079 | 18.1124 | 0 | 2018-02-19 07:00 | 7 | 2 | 65.8296 | 13.7511 | 0
2018-02-19 08:00 | 8 | 2 | 86.3355 | 18.0346 | 0 | 2018-02-19 08:00 | 8 | 2 | 86.5461 | 18.0786 | 0 | 2018-02-19 08:00 | 8 | 2 | 86.8025 | 18.1322 | 0 | 2018-02-19 08:00 | 8 | 2 | 65.8725 | 13.7601 | 0
2018-02-19 09:00 | 9 | 2 | 86.3798 | 18.0439 | 0 | 2018-02-19 09:00 | 9 | 2 | 86.7262 | 18.1162 | 0 | 2018-02-19 09:00 | 9 | 2 | 86.8711 | 18.1465 | 0 | 2018-02-19 09:00 | 9 | 2 | 65.967 | 13.7798 | 0
2018-02-19 10:00 | 10 | 2 | 86.2272 | 18.012 | 0 | 2018-02-19 10:00 | 10 | 2 | 86.5156 | 18.0722 | 0 | 2018-02-19 10:00 | 10 | 2 | 86.714 | 18.1137 | 0 | 2018-02-19 10:00 | 10 | 2 | 65.8272 | 13.7507 | 0
2018-02-19 11:00 | 11 | 2 | 86.2119 | 18.0088 | 0 | 2018-02-19 11:00 | 11 | 2 | 86.5141 | 18.0719 | 0 | 2018-02-19 11:00 | 11 | 2 | 86.7201 | 18.115 | 0 | 2018-02-19 11:00 | 11 | 2 | 65.829 | 13.751 | 0
2018-02-19 12:00 | 12 | 2 | 86.389 | 18.0458 | 0 | 2018-02-19 12:00 | 12 | 2 | 86.6835 | 18.1073 | 0 | 2018-02-19 12:00 | 12 | 2 | 86.8574 | 18.1436 | 0 | 2018-02-19 12:00 | 12 | 2 | 65.9455 | 13.7754 | 0
2018-02-19 13:00 | 13 | 2 | 86.4027 | 18.0487 | 0 | 2018-02-19 13:00 | 13 | 2 | 86.6224 | 18.0946 | 0 | 2018-02-19 13:00 | 13 | 2 | 86.7475 | 18.1207 | 0 | 2018-02-19 13:00 | 13 | 2 | 65.8806 | 13.7618 | 0
2018-02-19 14:00 | 14 | 2 | 86.3783 | 18.0436 | 0 | 2018-02-19 14:00 | 14 | 2 | 86.6606 | 18.1025 | 0 | 2018-02-19 14:00 | 14 | 2 | 86.7903 | 18.1296 | 0 | 2018-02-19 14:00 | 14 | 2 | 65.9113 | 13.7682 | 0
2018-02-19 15:00 | 15 | 2 | 86.3355 | 18.0346 | 0 | 2018-02-19 15:00 | 15 | 2 | 86.5248 | 18.0742 | 0 | 2018-02-19 15:00 | 15 | 2 | 86.7384 | 18.1188 | 0 | 2018-02-19 15:00 | 15 | 2 | 65.84 | 13.7533 | 0
2018-02-19 16:00 | 16 | 2 | 86.3493 | 18.0375 | 0 | 2018-02-19 16:00 | 16 | 2 | 86.4912 | 18.0671 | 0 | 2018-02-19 16:00 | 16 | 2 | 86.685 | 18.1076 | 0 | 2018-02-19 16:00 | 16 | 2 | 65.807 | 13.7464 | 0
2018-02-19 17:00 | 17 | 2 | 86.244 | 18.0155 | 0 | 2018-02-19 17:00 | 17 | 2 | 86.4683 | 18.0624 | 0 | 2018-02-19 17:00 | 17 | 2 | 86.6743 | 18.1054 | 0 | 2018-02-19 17:00 | 17 | 2 | 65.7942 | 13.7437 | 0
2018-02-19 18:00 | 18 | 2 | 86.3142 | 18.0302 | 0 | 2018-02-19 18:00 | 18 | 2 | 86.4378 | 18.056 | 0 | 2018-02-19 18:00 | 18 | 2 | 86.5934 | 18.0885 | 0 | 2018-02-19 18:00 | 18 | 2 | 65.7519 | 13.7349 | 0
2018-02-19 19:00 | 19 | 2 | 86.2089 | 18.0082 | 0 | 2018-02-19 19:00 | 19 | 2 | 86.3508 | 18.0378 | 0 | 2018-02-19 19:00 | 19 | 2 | 86.5583 | 18.0812 | 0 | 2018-02-19 19:00 | 19 | 2 | 65.7055 | 13.7252 | 0
2018-02-19 20:00 | 20 | 2 | 86.2181 | 18.0101 | 0 | 2018-02-19 20:00 | 20 | 2 | 86.4836 | 18.0656 | 0 | 2018-02-19 20:00 | 20 | 2 | 86.6896 | 18.1086 | 0 | 2018-02-19 20:00 | 20 | 2 | 65.8058 | 13.7462 | 0
2018-02-19 21:00 | 21 | 2 | 86.1494 | 17.9957 | 0 | 2018-02-19 21:00 | 21 | 2 | 86.4759 | 18.064 | 0 | 2018-02-19 21:00 | 21 | 2 | 86.63 | 18.0961 | 0 | 2018-02-19 21:00 | 21 | 2 | 65.7802 | 13.7408 | 0
2018-02-19 22:00 | 22 | 2 | 86.2593 | 18.0187 | 0 | 2018-02-19 22:00 | 22 | 2 | 86.5522 | 18.0799 | 0 | 2018-02-19 22:00 | 22 | 2 | 86.6468 | 18.0997 | 0 | 2018-02-19 22:00 | 22 | 2 | 65.8156 | 13.7482 | 0
2018-02-19 23:00 | 23 | 2 | 86.4424 | 18.057 | 0 | 2018-02-19 23:00 | 23 | 2 | 86.8055 | 18.1328 | 0 | 2018-02-19 23:00 | 23 | 2 | 86.8864 | 18.1497 | 0 | 2018-02-19 23:00 | 23 | 2 | 66.0029 | 13.7874 | 0
2018-02-20 | 0 | 3 | 86.4637 | 18.0614 | 0 | 2018-02-20 | 0 | 3 | 0 | 0 | 0 | 2018-02-20 | 0 | 3 | 0 | 0 | 0 | 2018-02-20 | 0 | 3 | 0 | 0 | 0
2018-02-20 01:00 | 1 | 3 | 86.5629 | 18.0821 | 0 | 2018-02-20 01:00 | 1 | 3 | 0 | 0 | 0 | 2018-02-20 01:00 | 1 | 3 | 0 | 0 | 0 | 2018-02-20 01:00 | 1 | 3 | 0 | 0 | 0
2018-02-20 02:00 | 2 | 3 | 86.3706 | 18.042 | 0 | 2018-02-20 02:00 | 2 | 3 | 0 | 0 | 0 | 2018-02-20 02:00 | 2 | 3 | 0 | 0 | 0 | 2018-02-20 02:00 | 2 | 3 | 0 | 0 | 0
2018-02-20 03:00 | 3 | 3 | 86.3523 | 18.0381 | 0 | 2018-02-20 03:00 | 3 | 3 | 0 | 0 | 0 | 2018-02-20 03:00 | 3 | 3 | 0 | 0 | 0 | 2018-02-20 03:00 | 3 | 3 | 0 | 0 | 0
2018-02-20 04:00 | 4 | 3 | 86.3676 | 18.0413 | 0 | 2018-02-20 04:00 | 4 | 3 | 0 | 0 | 0 | 2018-02-20 04:00 | 4 | 3 | 0 | 0 | 0 | 2018-02-20 04:00 | 4 | 3 | 0 | 0 | 0
2018-02-20 05:00 | 5 | 3 | 86.4027 | 18.0487 | 0 | 2018-02-20 05:00 | 5 | 3 | 0 | 0 | 0 | 2018-02-20 05:00 | 5 | 3 | 0 | 0 | 0 | 2018-02-20 05:00 | 5 | 3 | 0 | 0 | 0
2018-02-20 06:00 | 6 | 3 | 86.4652 | 18.0617 | 0 | 2018-02-20 06:00 | 6 | 3 | 0 | 0 | 0 | 2018-02-20 06:00 | 6 | 3 | 0 | 0 | 0 | 2018-02-20 06:00 | 6 | 3 | 0 | 0 | 0
2018-02-20 07:00 | 7 | 3 | 86.4012 | 18.0483 | 0 | 2018-02-20 07:00 | 7 | 3 | 0 | 0 | 0 | 2018-02-20 07:00 | 7 | 3 | 0 | 0 | 0 | 2018-02-20 07:00 | 7 | 3 | 0 | 0 | 0
2018-02-20 08:00 | 8 | 3 | 86.4515 | 18.0589 | 0 | 2018-02-20 08:00 | 8 | 3 | 0 | 0 | 0 | 2018-02-20 08:00 | 8 | 3 | 0 | 0 | 0 | 2018-02-20 08:00 | 8 | 3 | 0 | 0 | 0
2018-02-20 09:00 | 9 | 3 | 86.2028 | 18.0069 | 0 | 2018-02-20 09:00 | 9 | 3 | 0 | 0 | 0 | 2018-02-20 09:00 | 9 | 3 | 0 | 0 | 0 | 2018-02-20 09:00 | 9 | 3 | 0 | 0 | 0
2018-02-20 10:00 | 10 | 3 | 86.2715 | 18.0213 | 0 | 2018-02-20 10:00 | 10 | 3 | 0 | 0 | 0 | 2018-02-20 10:00 | 10 | 3 | 0 | 0 | 0 | 2018-02-20 10:00 | 10 | 3 | 0 | 0 | 0
2018-02-20 11:00 | 11 | 3 | 86.7567 | 18.1226 | 0 | 2018-02-20 11:00 | 11 | 3 | 0 | 0 | 0 | 2018-02-20 11:00 | 11 | 3 | 0 | 0 | 0 | 2018-02-20 11:00 | 11 | 3 | 0 | 0 | 0
2018-02-20 12:00 | 12 | 3 | 86.6194 | 18.0939 | 0 | 2018-02-20 12:00 | 12 | 3 | 0 | 0 | 0 | 2018-02-20 12:00 | 12 | 3 | 0 | 0 | 0 | 2018-02-20 12:00 | 12 | 3 | 0 | 0 | 0
2018-02-20 13:00 | 13 | 3 | 86.6377 | 18.0977 | 0 | 2018-02-20 13:00 | 13 | 3 | 0 | 0 | 0 | 2018-02-20 13:00 | 13 | 3 | 0 | 0 | 0 | 2018-02-20 13:00 | 13 | 3 | 0 | 0 | 0
2018-02-20 14:00 | 14 | 3 | 86.8757 | 18.1475 | 0 | 2018-02-20 14:00 | 14 | 3 | 0 | 0 | 0 | 2018-02-20 14:00 | 14 | 3 | 0 | 0 | 0 | 2018-02-20 14:00 | 14 | 3 | 0 | 0 | 0
2018-02-20 15:00 | 15 | 3 | 86.7994 | 18.1315 | 0 | 2018-02-20 15:00 | 15 | 3 | 0 | 0 | 0 | 2018-02-20 15:00 | 15 | 3 | 0 | 0 | 0 | 2018-02-20 15:00 | 15 | 3 | 0 | 0 | 0
2018-02-20 16:00 | 16 | 3 | 86.7674 | 18.1248 | 0 | 2018-02-20 16:00 | 16 | 3 | 0 | 0 | 0 | 2018-02-20 16:00 | 16 | 3 | 0 | 0 | 0 | 2018-02-20 16:00 | 16 | 3 | 0 | 0 | 0
2018-02-20 17:00 | 17 | 3 | 86.7384 | 18.1188 | 0 | 2018-02-20 17:00 | 17 | 3 | 0 | 0 | 0 | 2018-02-20 17:00 | 17 | 3 | 0 | 0 | 0 | 2018-02-20 17:00 | 17 | 3 | 0 | 0 | 0
2018-02-20 18:00 | 18 | 3 | 86.7124 | 18.1134 | 0 | 2018-02-20 18:00 | 18 | 3 | 0 | 0 | 0 | 2018-02-20 18:00 | 18 | 3 | 0 | 0 | 0 | 2018-02-20 18:00 | 18 | 3 | 0 | 0 | 0
2018-02-20 19:00 | 19 | 3 | 86.8376 | 18.1395 | 0 | 2018-02-20 19:00 | 19 | 3 | 0 | 0 | 0 | 2018-02-20 19:00 | 19 | 3 | 0 | 0 | 0 | 2018-02-20 19:00 | 19 | 3 | 0 | 0 | 0
2018-02-20 20:00 | 20 | 3 | 86.627 | 18.0955 | 0 | 2018-02-20 20:00 | 20 | 3 | 0 | 0 | 0 | 2018-02-20 20:00 | 20 | 3 | 0 | 0 | 0 | 2018-02-20 20:00 | 20 | 3 | 0 | 0 | 0
2018-02-20 21:00 | 21 | 3 | 86.6239 | 18.0949 | 0 | 2018-02-20 21:00 | 21 | 3 | 0 | 0 | 0 | 2018-02-20 21:00 | 21 | 3 | 0 | 0 | 0 | 2018-02-20 21:00 | 21 | 3 | 0 | 0 | 0
2018-02-20 22:00 | 22 | 3 | 86.714 | 18.1137 | 0 | 2018-02-20 22:00 | 22 | 3 | 0 | 0 | 0 | 2018-02-20 22:00 | 22 | 3 | 0 | 0 | 0 | 2018-02-20 22:00 | 22 | 3 | 0 | 0 | 0
2018-02-20 23:00 | 23 | 3 | 86.8971 | 18.1519 | 0 | 2018-02-20 23:00 | 23 | 3 | 0 | 0 | 0 | 2018-02-20 23:00 | 23 | 3 | 0 | 0 | 0 | 2018-02-20 23:00 | 23 | 3 | 0 | 0 | 0
2018-02-21 | 0 | 4 | 0 | 0 | 0 | 2018-02-21 | 0 | 4 | 0 | 0 | 0 | 2018-02-21 | 0 | 4 | 86.6712 | 18.1047 | 0 | 2018-02-21 | 0 | 4 | 32.9351 | 6.8798 | 0
2018-02-21 01:00 | 1 | 4 | 0 | 0 | 0 | 2018-02-21 01:00 | 1 | 4 | 0 | 0 | 0 | 2018-02-21 01:00 | 1 | 4 | 86.511 | 18.0713 | 0 | 2018-02-21 01:00 | 1 | 4 | 32.8742 | 6.8671 | 0
2018-02-21 02:00 | 2 | 4 | 0 | 0 | 0 | 2018-02-21 02:00 | 2 | 4 | 0 | 0 | 0 | 2018-02-21 02:00 | 2 | 4 | 86.7628 | 18.1239 | 0 | 2018-02-21 02:00 | 2 | 4 | 32.9699 | 6.8871 | 0
2018-02-21 03:00 | 3 | 4 | 0 | 0 | 0 | 2018-02-21 03:00 | 3 | 4 | 0 | 0 | 0 | 2018-02-21 03:00 | 3 | 4 | 86.7384 | 18.1188 | 0 | 2018-02-21 03:00 | 3 | 4 | 32.9606 | 6.8851 | 0
2018-02-21 04:00 | 4 | 4 | 0 | 0 | 0 | 2018-02-21 04:00 | 4 | 4 | 0 | 0 | 0 | 2018-02-21 04:00 | 4 | 4 | 86.8376 | 18.1395 | 0 | 2018-02-21 04:00 | 4 | 4 | 32.9983 | 6.893 | 0
2018-02-21 05:00 | 5 | 4 | 0 | 0 | 0 | 2018-02-21 05:00 | 5 | 4 | 0 | 0 | 0 | 2018-02-21 05:00 | 5 | 4 | 87.0222 | 18.1781 | 0 | 2018-02-21 05:00 | 5 | 4 | 33.0684 | 6.9077 | 0
2018-02-21 06:00 | 6 | 4 | 0 | 0 | 0 | 2018-02-21 06:00 | 6 | 4 | 0 | 0 | 0 | 2018-02-21 06:00 | 6 | 4 | 86.9627 | 18.1656 | 0 | 2018-02-21 06:00 | 6 | 4 | 33.0458 | 6.9029 | 0
2018-02-21 07:00 | 7 | 4 | 0 | 0 | 0 | 2018-02-21 07:00 | 7 | 4 | 0 | 0 | 0 | 2018-02-21 07:00 | 7 | 4 | 87.1321 | 18.201 | 0 | 2018-02-21 07:00 | 7 | 4 | 33.1102 | 6.9164 | 0
2018-02-21 08:00 | 8 | 4 | 0 | 0 | 0 | 2018-02-21 08:00 | 8 | 4 | 0 | 0 | 0 | 2018-02-21 08:00 | 8 | 4 | 87.1931 | 18.2138 | 0 | 2018-02-21 08:00 | 8 | 4 | 33.1334 | 6.9212 | 0
2018-02-21 09:00 | 9 | 4 | 0 | 0 | 0 | 2018-02-21 09:00 | 9 | 4 | 0 | 0 | 0 | 2018-02-21 09:00 | 9 | 4 | 86.7155 | 18.114 | 0 | 2018-02-21 09:00 | 9 | 4 | 32.9519 | 6.8833 | 0
2018-02-21 10:00 | 10 | 4 | 0 | 0 | 0 | 2018-02-21 10:00 | 10 | 4 | 0 | 0 | 0 | 2018-02-21 10:00 | 10 | 4 | 86.6743 | 18.1054 | 0 | 2018-02-21 10:00 | 10 | 4 | 32.9362 | 6.88 | 0
2018-02-21 11:00 | 11 | 4 | 0 | 0 | 0 | 2018-02-21 11:00 | 11 | 4 | 0 | 0 | 0 | 2018-02-21 11:00 | 11 | 4 | 86.8956 | 18.1516 | 0 | 2018-02-21 11:00 | 11 | 4 | 33.0203 | 6.8976 | 0
2018-02-21 12:00 | 12 | 4 | 0 | 0 | 0 | 2018-02-21 12:00 | 12 | 4 | 0 | 0 | 0 | 2018-02-21 12:00 | 12 | 4 | 86.9276 | 18.1583 | 0 | 2018-02-21 12:00 | 12 | 4 | 33.0325 | 6.9002 | 0
2018-02-21 13:00 | 13 | 4 | 0 | 0 | 0 | 2018-02-21 13:00 | 13 | 4 | 0 | 0 | 0 | 2018-02-21 13:00 | 13 | 4 | 87.2541 | 18.2265 | 0 | 2018-02-21 13:00 | 13 | 4 | 33.1566 | 6.9261 | 0
2018-02-21 14:00 | 14 | 4 | 0 | 0 | 0 | 2018-02-21 14:00 | 14 | 4 | 0 | 0 | 0 | 2018-02-21 14:00 | 14 | 4 | 87.4037 | 18.2578 | 0 | 2018-02-21 14:00 | 14 | 4 | 33.2134 | 6.9379 | 0
2018-02-21 15:00 | 15 | 4 | 0 | 0 | 0 | 2018-02-21 15:00 | 15 | 4 | 0 | 0 | 0 | 2018-02-21 15:00 | 15 | 4 | 87.2129 | 18.2179 | 0 | 2018-02-21 15:00 | 15 | 4 | 33.1409 | 6.9228 | 0
2018-02-21 16:00 | 16 | 4 | 0 | 0 | 0 | 2018-02-21 16:00 | 16 | 4 | 0 | 0 | 0 | 2018-02-21 16:00 | 16 | 4 | 86.9718 | 18.1675 | 0 | 2018-02-21 16:00 | 16 | 4 | 33.0493 | 6.9037 | 0
2018-02-21 17:00 | 17 | 4 | 0 | 0 | 0 | 2018-02-21 17:00 | 17 | 4 | 0 | 0 | 0 | 2018-02-21 17:00 | 17 | 4 | 87.1397 | 18.2026 | 0 | 2018-02-21 17:00 | 17 | 4 | 33.1131 | 6.917 | 0
2018-02-21 18:00 | 18 | 4 | 0 | 0 | 0 | 2018-02-21 18:00 | 18 | 4 | 0 | 0 | 0 | 2018-02-21 18:00 | 18 | 4 | 87.2435 | 18.2243 | 0 | 2018-02-21 18:00 | 18 | 4 | 33.1525 | 6.9252 | 0
2018-02-21 19:00 | 19 | 4 | 0 | 0 | 0 | 2018-02-21 19:00 | 19 | 4 | 0 | 0 | 0 | 2018-02-21 19:00 | 19 | 4 | 86.8894 | 18.1503 | 0 | 2018-02-21 19:00 | 19 | 4 | 33.018 | 6.8971 | 0
2018-02-21 20:00 | 20 | 4 | 0 | 0 | 0 | 2018-02-21 20:00 | 20 | 4 | 0 | 0 | 0 | 2018-02-21 20:00 | 20 | 4 | 87.1839 | 18.2118 | 0 | 2018-02-21 20:00 | 20 | 4 | 33.1299 | 6.9205 | 0
2018-02-21 21:00 | 21 | 4 | 0 | 0 | 0 | 2018-02-21 21:00 | 21 | 4 | 0 | 0 | 0 | 2018-02-21 21:00 | 21 | 4 | 87.2419 | 18.224 | 0 | 2018-02-21 21:00 | 21 | 4 | 33.1519 | 6.9251 | 0
2018-02-21 22:00 | 22 | 4 | 0 | 0 | 0 | 2018-02-21 22:00 | 22 | 4 | 0 | 0 | 0 | 2018-02-21 22:00 | 22 | 4 | 87.1733 | 18.2096 | 0 | 2018-02-21 22:00 | 22 | 4 | 33.1259 | 6.9197 | 0
2018-02-21 23:00 | 23 | 4 | 0 | 0 | 0 | 2018-02-21 23:00 | 23 | 4 | 0 | 0 | 0 | 2018-02-21 23:00 | 23 | 4 | 87.2557 | 18.2268 | 0 | 2018-02-21 23:00 | 23 | 4 | 33.1572 | 6.9262 | 0
2018-02-22 | 0 | 5 | 86.5492 | 18.0793 | 0 | 2018-02-22 | 0 | 5 | 0 | 0 | 0 | 2018-02-22 | 0 | 5 | 0 | 0 | 0 | 2018-02-22 | 0 | 5 | 0 | 0 | 0
2018-02-22 01:00 | 1 | 5 | 86.7201 | 18.115 | 0 | 2018-02-22 01:00 | 1 | 5 | 0 | 0 | 0 | 2018-02-22 01:00 | 1 | 5 | 0 | 0 | 0 | 2018-02-22 01:00 | 1 | 5 | 0 | 0 | 0
2018-02-22 02:00 | 2 | 5 | 86.5095 | 18.071 | 0 | 2018-02-22 02:00 | 2 | 5 | 0 | 0 | 0 | 2018-02-22 02:00 | 2 | 5 | 0 | 0 | 0 | 2018-02-22 02:00 | 2 | 5 | 0 | 0 | 0
2018-02-22 03:00 | 3 | 5 | 86.4576 | 18.0601 | 0 | 2018-02-22 03:00 | 3 | 5 | 0 | 0 | 0 | 2018-02-22 03:00 | 3 | 5 | 0 | 0 | 0 | 2018-02-22 03:00 | 3 | 5 | 0 | 0 | 0
2018-02-22 04:00 | 4 | 5 | 86.6316 | 18.0965 | 0 | 2018-02-22 04:00 | 4 | 5 | 0 | 0 | 0 | 2018-02-22 04:00 | 4 | 5 | 0 | 0 | 0 | 2018-02-22 04:00 | 4 | 5 | 0 | 0 | 0
2018-02-22 05:00 | 5 | 5 | 86.569 | 18.0834 | 0 | 2018-02-22 05:00 | 5 | 5 | 0 | 0 | 0 | 2018-02-22 05:00 | 5 | 5 | 0 | 0 | 0 | 2018-02-22 05:00 | 5 | 5 | 0 | 0 | 0
2018-02-22 06:00 | 6 | 5 | 86.6468 | 18.0997 | 0 | 2018-02-22 06:00 | 6 | 5 | 0 | 0 | 0 | 2018-02-22 06:00 | 6 | 5 | 0 | 0 | 0 | 2018-02-22 06:00 | 6 | 5 | 0 | 0 | 0
2018-02-22 07:00 | 7 | 5 | 86.6361 | 18.0974 | 0 | 2018-02-22 07:00 | 7 | 5 | 0 | 0 | 0 | 2018-02-22 07:00 | 7 | 5 | 0 | 0 | 0 | 2018-02-22 07:00 | 7 | 5 | 0 | 0 | 0
2018-02-22 08:00 | 8 | 5 | 86.6819 | 18.107 | 0 | 2018-02-22 08:00 | 8 | 5 | 0 | 0 | 0 | 2018-02-22 08:00 | 8 | 5 | 0 | 0 | 0 | 2018-02-22 08:00 | 8 | 5 | 0 | 0 | 0
2018-02-22 09:00 | 9 | 5 | 86.7094 | 18.1127 | 0 | 2018-02-22 09:00 | 9 | 5 | 0 | 0 | 0 | 2018-02-22 09:00 | 9 | 5 | 0 | 0 | 0 | 2018-02-22 09:00 | 9 | 5 | 0 | 0 | 0
2018-02-22 10:00 | 10 | 5 | 86.7933 | 18.1303 | 0 | 2018-02-22 10:00 | 10 | 5 | 0 | 0 | 0 | 2018-02-22 10:00 | 10 | 5 | 0 | 0 | 0 | 2018-02-22 10:00 | 10 | 5 | 0 | 0 | 0
2018-02-22 11:00 | 11 | 5 | 86.8009 | 18.1318 | 0 | 2018-02-22 11:00 | 11 | 5 | 0 | 0 | 0 | 2018-02-22 11:00 | 11 | 5 | 0 | 0 | 0 | 2018-02-22 11:00 | 11 | 5 | 0 | 0 | 0
2018-02-22 12:00 | 12 | 5 | 86.6728 | 18.1051 | 0 | 2018-02-22 12:00 | 12 | 5 | 0 | 0 | 0 | 2018-02-22 12:00 | 12 | 5 | 0 | 0 | 0 | 2018-02-22 12:00 | 12 | 5 | 0 | 0 | 0
2018-02-22 13:00 | 13 | 5 | 86.6316 | 18.0965 | 0 | 2018-02-22 13:00 | 13 | 5 | 0 | 0 | 0 | 2018-02-22 13:00 | 13 | 5 | 0 | 0 | 0 | 2018-02-22 13:00 | 13 | 5 | 0 | 0 | 0
2018-02-22 14:00 | 14 | 5 | 86.6316 | 18.0965 | 0 | 2018-02-22 14:00 | 14 | 5 | 0 | 0 | 0 | 2018-02-22 14:00 | 14 | 5 | 0 | 0 | 0 | 2018-02-22 14:00 | 14 | 5 | 0 | 0 | 0
2018-02-22 15:00 | 15 | 5 | 86.6636 | 18.1032 | 0 | 2018-02-22 15:00 | 15 | 5 | 0 | 0 | 0 | 2018-02-22 15:00 | 15 | 5 | 0 | 0 | 0 | 2018-02-22 15:00 | 15 | 5 | 0 | 0 | 0
2018-02-22 16:00 | 16 | 5 | 86.5568 | 18.0808 | 0 | 2018-02-22 16:00 | 16 | 5 | 0 | 0 | 0 | 2018-02-22 16:00 | 16 | 5 | 0 | 0 | 0 | 2018-02-22 16:00 | 16 | 5 | 0 | 0 | 0
2018-02-22 17:00 | 17 | 5 | 86.6865 | 18.1079 | 0 | 2018-02-22 17:00 | 17 | 5 | 0 | 0 | 0 | 2018-02-22 17:00 | 17 | 5 | 0 | 0 | 0 | 2018-02-22 17:00 | 17 | 5 | 0 | 0 | 0
2018-02-22 18:00 | 18 | 5 | 86.7262 | 18.1162 | 0 | 2018-02-22 18:00 | 18 | 5 | 0 | 0 | 0 | 2018-02-22 18:00 | 18 | 5 | 0 | 0 | 0 | 2018-02-22 18:00 | 18 | 5 | 0 | 0 | 0
2018-02-22 19:00 | 19 | 5 | 86.5187 | 18.0729 | 0 | 2018-02-22 19:00 | 19 | 5 | 0 | 0 | 0 | 2018-02-22 19:00 | 19 | 5 | 0 | 0 | 0 | 2018-02-22 19:00 | 19 | 5 | 0 | 0 | 0
2018-02-22 20:00 | 20 | 5 | 86.5766 | 18.085 | 0 | 2018-02-22 20:00 | 20 | 5 | 0 | 0 | 0 | 2018-02-22 20:00 | 20 | 5 | 0 | 0 | 0 | 2018-02-22 20:00 | 20 | 5 | 0 | 0 | 0
2018-02-22 21:00 | 21 | 5 | 86.6194 | 18.0939 | 0 | 2018-02-22 21:00 | 21 | 5 | 0 | 0 | 0 | 2018-02-22 21:00 | 21 | 5 | 0 | 0 | 0 | 2018-02-22 21:00 | 21 | 5 | 0 | 0 | 0
2018-02-22 22:00 | 22 | 5 | 86.6743 | 18.1054 | 0 | 2018-02-22 22:00 | 22 | 5 | 0 | 0 | 0 | 2018-02-22 22:00 | 22 | 5 | 0 | 0 | 0 | 2018-02-22 22:00 | 22 | 5 | 0 | 0 | 0
2018-02-22 23:00 | 23 | 5 | 86.5644 | 18.0824 | 0 | 2018-02-22 23:00 | 23 | 5 | 0 | 0 | 0 | 2018-02-22 23:00 | 23 | 5 | 0 | 0 | 0 | 2018-02-22 23:00 | 23 | 5 | 0 | 0 | 0
2018-02-23 | 0 | 6 | 86.2226 | 18.011 | 0 | 2018-02-23 | 0 | 6 | 86.688 | 18.1083 | 0 | 2018-02-23 | 0 | 6 | 0 | 0 | 0 | 2018-02-23 | 0 | 6 | 32.9414 | 6.8811 | 0
2018-02-23 01:00 | 1 | 6 | 86.1128 | 17.9881 | 0 | 2018-02-23 01:00 | 1 | 6 | 86.5232 | 18.0738 | 0 | 2018-02-23 01:00 | 1 | 6 | 0 | 0 | 0 | 2018-02-23 01:00 | 1 | 6 | 32.8788 | 6.8681 | 0
2018-02-23 02:00 | 2 | 6 | 86.2791 | 18.0228 | 0 | 2018-02-23 02:00 | 2 | 6 | 86.6896 | 18.1086 | 0 | 2018-02-23 02:00 | 2 | 6 | 0 | 0 | 0 | 2018-02-23 02:00 | 2 | 6 | 32.942 | 6.8813 | 0
2018-02-23 03:00 | 3 | 6 | 86.0014 | 17.9648 | 0 | 2018-02-23 03:00 | 3 | 6 | 86.4485 | 18.0582 | 0 | 2018-02-23 03:00 | 3 | 6 | 0 | 0 | 0 | 2018-02-23 03:00 | 3 | 6 | 32.8504 | 6.8621 | 0
2018-02-23 04:00 | 4 | 6 | 86.0533 | 17.9757 | 0 | 2018-02-23 04:00 | 4 | 6 | 86.4347 | 18.0553 | 0 | 2018-02-23 04:00 | 4 | 6 | 0 | 0 | 0 | 2018-02-23 04:00 | 4 | 6 | 32.8452 | 6.861 | 0
2018-02-23 05:00 | 5 | 6 | 86.2257 | 18.0117 | 0 | 2018-02-23 05:00 | 5 | 6 | 86.6117 | 18.0923 | 0 | 2018-02-23 05:00 | 5 | 6 | 0 | 0 | 0 | 2018-02-23 05:00 | 5 | 6 | 32.9124 | 6.8751 | 0
2018-02-23 06:00 | 6 | 6 | 86.4332 | 18.055 | 0 | 2018-02-23 06:00 | 6 | 6 | 86.9352 | 18.1599 | 0 | 2018-02-23 06:00 | 6 | 6 | 0 | 0 | 0 | 2018-02-23 06:00 | 6 | 6 | 33.0354 | 6.9008 | 0
2018-02-23 07:00 | 7 | 6 | 86.5873 | 18.0872 | 0 | 2018-02-23 07:00 | 7 | 6 | 87.0619 | 18.1864 | 0 | 2018-02-23 07:00 | 7 | 6 | 0 | 0 | 0 | 2018-02-23 07:00 | 7 | 6 | 33.0835 | 6.9108 | 0
2018-02-23 08:00 | 8 | 6 | 86.3691 | 18.0416 | 0 | 2018-02-23 08:00 | 8 | 6 | 86.7811 | 18.1277 | 0 | 2018-02-23 08:00 | 8 | 6 | 0 | 0 | 0 | 2018-02-23 08:00 | 8 | 6 | 32.9768 | 6.8885 | 0
2018-02-23 09:00 | 9 | 6 | 86.334 | 18.0343 | 0 | 2018-02-23 09:00 | 9 | 6 | 86.7399 | 18.1191 | 0 | 2018-02-23 09:00 | 9 | 6 | 0 | 0 | 0 | 2018-02-23 09:00 | 9 | 6 | 32.9612 | 6.8853 | 0
2018-02-23 10:00 | 10 | 6 | 86.5126 | 18.0716 | 0 | 2018-02-23 10:00 | 10 | 6 | 86.862 | 18.1446 | 0 | 2018-02-23 10:00 | 10 | 6 | 0 | 0 | 0 | 2018-02-23 10:00 | 10 | 6 | 33.0076 | 6.8949 | 0
2018-02-23 11:00 | 11 | 6 | 86.5003 | 18.069 | 0 | 2018-02-23 11:00 | 11 | 6 | 86.9306 | 18.1589 | 0 | 2018-02-23 11:00 | 11 | 6 | 0 | 0 | 0 | 2018-02-23 11:00 | 11 | 6 | 33.0336 | 6.9004 | 0
2018-02-23 12:00 | 12 | 6 | 86.7002 | 18.1108 | 0 | 2018-02-23 12:00 | 12 | 6 | 87.1412 | 18.2029 | 0 | 2018-02-23 12:00 | 12 | 6 | 0 | 0 | 0 | 2018-02-23 12:00 | 12 | 6 | 33.1137 | 6.9171 | 0
2018-02-23 13:00 | 13 | 6 | 86.363 | 18.0404 | 0 | 2018-02-23 13:00 | 13 | 6 | 86.8009 | 18.1318 | 0 | 2018-02-23 13:00 | 13 | 6 | 0 | 0 | 0 | 2018-02-23 13:00 | 13 | 6 | 32.9843 | 6.8901 | 0
2018-02-23 14:00 | 14 | 6 | 86.4408 | 18.0566 | 0 | 2018-02-23 14:00 | 14 | 6 | 86.8635 | 18.1449 | 0 | 2018-02-23 14:00 | 14 | 6 | 0 | 0 | 0 | 2018-02-23 14:00 | 14 | 6 | 33.0081 | 6.8951 | 0
2018-02-23 15:00 | 15 | 6 | 86.2943 | 18.026 | 0 | 2018-02-23 15:00 | 15 | 6 | 86.6743 | 18.1054 | 0 | 2018-02-23 15:00 | 15 | 6 | 0 | 0 | 0 | 2018-02-23 15:00 | 15 | 6 | 32.9362 | 6.88 | 0
2018-02-23 16:00 | 16 | 6 | 86.3706 | 18.042 | 0 | 2018-02-23 16:00 | 16 | 6 | 86.7491 | 18.121 | 0 | 2018-02-23 16:00 | 16 | 6 | 0 | 0 | 0 | 2018-02-23 16:00 | 16 | 6 | 32.9647 | 6.886 | 0
2018-02-23 17:00 | 17 | 6 | 86.2882 | 18.0247 | 0 | 2018-02-23 17:00 | 17 | 6 | 86.7445 | 18.1201 | 0 | 2018-02-23 17:00 | 17 | 6 | 0 | 0 | 0 | 2018-02-23 17:00 | 17 | 6 | 32.9629 | 6.8856 | 0
2018-02-23 18:00 | 18 | 6 | 86.1875 | 18.0037 | 0 | 2018-02-23 18:00 | 18 | 6 | 86.6667 | 18.1038 | 0 | 2018-02-23 18:00 | 18 | 6 | 0 | 0 | 0 | 2018-02-23 18:00 | 18 | 6 | 32.9333 | 6.8794 | 0
2018-02-23 19:00 | 19 | 6 | 86.099 | 17.9852 | 0 | 2018-02-23 19:00 | 19 | 6 | 86.5431 | 18.078 | 0 | 2018-02-23 19:00 | 19 | 6 | 0 | 0 | 0 | 2018-02-23 19:00 | 19 | 6 | 32.8864 | 6.8696 | 0
2018-02-23 20:00 | 20 | 6 | 86.1997 | 18.0063 | 0 | 2018-02-23 20:00 | 20 | 6 | 86.5187 | 18.0729 | 0 | 2018-02-23 20:00 | 20 | 6 | 0 | 0 | 0 | 2018-02-23 20:00 | 20 | 6 | 32.8771 | 6.8677 | 0
2018-02-23 21:00 | 21 | 6 | 86.3767 | 18.0432 | 0 | 2018-02-23 21:00 | 21 | 6 | 86.7247 | 18.1159 | 0 | 2018-02-23 21:00 | 21 | 6 | 0 | 0 | 0 | 2018-02-23 21:00 | 21 | 6 | 32.9554 | 6.8841 | 0
2018-02-23 22:00 | 22 | 6 | 86.3691 | 18.0416 | 0 | 2018-02-23 22:00 | 22 | 6 | 86.7659 | 18.1245 | 0 | 2018-02-23 22:00 | 22 | 6 | 0 | 0 | 0 | 2018-02-23 22:00 | 22 | 6 | 32.971 | 6.8873 | 0
2018-02-23 23:00 | 23 | 6 | 86.4012 | 18.0483 | 0 | 2018-02-23 23:00 | 23 | 6 | 86.7918 | 18.1299 | 0 | 2018-02-23 23:00 | 23 | 6 | 0 | 0 | 0 | 2018-02-23 23:00 | 23 | 6 | 32.9809 | 6.8894 | 0
2018-02-24 | 0 | 7 | 86.0121 | 17.9671 | 0 | 2018-02-24 | 0 | 7 | 0 | 0 | 0 | 2018-02-24 | 0 | 7 | 86.5507 | 18.0796 | 0 | 2018-02-24 | 0 | 7 | 32.8893 | 6.8702 | 0
2018-02-24 01:00 | 1 | 7 | 85.919 | 17.9476 | 0 | 2018-02-24 01:00 | 1 | 7 | 0 | 0 | 0 | 2018-02-24 01:00 | 1 | 7 | 86.5324 | 18.0758 | 0 | 2018-02-24 01:00 | 1 | 7 | 32.8823 | 6.8688 | 0
2018-02-24 02:00 | 2 | 7 | 86.0533 | 17.9757 | 0 | 2018-02-24 02:00 | 2 | 7 | 0 | 0 | 0 | 2018-02-24 02:00 | 2 | 7 | 86.6453 | 18.0993 | 0 | 2018-02-24 02:00 | 2 | 7 | 32.9252 | 6.8777 | 0
2018-02-24 03:00 | 3 | 7 | 86.1677 | 17.9996 | 0 | 2018-02-24 03:00 | 3 | 7 | 0 | 0 | 0 | 2018-02-24 03:00 | 3 | 7 | 86.7002 | 18.1108 | 0 | 2018-02-24 03:00 | 3 | 7 | 32.9461 | 6.8821 | 0
2018-02-24 04:00 | 4 | 7 | 86.3081 | 18.0289 | 0 | 2018-02-24 04:00 | 4 | 7 | 0 | 0 | 0 | 2018-02-24 04:00 | 4 | 7 | 86.8513 | 18.1424 | 0 | 2018-02-24 04:00 | 4 | 7 | 33.0035 | 6.8941 | 0
2018-02-24 05:00 | 5 | 7 | 86.2562 | 18.0181 | 0 | 2018-02-24 05:00 | 5 | 7 | 0 | 0 | 0 | 2018-02-24 05:00 | 5 | 7 | 86.8605 | 18.1443 | 0 | 2018-02-24 05:00 | 5 | 7 | 33.007 | 6.8948 | 0
2018-02-24 06:00 | 6 | 7 | 86.1234 | 17.9903 | 0 | 2018-02-24 06:00 | 6 | 7 | 0 | 0 | 0 | 2018-02-24 06:00 | 6 | 7 | 86.6682 | 18.1041 | 0 | 2018-02-24 06:00 | 6 | 7 | 32.9339 | 6.8796 | 0
2018-02-24 07:00 | 7 | 7 | 86.1906 | 18.0044 | 0 | 2018-02-24 07:00 | 7 | 7 | 0 | 0 | 0 | 2018-02-24 07:00 | 7 | 7 | 86.7247 | 18.1159 | 0 | 2018-02-24 07:00 | 7 | 7 | 32.9554 | 6.8841 | 0
2018-02-24 08:00 | 8 | 7 | 86.36 | 18.0397 | 0 | 2018-02-24 08:00 | 8 | 7 | 0 | 0 | 0 | 2018-02-24 08:00 | 8 | 7 | 86.952 | 18.1634 | 0 | 2018-02-24 08:00 | 8 | 7 | 33.0418 | 6.9021 | 0
2018-02-24 09:00 | 9 | 7 | 86.4912 | 18.0671 | 0 | 2018-02-24 09:00 | 9 | 7 | 0 | 0 | 0 | 2018-02-24 09:00 | 9 | 7 | 87.0588 | 18.1857 | 0 | 2018-02-24 09:00 | 9 | 7 | 33.0823 | 6.9106 | 0
2018-02-24 10:00 | 10 | 7 | 86.1982 | 18.0059 | 0 | 2018-02-24 10:00 | 10 | 7 | 0 | 0 | 0 | 2018-02-24 10:00 | 10 | 7 | 86.6392 | 18.0981 | 0 | 2018-02-24 10:00 | 10 | 7 | 32.9229 | 6.8773 | 0
2018-02-24 11:00 | 11 | 7 | 86.1707 | 18.0002 | 0 | 2018-02-24 11:00 | 11 | 7 | 0 | 0 | 0 | 2018-02-24 11:00 | 11 | 7 | 86.8849 | 18.1494 | 0 | 2018-02-24 11:00 | 11 | 7 | 33.0163 | 6.8968 | 0
2018-02-24 12:00 | 12 | 7 | 86.5019 | 18.0694 | 0 | 2018-02-24 12:00 | 12 | 7 | 0 | 0 | 0 | 2018-02-24 12:00 | 12 | 7 | 87.1504 | 18.2048 | 0 | 2018-02-24 12:00 | 12 | 7 | 33.1172 | 6.9178 | 0
2018-02-24 13:00 | 13 | 7 | 86.6148 | 18.093 | 0 | 2018-02-24 13:00 | 13 | 7 | 0 | 0 | 0 | 2018-02-24 13:00 | 13 | 7 | 87.3167 | 18.2396 | 0 | 2018-02-24 13:00 | 13 | 7 | 33.1803 | 6.931 | 0
2018-02-24 14:00 | 14 | 7 | 86.4439 | 18.0573 | 0 | 2018-02-24 14:00 | 14 | 7 | 0 | 0 | 0 | 2018-02-24 14:00 | 14 | 7 | 87.0832 | 18.1908 | 0 | 2018-02-24 14:00 | 14 | 7 | 33.0916 | 6.9125 | 0
2018-02-24 15:00 | 15 | 7 | 86.5522 | 18.0799 | 0 | 2018-02-24 15:00 | 15 | 7 | 0 | 0 | 0 | 2018-02-24 15:00 | 15 | 7 | 87.2938 | 18.2348 | 0 | 2018-02-24 15:00 | 15 | 7 | 33.1716 | 6.9292 | 0
2018-02-24 16:00 | 16 | 7 | 86.5644 | 18.0824 | 0 | 2018-02-24 16:00 | 16 | 7 | 0 | 0 | 0 | 2018-02-24 16:00 | 16 | 7 | 87.3579 | 18.2482 | 0 | 2018-02-24 16:00 | 16 | 7 | 33.196 | 6.9343 | 0
2018-02-24 17:00 | 17 | 7 | 86.7445 | 18.1201 | 0 | 2018-02-24 17:00 | 17 | 7 | 0 | 0 | 0 | 2018-02-24 17:00 | 17 | 7 | 87.57 | 18.2925 | 0 | 2018-02-24 17:00 | 17 | 7 | 33.2766 | 6.9511 | 0
2018-02-24 18:00 | 18 | 7 | 86.4668 | 18.062 | 0 | 2018-02-24 18:00 | 18 | 7 | 0 | 0 | 0 | 2018-02-24 18:00 | 18 | 7 | 87.3014 | 18.2364 | 0 | 2018-02-24 18:00 | 18 | 7 | 33.1745 | 6.9298 | 0
2018-02-24 19:00 | 19 | 7 | 86.3661 | 18.041 | 0 | 2018-02-24 19:00 | 19 | 7 | 0 | 0 | 0 | 2018-02-24 19:00 | 19 | 7 | 87.0954 | 18.1934 | 0 | 2018-02-24 19:00 | 19 | 7 | 33.0963 | 6.9135 | 0
2018-02-24 20:00 | 20 | 7 | 86.1173 | 17.989 | 0 | 2018-02-24 20:00 | 20 | 7 | 0 | 0 | 0 | 2018-02-24 20:00 | 20 | 7 | 86.891 | 18.1507 | 0 | 2018-02-24 20:00 | 20 | 7 | 33.0186 | 6.8973 | 0
2018-02-24 21:00 | 21 | 7 | 86.1555 | 17.997 | 0 | 2018-02-24 21:00 | 21 | 7 | 0 | 0 | 0 | 2018-02-24 21:00 | 21 | 7 | 86.9245 | 18.1577 | 0 | 2018-02-24 21:00 | 21 | 7 | 33.0313 | 6.8999 | 0
2018-02-24 22:00 | 22 | 7 | 86.2211 | 18.0107 | 0 | 2018-02-24 22:00 | 22 | 7 | 0 | 0 | 0 | 2018-02-24 22:00 | 22 | 7 | 87.0054 | 18.1746 | 0 | 2018-02-24 22:00 | 22 | 7 | 33.0621 | 6.9063 | 0
2018-02-24 23:00 | 23 | 7 | 86.2226 | 18.011 | 0 | 2018-02-24 23:00 | 23 | 7 | 0 | 0 | 0 | 2018-02-24 23:00 | 23 | 7 | 87.0787 | 18.1899 | 0 | 2018-02-24 23:00 | 23 | 7 | 33.0899 | 6.9122 | 0
2018-02-25 | 0 | 1 | 86.2364 | 18.0139 | 0 | 2018-02-25 | 0 | 1 | 86.7994 | 18.1315 | 0 | 2018-02-25 | 0 | 1 | 0 | 0 | 0 | 2018-02-25 | 0 | 1 | 32.9838 | 6.89 | 0
2018-02-25 01:00 | 1 | 1 | 86.3188 | 18.0311 | 0 | 2018-02-25 01:00 | 1 | 1 | 86.952 | 18.1634 | 0 | 2018-02-25 01:00 | 1 | 1 | 0 | 0 | 0 | 2018-02-25 01:00 | 1 | 1 | 33.0418 | 6.9021 | 0
2018-02-25 02:00 | 2 | 1 | 86.2119 | 18.0088 | 0 | 2018-02-25 02:00 | 2 | 1 | 86.8177 | 18.1353 | 0 | 2018-02-25 02:00 | 2 | 1 | 0 | 0 | 0 | 2018-02-25 02:00 | 2 | 1 | 32.9907 | 6.8914 | 0
2018-02-25 03:00 | 3 | 1 | 86.1845 | 18.0031 | 0 | 2018-02-25 03:00 | 3 | 1 | 86.7857 | 18.1287 | 0 | 2018-02-25 03:00 | 3 | 1 | 0 | 0 | 0 | 2018-02-25 03:00 | 3 | 1 | 32.9786 | 6.8889 | 0
2018-02-25 04:00 | 4 | 1 | 86.2455 | 18.0158 | 0 | 2018-02-25 04:00 | 4 | 1 | 86.833 | 18.1385 | 0 | 2018-02-25 04:00 | 4 | 1 | 0 | 0 | 0 | 2018-02-25 04:00 | 4 | 1 | 32.9965 | 6.8926 | 0
2018-02-25 05:00 | 5 | 1 | 86.2333 | 18.0133 | 0 | 2018-02-25 05:00 | 5 | 1 | 86.833 | 18.1385 | 0 | 2018-02-25 05:00 | 5 | 1 | 0 | 0 | 0 | 2018-02-25 05:00 | 5 | 1 | 32.9965 | 6.8926 | 0
2018-02-25 06:00 | 6 | 1 | 86.2776 | 18.0225 | 0 | 2018-02-25 06:00 | 6 | 1 | 86.8528 | 18.1427 | 0 | 2018-02-25 06:00 | 6 | 1 | 0 | 0 | 0 | 2018-02-25 06:00 | 6 | 1 | 33.0041 | 6.8942 | 0
2018-02-25 07:00 | 7 | 1 | 86.2867 | 18.0244 | 0 | 2018-02-25 07:00 | 7 | 1 | 86.8452 | 18.1411 | 0 | 2018-02-25 07:00 | 7 | 1 | 0 | 0 | 0 | 2018-02-25 07:00 | 7 | 1 | 33.0012 | 6.8936 | 0
2018-02-25 08:00 | 8 | 1 | 86.2989 | 18.027 | 0 | 2018-02-25 08:00 | 8 | 1 | 86.9032 | 18.1532 | 0 | 2018-02-25 08:00 | 8 | 1 | 0 | 0 | 0 | 2018-02-25 08:00 | 8 | 1 | 33.0232 | 6.8982 | 0
2018-02-25 09:00 | 9 | 1 | 86.2867 | 18.0244 | 0 | 2018-02-25 09:00 | 9 | 1 | 86.8162 | 18.135 | 0 | 2018-02-25 09:00 | 9 | 1 | 0 | 0 | 0 | 2018-02-25 09:00 | 9 | 1 | 32.9902 | 6.8913 | 0
2018-02-25 10:00 | 10 | 1 | 86.2882 | 18.0247 | 0 | 2018-02-25 10:00 | 10 | 1 | 86.8528 | 18.1427 | 0 | 2018-02-25 10:00 | 10 | 1 | 0 | 0 | 0 | 2018-02-25 10:00 | 10 | 1 | 33.0041 | 6.8942 | 0
2018-02-25 11:00 | 11 | 1 | 86.1845 | 18.0031 | 0 | 2018-02-25 11:00 | 11 | 1 | 86.743 | 18.1197 | 0 | 2018-02-25 11:00 | 11 | 1 | 0 | 0 | 0 | 2018-02-25 11:00 | 11 | 1 | 32.9623 | 6.8855 | 0
2018-02-25 12:00 | 12 | 1 | 86.1418 | 17.9942 | 0 | 2018-02-25 12:00 | 12 | 1 | 86.714 | 18.1137 | 0 | 2018-02-25 12:00 | 12 | 1 | 0 | 0 | 0 | 2018-02-25 12:00 | 12 | 1 | 32.9513 | 6.8832 | 0
2018-02-25 13:00 | 13 | 1 | 86.1479 | 17.9954 | 0 | 2018-02-25 13:00 | 13 | 1 | 86.7659 | 18.1245 | 0 | 2018-02-25 13:00 | 13 | 1 | 0 | 0 | 0 | 2018-02-25 13:00 | 13 | 1 | 32.971 | 6.8873 | 0
2018-02-25 14:00 | 14 | 1 | 86.1112 | 17.9878 | 0 | 2018-02-25 14:00 | 14 | 1 | 86.7018 | 18.1111 | 0 | 2018-02-25 14:00 | 14 | 1 | 0 | 0 | 0 | 2018-02-25 14:00 | 14 | 1 | 32.9467 | 6.8822 | 0
2018-02-25 15:00 | 15 | 1 | 86.2455 | 18.0158 | 0 | 2018-02-25 15:00 | 15 | 1 | 86.8482 | 18.1417 | 0 | 2018-02-25 15:00 | 15 | 1 | 0 | 0 | 0 | 2018-02-25 15:00 | 15 | 1 | 33.0023 | 6.8939 | 0
2018-02-25 16:00 | 16 | 1 | 86.3447 | 18.0365 | 0 | 2018-02-25 16:00 | 16 | 1 | 86.9398 | 18.1609 | 0 | 2018-02-25 16:00 | 16 | 1 | 0 | 0 | 0 | 2018-02-25 16:00 | 16 | 1 | 33.0371 | 6.9011 | 0
2018-02-25 17:00 | 17 | 1 | 86.4805 | 18.0649 | 0 | 2018-02-25 17:00 | 17 | 1 | 86.9856 | 18.1704 | 0 | 2018-02-25 17:00 | 17 | 1 | 0 | 0 | 0 | 2018-02-25 17:00 | 17 | 1 | 33.0545 | 6.9048 | 0
2018-02-25 18:00 | 18 | 1 | 86.4332 | 18.055 | 0 | 2018-02-25 18:00 | 18 | 1 | 86.92 | 18.1567 | 0 | 2018-02-25 18:00 | 18 | 1 | 0 | 0 | 0 | 2018-02-25 18:00 | 18 | 1 | 33.0296 | 6.8996 | 0
2018-02-25 19:00 | 19 | 1 | 85.6794 | 17.8976 | 0 | 2018-02-25 19:00 | 19 | 1 | 85.9266 | 17.9492 | 0 | 2018-02-25 19:00 | 19 | 1 | 0 | 0 | 0 | 2018-02-25 19:00 | 19 | 1 | 32.6521 | 6.8207 | 0
2018-02-25 20:00 | 20 | 1 | 86.3294 | 18.0333 | 0 | 2018-02-25 20:00 | 20 | 1 | 86.5888 | 18.0875 | 0 | 2018-02-25 20:00 | 20 | 1 | 0 | 0 | 0 | 2018-02-25 20:00 | 20 | 1 | 32.9037 | 6.8733 | 0
2018-02-25 21:00 | 21 | 1 | 86.3569 | 18.0391 | 0 | 2018-02-25 21:00 | 21 | 1 | 86.6728 | 18.1051 | 0 | 2018-02-25 21:00 | 21 | 1 | 0 | 0 | 0 | 2018-02-25 21:00 | 21 | 1 | 32.9357 | 6.8799 | 0
2018-02-25 22:00 | 22 | 1 | 86.4881 | 18.0665 | 0 | 2018-02-25 22:00 | 22 | 1 | 86.8086 | 18.1334 | 0 | 2018-02-25 22:00 | 22 | 1 | 0 | 0 | 0 | 2018-02-25 22:00 | 22 | 1 | 32.9873 | 6.8907 | 0
2018-02-25 23:00 | 23 | 1 | 86.4332 | 18.055 | 0 | 2018-02-25 23:00 | 23 | 1 | 86.7353 | 18.1181 | 0 | 2018-02-25 23:00 | 23 | 1 | 0 | 0 | 0 | 2018-02-25 23:00 | 23 | 1 | 32.9594 | 6.8849 | 0
2018-02-26 | 0 | 2 | 86.4088 | 18.0499 | 0 | 2018-02-26 | 0 | 2 | 86.7002 | 18.1108 | 0 | 2018-02-26 | 0 | 2 | 86.9352 | 18.1599 | 0 | 2018-02-26 | 0 | 2 | 65.9815 | 13.7829 | 0
2018-02-26 01:00 | 1 | 2 | 86.0426 | 17.9734 | 0 | 2018-02-26 01:00 | 1 | 2 | 86.3127 | 18.0299 | 0 | 2018-02-26 01:00 | 1 | 2 | 86.5278 | 18.0748 | 0 | 2018-02-26 01:00 | 1 | 2 | 65.6794 | 13.7198 | 0
2018-02-26 02:00 | 2 | 2 | 86.392 | 18.0464 | 0 | 2018-02-26 02:00 | 2 | 2 | 86.6392 | 18.0981 | 0 | 2018-02-26 02:00 | 2 | 2 | 86.8421 | 18.1404 | 0 | 2018-02-26 02:00 | 2 | 2 | 65.9229 | 13.7706 | 0
2018-02-26 03:00 | 3 | 2 | 86.2776 | 18.0225 | 0 | 2018-02-26 03:00 | 3 | 2 | 86.5766 | 18.085 | 0 | 2018-02-26 03:00 | 3 | 2 | 86.7536 | 18.122 | 0 | 2018-02-26 03:00 | 3 | 2 | 65.8655 | 13.7586 | 0
2018-02-26 04:00 | 4 | 2 | 86.5034 | 18.0697 | 0 | 2018-02-26 04:00 | 4 | 2 | 86.8849 | 18.1494 | 0 | 2018-02-26 04:00 | 4 | 2 | 87.0283 | 18.1793 | 0 | 2018-02-26 04:00 | 4 | 2 | 66.087 | 13.8049 | 0
2018-02-26 05:00 | 5 | 2 | 86.3661 | 18.041 | 0 | 2018-02-26 05:00 | 5 | 2 | 86.772 | 18.1258 | 0 | 2018-02-26 05:00 | 5 | 2 | 87.0054 | 18.1746 | 0 | 2018-02-26 05:00 | 5 | 2 | 66.0354 | 13.7941 | 0
2018-02-26 06:00 | 6 | 2 | 86.2898 | 18.0251 | 0 | 2018-02-26 06:00 | 6 | 2 | 86.6499 | 18.1003 | 0 | 2018-02-26 06:00 | 6 | 2 | 86.8147 | 18.1347 | 0 | 2018-02-26 06:00 | 6 | 2 | 65.9165 | 13.7693 | 0
2018-02-26 07:00 | 7 | 2 | 86.2043 | 18.0072 | 0 | 2018-02-26 07:00 | 7 | 2 | 86.5278 | 18.0748 | 0 | 2018-02-26 07:00 | 7 | 2 | 86.7079 | 18.1124 | 0 | 2018-02-26 07:00 | 7 | 2 | 65.8296 | 13.7511 | 0
2018-02-26 08:00 | 8 | 2 | 86.3355 | 18.0346 | 0 | 2018-02-26 08:00 | 8 | 2 | 86.5461 | 18.0786 | 0 | 2018-02-26 08:00 | 8 | 2 | 86.8025 | 18.1322 | 0 | 2018-02-26 08:00 | 8 | 2 | 65.8725 | 13.7601 | 0
2018-02-26 09:00 | 9 | 2 | 86.3798 | 18.0439 | 0 | 2018-02-26 09:00 | 9 | 2 | 86.7262 | 18.1162 | 0 | 2018-02-26 09:00 | 9 | 2 | 86.8711 | 18.1465 | 0 | 2018-02-26 09:00 | 9 | 2 | 65.967 | 13.7798 | 0
2018-02-26 10:00 | 10 | 2 | 86.2272 | 18.012 | 0 | 2018-02-26 10:00 | 10 | 2 | 86.5156 | 18.0722 | 0 | 2018-02-26 10:00 | 10 | 2 | 86.714 | 18.1137 | 0 | 2018-02-26 10:00 | 10 | 2 | 65.8272 | 13.7507 | 0
2018-02-26 11:00 | 11 | 2 | 86.2119 | 18.0088 | 0 | 2018-02-26 11:00 | 11 | 2 | 86.5141 | 18.0719 | 0 | 2018-02-26 11:00 | 11 | 2 | 86.7201 | 18.115 | 0 | 2018-02-26 11:00 | 11 | 2 | 65.829 | 13.751 | 0
2018-02-26 12:00 | 12 | 2 | 86.389 | 18.0458 | 0 | 2018-02-26 12:00 | 12 | 2 | 86.6835 | 18.1073 | 0 | 2018-02-26 12:00 | 12 | 2 | 86.8574 | 18.1436 | 0 | 2018-02-26 12:00 | 12 | 2 | 65.9455 | 13.7754 | 0
2018-02-26 13:00 | 13 | 2 | 86.4027 | 18.0487 | 0 | 2018-02-26 13:00 | 13 | 2 | 86.6224 | 18.0946 | 0 | 2018-02-26 13:00 | 13 | 2 | 86.7475 | 18.1207 | 0 | 2018-02-26 13:00 | 13 | 2 | 65.8806 | 13.7618 | 0
2018-02-26 14:00 | 14 | 2 | 86.3783 | 18.0436 | 0 | 2018-02-26 14:00 | 14 | 2 | 86.6606 | 18.1025 | 0 | 2018-02-26 14:00 | 14 | 2 | 86.7903 | 18.1296 | 0 | 2018-02-26 14:00 | 14 | 2 | 65.9113 | 13.7682 | 0
2018-02-26 15:00 | 15 | 2 | 86.3355 | 18.0346 | 0 | 2018-02-26 15:00 | 15 | 2 | 86.5248 | 18.0742 | 0 | 2018-02-26 15:00 | 15 | 2 | 86.7384 | 18.1188 | 0 | 2018-02-26 15:00 | 15 | 2 | 65.84 | 13.7533 | 0
2018-02-26 16:00 | 16 | 2 | 86.3493 | 18.0375 | 0 | 2018-02-26 16:00 | 16 | 2 | 86.4912 | 18.0671 | 0 | 2018-02-26 16:00 | 16 | 2 | 86.685 | 18.1076 | 0 | 2018-02-26 16:00 | 16 | 2 | 65.807 | 13.7464 | 0
2018-02-26 17:00 | 17 | 2 | 86.244 | 18.0155 | 0 | 2018-02-26 17:00 | 17 | 2 | 86.4683 | 18.0624 | 0 | 2018-02-26 17:00 | 17 | 2 | 86.6743 | 18.1054 | 0 | 2018-02-26 17:00 | 17 | 2 | 65.7942 | 13.7437 | 0
2018-02-26 18:00 | 18 | 2 | 86.3142 | 18.0302 | 0 | 2018-02-26 18:00 | 18 | 2 | 86.4378 | 18.056 | 0 | 2018-02-26 18:00 | 18 | 2 | 86.5934 | 18.0885 | 0 | 2018-02-26 18:00 | 18 | 2 | 65.7519 | 13.7349 | 0
2018-02-26 19:00 | 19 | 2 | 86.2089 | 18.0082 | 0 | 2018-02-26 19:00 | 19 | 2 | 86.3508 | 18.0378 | 0 | 2018-02-26 19:00 | 19 | 2 | 86.5583 | 18.0812 | 0 | 2018-02-26 19:00 | 19 | 2 | 65.7055 | 13.7252 | 0
2018-02-26 20:00 | 20 | 2 | 86.2181 | 18.0101 | 0 | 2018-02-26 20:00 | 20 | 2 | 86.4836 | 18.0656 | 0 | 2018-02-26 20:00 | 20 | 2 | 86.6896 | 18.1086 | 0 | 2018-02-26 20:00 | 20 | 2 | 65.8058 | 13.7462 | 0
2018-02-26 21:00 | 21 | 2 | 86.1494 | 17.9957 | 0 | 2018-02-26 21:00 | 21 | 2 | 86.4759 | 18.064 | 0 | 2018-02-26 21:00 | 21 | 2 | 86.63 | 18.0961 | 0 | 2018-02-26 21:00 | 21 | 2 | 65.7802 | 13.7408 | 0
2018-02-26 22:00 | 22 | 2 | 86.2593 | 18.0187 | 0 | 2018-02-26 22:00 | 22 | 2 | 86.5522 | 18.0799 | 0 | 2018-02-26 22:00 | 22 | 2 | 86.6468 | 18.0997 | 0 | 2018-02-26 22:00 | 22 | 2 | 65.8156 | 13.7482 | 0
2018-02-26 23:00 | 23 | 2 | 86.4424 | 18.057 | 0 | 2018-02-26 23:00 | 23 | 2 | 86.8055 | 18.1328 | 0 | 2018-02-26 23:00 | 23 | 2 | 86.8864 | 18.1497 | 0 | 2018-02-26 23:00 | 23 | 2 | 66.0029 | 13.7874 | 0
2018-02-27 | 0 | 3 | 86.4637 | 18.0614 | 0 | 2018-02-27 | 0 | 3 | 0 | 0 | 0 | 2018-02-27 | 0 | 3 | 0 | 0 | 0 | 2018-02-27 | 0 | 3 | 0 | 0 | 0
2018-02-27 01:00 | 1 | 3 | 86.5629 | 18.0821 | 0 | 2018-02-27 01:00 | 1 | 3 | 0 | 0 | 0 | 2018-02-27 01:00 | 1 | 3 | 0 | 0 | 0 | 2018-02-27 01:00 | 1 | 3 | 0 | 0 | 0
2018-02-27 02:00 | 2 | 3 | 86.3706 | 18.042 | 0 | 2018-02-27 02:00 | 2 | 3 | 0 | 0 | 0 | 2018-02-27 02:00 | 2 | 3 | 0 | 0 | 0 | 2018-02-27 02:00 | 2 | 3 | 0 | 0 | 0
2018-02-27 03:00 | 3 | 3 | 86.3523 | 18.0381 | 0 | 2018-02-27 03:00 | 3 | 3 | 0 | 0 | 0 | 2018-02-27 03:00 | 3 | 3 | 0 | 0 | 0 | 2018-02-27 03:00 | 3 | 3 | 0 | 0 | 0
2018-02-27 04:00 | 4 | 3 | 86.3676 | 18.0413 | 0 | 2018-02-27 04:00 | 4 | 3 | 0 | 0 | 0 | 2018-02-27 04:00 | 4 | 3 | 0 | 0 | 0 | 2018-02-27 04:00 | 4 | 3 | 0 | 0 | 0
2018-02-27 05:00 | 5 | 3 | 86.4027 | 18.0487 | 0 | 2018-02-27 05:00 | 5 | 3 | 0 | 0 | 0 | 2018-02-27 05:00 | 5 | 3 | 0 | 0 | 0 | 2018-02-27 05:00 | 5 | 3 | 0 | 0 | 0
2018-02-27 06:00 | 6 | 3 | 86.4652 | 18.0617 | 0 | 2018-02-27 06:00 | 6 | 3 | 0 | 0 | 0 | 2018-02-27 06:00 | 6 | 3 | 0 | 0 | 0 | 2018-02-27 06:00 | 6 | 3 | 0 | 0 | 0
2018-02-27 07:00 | 7 | 3 | 86.4012 | 18.0483 | 0 | 2018-02-27 07:00 | 7 | 3 | 0 | 0 | 0 | 2018-02-27 07:00 | 7 | 3 | 0 | 0 | 0 | 2018-02-27 07:00 | 7 | 3 | 0 | 0 | 0
2018-02-27 08:00 | 8 | 3 | 86.4515 | 18.0589 | 0 | 2018-02-27 08:00 | 8 | 3 | 0 | 0 | 0 | 2018-02-27 08:00 | 8 | 3 | 0 | 0 | 0 | 2018-02-27 08:00 | 8 | 3 | 0 | 0 | 0
2018-02-27 09:00 | 9 | 3 | 86.2028 | 18.0069 | 0 | 2018-02-27 09:00 | 9 | 3 | 0 | 0 | 0 | 2018-02-27 09:00 | 9 | 3 | 0 | 0 | 0 | 2018-02-27 09:00 | 9 | 3 | 0 | 0 | 0
2018-02-27 10:00 | 10 | 3 | 86.2715 | 18.0213 | 0 | 2018-02-27 10:00 | 10 | 3 | 0 | 0 | 0 | 2018-02-27 10:00 | 10 | 3 | 0 | 0 | 0 | 2018-02-27 10:00 | 10 | 3 | 0 | 0 | 0
2018-02-27 11:00 | 11 | 3 | 86.7567 | 18.1226 | 0 | 2018-02-27 11:00 | 11 | 3 | 0 | 0 | 0 | 2018-02-27 11:00 | 11 | 3 | 0 | 0 | 0 | 2018-02-27 11:00 | 11 | 3 | 0 | 0 | 0
2018-02-27 12:00 | 12 | 3 | 86.6194 | 18.0939 | 0 | 2018-02-27 12:00 | 12 | 3 | 0 | 0 | 0 | 2018-02-27 12:00 | 12 | 3 | 0 | 0 | 0 | 2018-02-27 12:00 | 12 | 3 | 0 | 0 | 0
2018-02-27 13:00 | 13 | 3 | 86.6377 | 18.0977 | 0 | 2018-02-27 13:00 | 13 | 3 | 0 | 0 | 0 | 2018-02-27 13:00 | 13 | 3 | 0 | 0 | 0 | 2018-02-27 13:00 | 13 | 3 | 0 | 0 | 0
2018-02-27 14:00 | 14 | 3 | 86.8757 | 18.1475 | 0 | 2018-02-27 14:00 | 14 | 3 | 0 | 0 | 0 | 2018-02-27 14:00 | 14 | 3 | 0 | 0 | 0 | 2018-02-27 14:00 | 14 | 3 | 0 | 0 | 0
2018-02-27 15:00 | 15 | 3 | 86.7994 | 18.1315 | 0 | 2018-02-27 15:00 | 15 | 3 | 0 | 0 | 0 | 2018-02-27 15:00 | 15 | 3 | 0 | 0 | 0 | 2018-02-27 15:00 | 15 | 3 | 0 | 0 | 0
2018-02-27 16:00 | 16 | 3 | 86.7674 | 18.1248 | 0 | 2018-02-27 16:00 | 16 | 3 | 0 | 0 | 0 | 2018-02-27 16:00 | 16 | 3 | 0 | 0 | 0 | 2018-02-27 16:00 | 16 | 3 | 0 | 0 | 0
2018-02-27 17:00 | 17 | 3 | 86.7384 | 18.1188 | 0 | 2018-02-27 17:00 | 17 | 3 | 0 | 0 | 0 | 2018-02-27 17:00 | 17 | 3 | 0 | 0 | 0 | 2018-02-27 17:00 | 17 | 3 | 0 | 0 | 0
2018-02-27 18:00 | 18 | 3 | 86.7124 | 18.1134 | 0 | 2018-02-27 18:00 | 18 | 3 | 0 | 0 | 0 | 2018-02-27 18:00 | 18 | 3 | 0 | 0 | 0 | 2018-02-27 18:00 | 18 | 3 | 0 | 0 | 0
2018-02-27 19:00 | 19 | 3 | 86.8376 | 18.1395 | 0 | 2018-02-27 19:00 | 19 | 3 | 0 | 0 | 0 | 2018-02-27 19:00 | 19 | 3 | 0 | 0 | 0 | 2018-02-27 19:00 | 19 | 3 | 0 | 0 | 0
2018-02-27 20:00 | 20 | 3 | 86.627 | 18.0955 | 0 | 2018-02-27 20:00 | 20 | 3 | 0 | 0 | 0 | 2018-02-27 20:00 | 20 | 3 | 0 | 0 | 0 | 2018-02-27 20:00 | 20 | 3 | 0 | 0 | 0
2018-02-27 21:00 | 21 | 3 | 86.6239 | 18.0949 | 0 | 2018-02-27 21:00 | 21 | 3 | 0 | 0 | 0 | 2018-02-27 21:00 | 21 | 3 | 0 | 0 | 0 | 2018-02-27 21:00 | 21 | 3 | 0 | 0 | 0
2018-02-27 22:00 | 22 | 3 | 86.714 | 18.1137 | 0 | 2018-02-27 22:00 | 22 | 3 | 0 | 0 | 0 | 2018-02-27 22:00 | 22 | 3 | 0 | 0 | 0 | 2018-02-27 22:00 | 22 | 3 | 0 | 0 | 0
2018-02-27 23:00 | 23 | 3 | 86.8971 | 18.1519 | 0 | 2018-02-27 23:00 | 23 | 3 | 0 | 0 | 0 | 2018-02-27 23:00 | 23 | 3 | 0 | 0 | 0 | 2018-02-27 23:00 | 23 | 3 | 0 | 0 | 0
2018-02-28 | 0 | 4 | 0 | 0 | 0 | 2018-02-28 | 0 | 4 | 0 | 0 | 0 | 2018-02-28 | 0 | 4 | 86.6712 | 18.1047 | 0 | 2018-02-28 | 0 | 4 | 32.9351 | 6.8798 | 0
2018-02-28 01:00 | 1 | 4 | 0 | 0 | 0 | 2018-02-28 01:00 | 1 | 4 | 0 | 0 | 0 | 2018-02-28 01:00 | 1 | 4 | 86.511 | 18.0713 | 0 | 2018-02-28 01:00 | 1 | 4 | 32.8742 | 6.8671 | 0
2018-02-28 02:00 | 2 | 4 | 0 | 0 | 0 | 2018-02-28 02:00 | 2 | 4 | 0 | 0 | 0 | 2018-02-28 02:00 | 2 | 4 | 86.7628 | 18.1239 | 0 | 2018-02-28 02:00 | 2 | 4 | 32.9699 | 6.8871 | 0
2018-02-28 03:00 | 3 | 4 | 0 | 0 | 0 | 2018-02-28 03:00 | 3 | 4 | 0 | 0 | 0 | 2018-02-28 03:00 | 3 | 4 | 86.7384 | 18.1188 | 0 | 2018-02-28 03:00 | 3 | 4 | 32.9606 | 6.8851 | 0
2018-02-28 04:00 | 4 | 4 | 0 | 0 | 0 | 2018-02-28 04:00 | 4 | 4 | 0 | 0 | 0 | 2018-02-28 04:00 | 4 | 4 | 86.8376 | 18.1395 | 0 | 2018-02-28 04:00 | 4 | 4 | 32.9983 | 6.893 | 0
2018-02-28 05:00 | 5 | 4 | 0 | 0 | 0 | 2018-02-28 05:00 | 5 | 4 | 0 | 0 | 0 | 2018-02-28 05:00 | 5 | 4 | 87.0222 | 18.1781 | 0 | 2018-02-28 05:00 | 5 | 4 | 33.0684 | 6.9077 | 0
2018-02-28 06:00 | 6 | 4 | 0 | 0 | 0 | 2018-02-28 06:00 | 6 | 4 | 0 | 0 | 0 | 2018-02-28 06:00 | 6 | 4 | 86.9627 | 18.1656 | 0 | 2018-02-28 06:00 | 6 | 4 | 33.0458 | 6.9029 | 0
2018-02-28 07:00 | 7 | 4 | 0 | 0 | 0 | 2018-02-28 07:00 | 7 | 4 | 0 | 0 | 0 | 2018-02-28 07:00 | 7 | 4 | 87.1321 | 18.201 | 0 | 2018-02-28 07:00 | 7 | 4 | 33.1102 | 6.9164 | 0
2018-02-28 08:00 | 8 | 4 | 0 | 0 | 0 | 2018-02-28 08:00 | 8 | 4 | 0 | 0 | 0 | 2018-02-28 08:00 | 8 | 4 | 87.1931 | 18.2138 | 0 | 2018-02-28 08:00 | 8 | 4 | 33.1334 | 6.9212 | 0
2018-02-28 09:00 | 9 | 4 | 0 | 0 | 0 | 2018-02-28 09:00 | 9 | 4 | 0 | 0 | 0 | 2018-02-28 09:00 | 9 | 4 | 86.7155 | 18.114 | 0 | 2018-02-28 09:00 | 9 | 4 | 32.9519 | 6.8833 | 0
2018-02-28 10:00 | 10 | 4 | 0 | 0 | 0 | 2018-02-28 10:00 | 10 | 4 | 0 | 0 | 0 | 2018-02-28 10:00 | 10 | 4 | 86.6743 | 18.1054 | 0 | 2018-02-28 10:00 | 10 | 4 | 32.9362 | 6.88 | 0
2018-02-28 11:00 | 11 | 4 | 0 | 0 | 0 | 2018-02-28 11:00 | 11 | 4 | 0 | 0 | 0 | 2018-02-28 11:00 | 11 | 4 | 86.8956 | 18.1516 | 0 | 2018-02-28 11:00 | 11 | 4 | 33.0203 | 6.8976 | 0
2018-02-28 12:00 | 12 | 4 | 0 | 0 | 0 | 2018-02-28 12:00 | 12 | 4 | 0 | 0 | 0 | 2018-02-28 12:00 | 12 | 4 | 86.9276 | 18.1583 | 0 | 2018-02-28 12:00 | 12 | 4 | 33.0325 | 6.9002 | 0
2018-02-28 13:00 | 13 | 4 | 0 | 0 | 0 | 2018-02-28 13:00 | 13 | 4 | 0 | 0 | 0 | 2018-02-28 13:00 | 13 | 4 | 87.2541 | 18.2265 | 0 | 2018-02-28 13:00 | 13 | 4 | 33.1566 | 6.9261 | 0
2018-02-28 14:00 | 14 | 4 | 0 | 0 | 0 | 2018-02-28 14:00 | 14 | 4 | 0 | 0 | 0 | 2018-02-28 14:00 | 14 | 4 | 87.4037 | 18.2578 | 0 | 2018-02-28 14:00 | 14 | 4 | 33.2134 | 6.9379 | 0
2018-02-28 15:00 | 15 | 4 | 0 | 0 | 0 | 2018-02-28 15:00 | 15 | 4 | 0 | 0 | 0 | 2018-02-28 15:00 | 15 | 4 | 87.2129 | 18.2179 | 0 | 2018-02-28 15:00 | 15 | 4 | 33.1409 | 6.9228 | 0
2018-02-28 16:00 | 16 | 4 | 0 | 0 | 0 | 2018-02-28 16:00 | 16 | 4 | 0 | 0 | 0 | 2018-02-28 16:00 | 16 | 4 | 86.9718 | 18.1675 | 0 | 2018-02-28 16:00 | 16 | 4 | 33.0493 | 6.9037 | 0
2018-02-28 17:00 | 17 | 4 | 0 | 0 | 0 | 2018-02-28 17:00 | 17 | 4 | 0 | 0 | 0 | 2018-02-28 17:00 | 17 | 4 | 87.1397 | 18.2026 | 0 | 2018-02-28 17:00 | 17 | 4 | 33.1131 | 6.917 | 0
2018-02-28 18:00 | 18 | 4 | 0 | 0 | 0 | 2018-02-28 18:00 | 18 | 4 | 0 | 0 | 0 | 2018-02-28 18:00 | 18 | 4 | 87.2435 | 18.2243 | 0 | 2018-02-28 18:00 | 18 | 4 | 33.1525 | 6.9252 | 0
2018-02-28 19:00 | 19 | 4 | 0 | 0 | 0 | 2018-02-28 19:00 | 19 | 4 | 0 | 0 | 0 | 2018-02-28 19:00 | 19 | 4 | 86.8894 | 18.1503 | 0 | 2018-02-28 19:00 | 19 | 4 | 33.018 | 6.8971 | 0
2018-02-28 20:00 | 20 | 4 | 0 | 0 | 0 | 2018-02-28 20:00 | 20 | 4 | 0 | 0 | 0 | 2018-02-28 20:00 | 20 | 4 | 87.1839 | 18.2118 | 0 | 2018-02-28 20:00 | 20 | 4 | 33.1299 | 6.9205 | 0
2018-02-28 21:00 | 21 | 4 | 0 | 0 | 0 | 2018-02-28 21:00 | 21 | 4 | 0 | 0 | 0 | 2018-02-28 21:00 | 21 | 4 | 87.2419 | 18.224 | 0 | 2018-02-28 21:00 | 21 | 4 | 33.1519 | 6.9251 | 0
2018-02-28 22:00 | 22 | 4 | 0 | 0 | 0 | 2018-02-28 22:00 | 22 | 4 | 0 | 0 | 0 | 2018-02-28 22:00 | 22 | 4 | 87.1733 | 18.2096 | 0 | 2018-02-28 22:00 | 22 | 4 | 33.1259 | 6.9197 | 0
2018-02-28 23:00 | 23 | 4 | 0 | 0 | 0 | 2018-02-28 23:00 | 23 | 4 | 0 | 0 | 0 | 2018-02-28 23:00 | 23 | 4 | 87.2557 | 18.2268 | 0 | 2018-02-28 23:00 | 23 | 4 | 33.1572 | 6.9262 | 0
2018-03-01 | 0 | 5 | 86.5492 | 18.0793 | 0 | 2018-03-01 | 0 | 5 | 0 | 0 | 0 | 2018-03-01 | 0 | 5 | 0 | 0 | 0 | 2018-03-01 | 0 | 5 | 0 | 0 | 0
2018-03-01 01:00 | 1 | 5 | 86.7201 | 18.115 | 0 | 2018-03-01 01:00 | 1 | 5 | 0 | 0 | 0 | 2018-03-01 01:00 | 1 | 5 | 0 | 0 | 0 | 2018-03-01 01:00 | 1 | 5 | 0 | 0 | 0
2018-03-01 02:00 | 2 | 5 | 86.5095 | 18.071 | 0 | 2018-03-01 02:00 | 2 | 5 | 0 | 0 | 0 | 2018-03-01 02:00 | 2 | 5 | 0 | 0 | 0 | 2018-03-01 02:00 | 2 | 5 | 0 | 0 | 0
2018-03-01 03:00 | 3 | 5 | 86.4576 | 18.0601 | 0 | 2018-03-01 03:00 | 3 | 5 | 0 | 0 | 0 | 2018-03-01 03:00 | 3 | 5 | 0 | 0 | 0 | 2018-03-01 03:00 | 3 | 5 | 0 | 0 | 0
2018-03-01 04:00 | 4 | 5 | 86.6316 | 18.0965 | 0 | 2018-03-01 04:00 | 4 | 5 | 0 | 0 | 0 | 2018-03-01 04:00 | 4 | 5 | 0 | 0 | 0 | 2018-03-01 04:00 | 4 | 5 | 0 | 0 | 0
2018-03-01 05:00 | 5 | 5 | 86.569 | 18.0834 | 0 | 2018-03-01 05:00 | 5 | 5 | 0 | 0 | 0 | 2018-03-01 05:00 | 5 | 5 | 0 | 0 | 0 | 2018-03-01 05:00 | 5 | 5 | 0 | 0 | 0
2018-03-01 06:00 | 6 | 5 | 86.6468 | 18.0997 | 0 | 2018-03-01 06:00 | 6 | 5 | 0 | 0 | 0 | 2018-03-01 06:00 | 6 | 5 | 0 | 0 | 0 | 2018-03-01 06:00 | 6 | 5 | 0 | 0 | 0
2018-03-01 07:00 | 7 | 5 | 86.6361 | 18.0974 | 0 | 2018-03-01 07:00 | 7 | 5 | 0 | 0 | 0 | 2018-03-01 07:00 | 7 | 5 | 0 | 0 | 0 | 2018-03-01 07:00 | 7 | 5 | 0 | 0 | 0
2018-03-01 08:00 | 8 | 5 | 86.6819 | 18.107 | 0 | 2018-03-01 08:00 | 8 | 5 | 0 | 0 | 0 | 2018-03-01 08:00 | 8 | 5 | 0 | 0 | 0 | 2018-03-01 08:00 | 8 | 5 | 0 | 0 | 0
2018-03-01 09:00 | 9 | 5 | 86.7094 | 18.1127 | 0 | 2018-03-01 09:00 | 9 | 5 | 0 | 0 | 0 | 2018-03-01 09:00 | 9 | 5 | 0 | 0 | 0 | 2018-03-01 09:00 | 9 | 5 | 0 | 0 | 0
2018-03-01 10:00 | 10 | 5 | 86.7933 | 18.1303 | 0 | 2018-03-01 10:00 | 10 | 5 | 0 | 0 | 0 | 2018-03-01 10:00 | 10 | 5 | 0 | 0 | 0 | 2018-03-01 10:00 | 10 | 5 | 0 | 0 | 0
2018-03-01 11:00 | 11 | 5 | 86.8009 | 18.1318 | 0 | 2018-03-01 11:00 | 11 | 5 | 0 | 0 | 0 | 2018-03-01 11:00 | 11 | 5 | 0 | 0 | 0 | 2018-03-01 11:00 | 11 | 5 | 0 | 0 | 0
2018-03-01 12:00 | 12 | 5 | 86.6728 | 18.1051 | 0 | 2018-03-01 12:00 | 12 | 5 | 0 | 0 | 0 | 2018-03-01 12:00 | 12 | 5 | 0 | 0 | 0 | 2018-03-01 12:00 | 12 | 5 | 0 | 0 | 0
2018-03-01 13:00 | 13 | 5 | 86.6316 | 18.0965 | 0 | 2018-03-01 13:00 | 13 | 5 | 0 | 0 | 0 | 2018-03-01 13:00 | 13 | 5 | 0 | 0 | 0 | 2018-03-01 13:00 | 13 | 5 | 0 | 0 | 0
2018-03-01 14:00 | 14 | 5 | 86.6316 | 18.0965 | 0 | 2018-03-01 14:00 | 14 | 5 | 0 | 0 | 0 | 2018-03-01 14:00 | 14 | 5 | 0 | 0 | 0 | 2018-03-01 14:00 | 14 | 5 | 0 | 0 | 0
2018-03-01 15:00 | 15 | 5 | 86.6636 | 18.1032 | 0 | 2018-03-01 15:00 | 15 | 5 | 0 | 0 | 0 | 2018-03-01 15:00 | 15 | 5 | 0 | 0 | 0 | 2018-03-01 15:00 | 15 | 5 | 0 | 0 | 0
2018-03-01 16:00 | 16 | 5 | 86.5568 | 18.0808 | 0 | 2018-03-01 16:00 | 16 | 5 | 0 | 0 | 0 | 2018-03-01 16:00 | 16 | 5 | 0 | 0 | 0 | 2018-03-01 16:00 | 16 | 5 | 0 | 0 | 0
2018-03-01 17:00 | 17 | 5 | 86.6865 | 18.1079 | 0 | 2018-03-01 17:00 | 17 | 5 | 0 | 0 | 0 | 2018-03-01 17:00 | 17 | 5 | 0 | 0 | 0 | 2018-03-01 17:00 | 17 | 5 | 0 | 0 | 0
2018-03-01 18:00 | 18 | 5 | 86.7262 | 18.1162 | 0 | 2018-03-01 18:00 | 18 | 5 | 0 | 0 | 0 | 2018-03-01 18:00 | 18 | 5 | 0 | 0 | 0 | 2018-03-01 18:00 | 18 | 5 | 0 | 0 | 0
2018-03-01 19:00 | 19 | 5 | 86.5187 | 18.0729 | 0 | 2018-03-01 19:00 | 19 | 5 | 0 | 0 | 0 | 2018-03-01 19:00 | 19 | 5 | 0 | 0 | 0 | 2018-03-01 19:00 | 19 | 5 | 0 | 0 | 0
2018-03-01 20:00 | 20 | 5 | 86.5766 | 18.085 | 0 | 2018-03-01 20:00 | 20 | 5 | 0 | 0 | 0 | 2018-03-01 20:00 | 20 | 5 | 0 | 0 | 0 | 2018-03-01 20:00 | 20 | 5 | 0 | 0 | 0
2018-03-01 21:00 | 21 | 5 | 86.6194 | 18.0939 | 0 | 2018-03-01 21:00 | 21 | 5 | 0 | 0 | 0 | 2018-03-01 21:00 | 21 | 5 | 0 | 0 | 0 | 2018-03-01 21:00 | 21 | 5 | 0 | 0 | 0
2018-03-01 22:00 | 22 | 5 | 86.6743 | 18.1054 | 0 | 2018-03-01 22:00 | 22 | 5 | 0 | 0 | 0 | 2018-03-01 22:00 | 22 | 5 | 0 | 0 | 0 | 2018-03-01 22:00 | 22 | 5 | 0 | 0 | 0
2018-03-01 23:00 | 23 | 5 | 86.5644 | 18.0824 | 0 | 2018-03-01 23:00 | 23 | 5 | 0 | 0 | 0 | 2018-03-01 23:00 | 23 | 5 | 0 | 0 | 0 | 2018-03-01 23:00 | 23 | 5 | 0 | 0 | 0
2018-03-02 | 0 | 6 | 86.2226 | 18.011 | 0 | 2018-03-02 | 0 | 6 | 86.688 | 18.1083 | 0 | 2018-03-02 | 0 | 6 | 0 | 0 | 0 | 2018-03-02 | 0 | 6 | 32.9414 | 6.8811 | 0
2018-03-02 01:00 | 1 | 6 | 86.1128 | 17.9881 | 0 | 2018-03-02 01:00 | 1 | 6 | 86.5232 | 18.0738 | 0 | 2018-03-02 01:00 | 1 | 6 | 0 | 0 | 0 | 2018-03-02 01:00 | 1 | 6 | 32.8788 | 6.8681 | 0
2018-03-02 02:00 | 2 | 6 | 86.2791 | 18.0228 | 0 | 2018-03-02 02:00 | 2 | 6 | 86.6896 | 18.1086 | 0 | 2018-03-02 02:00 | 2 | 6 | 0 | 0 | 0 | 2018-03-02 02:00 | 2 | 6 | 32.942 | 6.8813 | 0
2018-03-02 03:00 | 3 | 6 | 86.0014 | 17.9648 | 0 | 2018-03-02 03:00 | 3 | 6 | 86.4485 | 18.0582 | 0 | 2018-03-02 03:00 | 3 | 6 | 0 | 0 | 0 | 2018-03-02 03:00 | 3 | 6 | 32.8504 | 6.8621 | 0
2018-03-02 04:00 | 4 | 6 | 86.0533 | 17.9757 | 0 | 2018-03-02 04:00 | 4 | 6 | 86.4347 | 18.0553 | 0 | 2018-03-02 04:00 | 4 | 6 | 0 | 0 | 0 | 2018-03-02 04:00 | 4 | 6 | 32.8452 | 6.861 | 0
2018-03-02 05:00 | 5 | 6 | 86.2257 | 18.0117 | 0 | 2018-03-02 05:00 | 5 | 6 | 86.6117 | 18.0923 | 0 | 2018-03-02 05:00 | 5 | 6 | 0 | 0 | 0 | 2018-03-02 05:00 | 5 | 6 | 32.9124 | 6.8751 | 0
2018-03-02 06:00 | 6 | 6 | 86.4332 | 18.055 | 0 | 2018-03-02 06:00 | 6 | 6 | 86.9352 | 18.1599 | 0 | 2018-03-02 06:00 | 6 | 6 | 0 | 0 | 0 | 2018-03-02 06:00 | 6 | 6 | 33.0354 | 6.9008 | 0
2018-03-02 07:00 | 7 | 6 | 86.5873 | 18.0872 | 0 | 2018-03-02 07:00 | 7 | 6 | 87.0619 | 18.1864 | 0 | 2018-03-02 07:00 | 7 | 6 | 0 | 0 | 0 | 2018-03-02 07:00 | 7 | 6 | 33.0835 | 6.9108 | 0
2018-03-02 08:00 | 8 | 6 | 86.3691 | 18.0416 | 0 | 2018-03-02 08:00 | 8 | 6 | 86.7811 | 18.1277 | 0 | 2018-03-02 08:00 | 8 | 6 | 0 | 0 | 0 | 2018-03-02 08:00 | 8 | 6 | 32.9768 | 6.8885 | 0
2018-03-02 09:00 | 9 | 6 | 86.334 | 18.0343 | 0 | 2018-03-02 09:00 | 9 | 6 | 86.7399 | 18.1191 | 0 | 2018-03-02 09:00 | 9 | 6 | 0 | 0 | 0 | 2018-03-02 09:00 | 9 | 6 | 32.9612 | 6.8853 | 0
2018-03-02 10:00 | 10 | 6 | 86.5126 | 18.0716 | 0 | 2018-03-02 10:00 | 10 | 6 | 86.862 | 18.1446 | 0 | 2018-03-02 10:00 | 10 | 6 | 0 | 0 | 0 | 2018-03-02 10:00 | 10 | 6 | 33.0076 | 6.8949 | 0
2018-03-02 11:00 | 11 | 6 | 86.5003 | 18.069 | 0 | 2018-03-02 11:00 | 11 | 6 | 86.9306 | 18.1589 | 0 | 2018-03-02 11:00 | 11 | 6 | 0 | 0 | 0 | 2018-03-02 11:00 | 11 | 6 | 33.0336 | 6.9004 | 0
2018-03-02 12:00 | 12 | 6 | 86.7002 | 18.1108 | 0 | 2018-03-02 12:00 | 12 | 6 | 87.1412 | 18.2029 | 0 | 2018-03-02 12:00 | 12 | 6 | 0 | 0 | 0 | 2018-03-02 12:00 | 12 | 6 | 33.1137 | 6.9171 | 0
2018-03-02 13:00 | 13 | 6 | 86.363 | 18.0404 | 0 | 2018-03-02 13:00 | 13 | 6 | 86.8009 | 18.1318 | 0 | 2018-03-02 13:00 | 13 | 6 | 0 | 0 | 0 | 2018-03-02 13:00 | 13 | 6 | 32.9843 | 6.8901 | 0
2018-03-02 14:00 | 14 | 6 | 86.4408 | 18.0566 | 0 | 2018-03-02 14:00 | 14 | 6 | 86.8635 | 18.1449 | 0 | 2018-03-02 14:00 | 14 | 6 | 0 | 0 | 0 | 2018-03-02 14:00 | 14 | 6 | 33.0081 | 6.8951 | 0
2018-03-02 15:00 | 15 | 6 | 86.2943 | 18.026 | 0 | 2018-03-02 15:00 | 15 | 6 | 86.6743 | 18.1054 | 0 | 2018-03-02 15:00 | 15 | 6 | 0 | 0 | 0 | 2018-03-02 15:00 | 15 | 6 | 32.9362 | 6.88 | 0
2018-03-02 16:00 | 16 | 6 | 86.3706 | 18.042 | 0 | 2018-03-02 16:00 | 16 | 6 | 86.7491 | 18.121 | 0 | 2018-03-02 16:00 | 16 | 6 | 0 | 0 | 0 | 2018-03-02 16:00 | 16 | 6 | 32.9647 | 6.886 | 0
2018-03-02 17:00 | 17 | 6 | 86.2882 | 18.0247 | 0 | 2018-03-02 17:00 | 17 | 6 | 86.7445 | 18.1201 | 0 | 2018-03-02 17:00 | 17 | 6 | 0 | 0 | 0 | 2018-03-02 17:00 | 17 | 6 | 32.9629 | 6.8856 | 0
2018-03-02 18:00 | 18 | 6 | 86.1875 | 18.0037 | 0 | 2018-03-02 18:00 | 18 | 6 | 86.6667 | 18.1038 | 0 | 2018-03-02 18:00 | 18 | 6 | 0 | 0 | 0 | 2018-03-02 18:00 | 18 | 6 | 32.9333 | 6.8794 | 0
2018-03-02 19:00 | 19 | 6 | 86.099 | 17.9852 | 0 | 2018-03-02 19:00 | 19 | 6 | 86.5431 | 18.078 | 0 | 2018-03-02 19:00 | 19 | 6 | 0 | 0 | 0 | 2018-03-02 19:00 | 19 | 6 | 32.8864 | 6.8696 | 0
2018-03-02 20:00 | 20 | 6 | 86.1997 | 18.0063 | 0 | 2018-03-02 20:00 | 20 | 6 | 86.5187 | 18.0729 | 0 | 2018-03-02 20:00 | 20 | 6 | 0 | 0 | 0 | 2018-03-02 20:00 | 20 | 6 | 32.8771 | 6.8677 | 0
2018-03-02 21:00 | 21 | 6 | 86.3767 | 18.0432 | 0 | 2018-03-02 21:00 | 21 | 6 | 86.7247 | 18.1159 | 0 | 2018-03-02 21:00 | 21 | 6 | 0 | 0 | 0 | 2018-03-02 21:00 | 21 | 6 | 32.9554 | 6.8841 | 0
2018-03-02 22:00 | 22 | 6 | 86.3691 | 18.0416 | 0 | 2018-03-02 22:00 | 22 | 6 | 86.7659 | 18.1245 | 0 | 2018-03-02 22:00 | 22 | 6 | 0 | 0 | 0 | 2018-03-02 22:00 | 22 | 6 | 32.971 | 6.8873 | 0
2018-03-02 23:00 | 23 | 6 | 86.4012 | 18.0483 | 0 | 2018-03-02 23:00 | 23 | 6 | 86.7918 | 18.1299 | 0 | 2018-03-02 23:00 | 23 | 6 | 0 | 0 | 0 | 2018-03-02 23:00 | 23 | 6 | 32.9809 | 6.8894 | 0
2018-03-03 | 0 | 7 | 86.0121 | 17.9671 | 0 | 2018-03-03 | 0 | 7 | 0 | 0 | 0 | 2018-03-03 | 0 | 7 | 86.5507 | 18.0796 | 0 | 2018-03-03 | 0 | 7 | 32.8893 | 6.8702 | 0
2018-03-03 01:00 | 1 | 7 | 85.919 | 17.9476 | 0 | 2018-03-03 01:00 | 1 | 7 | 0 | 0 | 0 | 2018-03-03 01:00 | 1 | 7 | 86.5324 | 18.0758 | 0 | 2018-03-03 01:00 | 1 | 7 | 32.8823 | 6.8688 | 0
2018-03-03 02:00 | 2 | 7 | 86.0533 | 17.9757 | 0 | 2018-03-03 02:00 | 2 | 7 | 0 | 0 | 0 | 2018-03-03 02:00 | 2 | 7 | 86.6453 | 18.0993 | 0 | 2018-03-03 02:00 | 2 | 7 | 32.9252 | 6.8777 | 0
2018-03-03 03:00 | 3 | 7 | 86.1677 | 17.9996 | 0 | 2018-03-03 03:00 | 3 | 7 | 0 | 0 | 0 | 2018-03-03 03:00 | 3 | 7 | 86.7002 | 18.1108 | 0 | 2018-03-03 03:00 | 3 | 7 | 32.9461 | 6.8821 | 0
2018-03-03 04:00 | 4 | 7 | 86.3081 | 18.0289 | 0 | 2018-03-03 04:00 | 4 | 7 | 0 | 0 | 0 | 2018-03-03 04:00 | 4 | 7 | 86.8513 | 18.1424 | 0 | 2018-03-03 04:00 | 4 | 7 | 33.0035 | 6.8941 | 0
2018-03-03 05:00 | 5 | 7 | 86.2562 | 18.0181 | 0 | 2018-03-03 05:00 | 5 | 7 | 0 | 0 | 0 | 2018-03-03 05:00 | 5 | 7 | 86.8605 | 18.1443 | 0 | 2018-03-03 05:00 | 5 | 7 | 33.007 | 6.8948 | 0
2018-03-03 06:00 | 6 | 7 | 86.1234 | 17.9903 | 0 | 2018-03-03 06:00 | 6 | 7 | 0 | 0 | 0 | 2018-03-03 06:00 | 6 | 7 | 86.6682 | 18.1041 | 0 | 2018-03-03 06:00 | 6 | 7 | 32.9339 | 6.8796 | 0
2018-03-03 07:00 | 7 | 7 | 86.1906 | 18.0044 | 0 | 2018-03-03 07:00 | 7 | 7 | 0 | 0 | 0 | 2018-03-03 07:00 | 7 | 7 | 86.7247 | 18.1159 | 0 | 2018-03-03 07:00 | 7 | 7 | 32.9554 | 6.8841 | 0
2018-03-03 08:00 | 8 | 7 | 86.36 | 18.0397 | 0 | 2018-03-03 08:00 | 8 | 7 | 0 | 0 | 0 | 2018-03-03 08:00 | 8 | 7 | 86.952 | 18.1634 | 0 | 2018-03-03 08:00 | 8 | 7 | 33.0418 | 6.9021 | 0
2018-03-03 09:00 | 9 | 7 | 86.4912 | 18.0671 | 0 | 2018-03-03 09:00 | 9 | 7 | 0 | 0 | 0 | 2018-03-03 09:00 | 9 | 7 | 87.0588 | 18.1857 | 0 | 2018-03-03 09:00 | 9 | 7 | 33.0823 | 6.9106 | 0
2018-03-03 10:00 | 10 | 7 | 86.1982 | 18.0059 | 0 | 2018-03-03 10:00 | 10 | 7 | 0 | 0 | 0 | 2018-03-03 10:00 | 10 | 7 | 86.6392 | 18.0981 | 0 | 2018-03-03 10:00 | 10 | 7 | 32.9229 | 6.8773 | 0
2018-03-03 11:00 | 11 | 7 | 86.1707 | 18.0002 | 0 | 2018-03-03 11:00 | 11 | 7 | 0 | 0 | 0 | 2018-03-03 11:00 | 11 | 7 | 86.8849 | 18.1494 | 0 | 2018-03-03 11:00 | 11 | 7 | 33.0163 | 6.8968 | 0
2018-03-03 12:00 | 12 | 7 | 86.5019 | 18.0694 | 0 | 2018-03-03 12:00 | 12 | 7 | 0 | 0 | 0 | 2018-03-03 12:00 | 12 | 7 | 87.1504 | 18.2048 | 0 | 2018-03-03 12:00 | 12 | 7 | 33.1172 | 6.9178 | 0
2018-03-03 13:00 | 13 | 7 | 86.6148 | 18.093 | 0 | 2018-03-03 13:00 | 13 | 7 | 0 | 0 | 0 | 2018-03-03 13:00 | 13 | 7 | 87.3167 | 18.2396 | 0 | 2018-03-03 13:00 | 13 | 7 | 33.1803 | 6.931 | 0
2018-03-03 14:00 | 14 | 7 | 86.4439 | 18.0573 | 0 | 2018-03-03 14:00 | 14 | 7 | 0 | 0 | 0 | 2018-03-03 14:00 | 14 | 7 | 87.0832 | 18.1908 | 0 | 2018-03-03 14:00 | 14 | 7 | 33.0916 | 6.9125 | 0
2018-03-03 15:00 | 15 | 7 | 86.5522 | 18.0799 | 0 | 2018-03-03 15:00 | 15 | 7 | 0 | 0 | 0 | 2018-03-03 15:00 | 15 | 7 | 87.2938 | 18.2348 | 0 | 2018-03-03 15:00 | 15 | 7 | 33.1716 | 6.9292 | 0
2018-03-03 16:00 | 16 | 7 | 86.5644 | 18.0824 | 0 | 2018-03-03 16:00 | 16 | 7 | 0 | 0 | 0 | 2018-03-03 16:00 | 16 | 7 | 87.3579 | 18.2482 | 0 | 2018-03-03 16:00 | 16 | 7 | 33.196 | 6.9343 | 0
2018-03-03 17:00 | 17 | 7 | 86.7445 | 18.1201 | 0 | 2018-03-03 17:00 | 17 | 7 | 0 | 0 | 0 | 2018-03-03 17:00 | 17 | 7 | 87.57 | 18.2925 | 0 | 2018-03-03 17:00 | 17 | 7 | 33.2766 | 6.9511 | 0
2018-03-03 18:00 | 18 | 7 | 86.4668 | 18.062 | 0 | 2018-03-03 18:00 | 18 | 7 | 0 | 0 | 0 | 2018-03-03 18:00 | 18 | 7 | 87.3014 | 18.2364 | 0 | 2018-03-03 18:00 | 18 | 7 | 33.1745 | 6.9298 | 0
2018-03-03 19:00 | 19 | 7 | 86.3661 | 18.041 | 0 | 2018-03-03 19:00 | 19 | 7 | 0 | 0 | 0 | 2018-03-03 19:00 | 19 | 7 | 87.0954 | 18.1934 | 0 | 2018-03-03 19:00 | 19 | 7 | 33.0963 | 6.9135 | 0
2018-03-03 20:00 | 20 | 7 | 86.1173 | 17.989 | 0 | 2018-03-03 20:00 | 20 | 7 | 0 | 0 | 0 | 2018-03-03 20:00 | 20 | 7 | 86.891 | 18.1507 | 0 | 2018-03-03 20:00 | 20 | 7 | 33.0186 | 6.8973 | 0
2018-03-03 21:00 | 21 | 7 | 86.1555 | 17.997 | 0 | 2018-03-03 21:00 | 21 | 7 | 0 | 0 | 0 | 2018-03-03 21:00 | 21 | 7 | 86.9245 | 18.1577 | 0 | 2018-03-03 21:00 | 21 | 7 | 33.0313 | 6.8999 | 0
2018-03-03 22:00 | 22 | 7 | 86.2211 | 18.0107 | 0 | 2018-03-03 22:00 | 22 | 7 | 0 | 0 | 0 | 2018-03-03 22:00 | 22 | 7 | 87.0054 | 18.1746 | 0 | 2018-03-03 22:00 | 22 | 7 | 33.0621 | 6.9063 | 0
2018-03-03 23:00 | 23 | 7 | 86.2226 | 18.011 | 0 | 2018-03-03 23:00 | 23 | 7 | 0 | 0 | 0 | 2018-03-03 23:00 | 23 | 7 | 87.0787 | 18.1899 | 0 | 2018-03-03 23:00 | 23 | 7 | 33.0899 | 6.9122 | 0
2018-03-04 | 0 | 1 | 86.2364 | 18.0139 | 0 | 2018-03-04 | 0 | 1 | 86.7994 | 18.1315 | 0 | 2018-03-04 | 0 | 1 | 0 | 0 | 0 | 2018-03-04 | 0 | 1 | 32.9838 | 6.89 | 0
2018-03-04 01:00 | 1 | 1 | 86.3188 | 18.0311 | 0 | 2018-03-04 01:00 | 1 | 1 | 86.952 | 18.1634 | 0 | 2018-03-04 01:00 | 1 | 1 | 0 | 0 | 0 | 2018-03-04 01:00 | 1 | 1 | 33.0418 | 6.9021 | 0
2018-03-04 02:00 | 2 | 1 | 86.2119 | 18.0088 | 0 | 2018-03-04 02:00 | 2 | 1 | 86.8177 | 18.1353 | 0 | 2018-03-04 02:00 | 2 | 1 | 0 | 0 | 0 | 2018-03-04 02:00 | 2 | 1 | 32.9907 | 6.8914 | 0
2018-03-04 03:00 | 3 | 1 | 86.1845 | 18.0031 | 0 | 2018-03-04 03:00 | 3 | 1 | 86.7857 | 18.1287 | 0 | 2018-03-04 03:00 | 3 | 1 | 0 | 0 | 0 | 2018-03-04 03:00 | 3 | 1 | 32.9786 | 6.8889 | 0
2018-03-04 04:00 | 4 | 1 | 86.2455 | 18.0158 | 0 | 2018-03-04 04:00 | 4 | 1 | 86.833 | 18.1385 | 0 | 2018-03-04 04:00 | 4 | 1 | 0 | 0 | 0 | 2018-03-04 04:00 | 4 | 1 | 32.9965 | 6.8926 | 0
2018-03-04 05:00 | 5 | 1 | 86.2333 | 18.0133 | 0 | 2018-03-04 05:00 | 5 | 1 | 86.833 | 18.1385 | 0 | 2018-03-04 05:00 | 5 | 1 | 0 | 0 | 0 | 2018-03-04 05:00 | 5 | 1 | 32.9965 | 6.8926 | 0
2018-03-04 06:00 | 6 | 1 | 86.2776 | 18.0225 | 0 | 2018-03-04 06:00 | 6 | 1 | 86.8528 | 18.1427 | 0 | 2018-03-04 06:00 | 6 | 1 | 0 | 0 | 0 | 2018-03-04 06:00 | 6 | 1 | 33.0041 | 6.8942 | 0
2018-03-04 07:00 | 7 | 1 | 86.2867 | 18.0244 | 0 | 2018-03-04 07:00 | 7 | 1 | 86.8452 | 18.1411 | 0 | 2018-03-04 07:00 | 7 | 1 | 0 | 0 | 0 | 2018-03-04 07:00 | 7 | 1 | 33.0012 | 6.8936 | 0
2018-03-04 08:00 | 8 | 1 | 86.2989 | 18.027 | 0 | 2018-03-04 08:00 | 8 | 1 | 86.9032 | 18.1532 | 0 | 2018-03-04 08:00 | 8 | 1 | 0 | 0 | 0 | 2018-03-04 08:00 | 8 | 1 | 33.0232 | 6.8982 | 0
2018-03-04 09:00 | 9 | 1 | 86.2867 | 18.0244 | 0 | 2018-03-04 09:00 | 9 | 1 | 86.8162 | 18.135 | 0 | 2018-03-04 09:00 | 9 | 1 | 0 | 0 | 0 | 2018-03-04 09:00 | 9 | 1 | 32.9902 | 6.8913 | 0
2018-03-04 10:00 | 10 | 1 | 86.2882 | 18.0247 | 0 | 2018-03-04 10:00 | 10 | 1 | 86.8528 | 18.1427 | 0 | 2018-03-04 10:00 | 10 | 1 | 0 | 0 | 0 | 2018-03-04 10:00 | 10 | 1 | 33.0041 | 6.8942 | 0
2018-03-04 11:00 | 11 | 1 | 86.1845 | 18.0031 | 0 | 2018-03-04 11:00 | 11 | 1 | 86.743 | 18.1197 | 0 | 2018-03-04 11:00 | 11 | 1 | 0 | 0 | 0 | 2018-03-04 11:00 | 11 | 1 | 32.9623 | 6.8855 | 0
2018-03-04 12:00 | 12 | 1 | 86.1418 | 17.9942 | 0 | 2018-03-04 12:00 | 12 | 1 | 86.714 | 18.1137 | 0 | 2018-03-04 12:00 | 12 | 1 | 0 | 0 | 0 | 2018-03-04 12:00 | 12 | 1 | 32.9513 | 6.8832 | 0
2018-03-04 13:00 | 13 | 1 | 86.1479 | 17.9954 | 0 | 2018-03-04 13:00 | 13 | 1 | 86.7659 | 18.1245 | 0 | 2018-03-04 13:00 | 13 | 1 | 0 | 0 | 0 | 2018-03-04 13:00 | 13 | 1 | 32.971 | 6.8873 | 0
2018-03-04 14:00 | 14 | 1 | 86.1112 | 17.9878 | 0 | 2018-03-04 14:00 | 14 | 1 | 86.7018 | 18.1111 | 0 | 2018-03-04 14:00 | 14 | 1 | 0 | 0 | 0 | 2018-03-04 14:00 | 14 | 1 | 32.9467 | 6.8822 | 0
2018-03-04 15:00 | 15 | 1 | 86.2455 | 18.0158 | 0 | 2018-03-04 15:00 | 15 | 1 | 86.8482 | 18.1417 | 0 | 2018-03-04 15:00 | 15 | 1 | 0 | 0 | 0 | 2018-03-04 15:00 | 15 | 1 | 33.0023 | 6.8939 | 0
2018-03-04 16:00 | 16 | 1 | 86.3447 | 18.0365 | 0 | 2018-03-04 16:00 | 16 | 1 | 86.9398 | 18.1609 | 0 | 2018-03-04 16:00 | 16 | 1 | 0 | 0 | 0 | 2018-03-04 16:00 | 16 | 1 | 33.0371 | 6.9011 | 0
2018-03-04 17:00 | 17 | 1 | 86.4805 | 18.0649 | 0 | 2018-03-04 17:00 | 17 | 1 | 86.9856 | 18.1704 | 0 | 2018-03-04 17:00 | 17 | 1 | 0 | 0 | 0 | 2018-03-04 17:00 | 17 | 1 | 33.0545 | 6.9048 | 0
2018-03-04 18:00 | 18 | 1 | 86.4332 | 18.055 | 0 | 2018-03-04 18:00 | 18 | 1 | 86.92 | 18.1567 | 0 | 2018-03-04 18:00 | 18 | 1 | 0 | 0 | 0 | 2018-03-04 18:00 | 18 | 1 | 33.0296 | 6.8996 | 0
2018-03-04 19:00 | 19 | 1 | 85.6794 | 17.8976 | 0 | 2018-03-04 19:00 | 19 | 1 | 85.9266 | 17.9492 | 0 | 2018-03-04 19:00 | 19 | 1 | 0 | 0 | 0 | 2018-03-04 19:00 | 19 | 1 | 32.6521 | 6.8207 | 0
2018-03-04 20:00 | 20 | 1 | 86.3294 | 18.0333 | 0 | 2018-03-04 20:00 | 20 | 1 | 86.5888 | 18.0875 | 0 | 2018-03-04 20:00 | 20 | 1 | 0 | 0 | 0 | 2018-03-04 20:00 | 20 | 1 | 32.9037 | 6.8733 | 0
2018-03-04 21:00 | 21 | 1 | 86.3569 | 18.0391 | 0 | 2018-03-04 21:00 | 21 | 1 | 86.6728 | 18.1051 | 0 | 2018-03-04 21:00 | 21 | 1 | 0 | 0 | 0 | 2018-03-04 21:00 | 21 | 1 | 32.9357 | 6.8799 | 0
2018-03-04 22:00 | 22 | 1 | 86.4881 | 18.0665 | 0 | 2018-03-04 22:00 | 22 | 1 | 86.8086 | 18.1334 | 0 | 2018-03-04 22:00 | 22 | 1 | 0 | 0 | 0 | 2018-03-04 22:00 | 22 | 1 | 32.9873 | 6.8907 | 0
2018-03-04 23:00 | 23 | 1 | 86.4332 | 18.055 | 0 | 2018-03-04 23:00 | 23 | 1 | 86.7353 | 18.1181 | 0 | 2018-03-04 23:00 | 23 | 1 | 0 | 0 | 0 | 2018-03-04 23:00 | 23 | 1 | 32.9594 | 6.8849 | 0
2018-03-05 | 0 | 2 | 86.4088 | 18.0499 | 0 | 2018-03-05 | 0 | 2 | 86.7002 | 18.1108 | 0 | 2018-03-05 | 0 | 2 | 86.9352 | 18.1599 | 0 | 2018-03-05 | 0 | 2 | 65.9815 | 13.7829 | 0
2018-03-05 01:00 | 1 | 2 | 86.0426 | 17.9734 | 0 | 2018-03-05 01:00 | 1 | 2 | 86.3127 | 18.0299 | 0 | 2018-03-05 01:00 | 1 | 2 | 86.5278 | 18.0748 | 0 | 2018-03-05 01:00 | 1 | 2 | 65.6794 | 13.7198 | 0
2018-03-05 02:00 | 2 | 2 | 86.392 | 18.0464 | 0 | 2018-03-05 02:00 | 2 | 2 | 86.6392 | 18.0981 | 0 | 2018-03-05 02:00 | 2 | 2 | 86.8421 | 18.1404 | 0 | 2018-03-05 02:00 | 2 | 2 | 65.9229 | 13.7706 | 0
2018-03-05 03:00 | 3 | 2 | 86.2776 | 18.0225 | 0 | 2018-03-05 03:00 | 3 | 2 | 86.5766 | 18.085 | 0 | 2018-03-05 03:00 | 3 | 2 | 86.7536 | 18.122 | 0 | 2018-03-05 03:00 | 3 | 2 | 65.8655 | 13.7586 | 0
2018-03-05 04:00 | 4 | 2 | 86.5034 | 18.0697 | 0 | 2018-03-05 04:00 | 4 | 2 | 86.8849 | 18.1494 | 0 | 2018-03-05 04:00 | 4 | 2 | 87.0283 | 18.1793 | 0 | 2018-03-05 04:00 | 4 | 2 | 66.087 | 13.8049 | 0
2018-03-05 05:00 | 5 | 2 | 86.3661 | 18.041 | 0 | 2018-03-05 05:00 | 5 | 2 | 86.772 | 18.1258 | 0 | 2018-03-05 05:00 | 5 | 2 | 87.0054 | 18.1746 | 0 | 2018-03-05 05:00 | 5 | 2 | 66.0354 | 13.7941 | 0
2018-03-05 06:00 | 6 | 2 | 86.2898 | 18.0251 | 0 | 2018-03-05 06:00 | 6 | 2 | 86.6499 | 18.1003 | 0 | 2018-03-05 06:00 | 6 | 2 | 86.8147 | 18.1347 | 0 | 2018-03-05 06:00 | 6 | 2 | 65.9165 | 13.7693 | 0
2018-03-05 07:00 | 7 | 2 | 86.2043 | 18.0072 | 0 | 2018-03-05 07:00 | 7 | 2 | 86.5278 | 18.0748 | 0 | 2018-03-05 07:00 | 7 | 2 | 86.7079 | 18.1124 | 0 | 2018-03-05 07:00 | 7 | 2 | 65.8296 | 13.7511 | 0
2018-03-05 08:00 | 8 | 2 | 86.3355 | 18.0346 | 0 | 2018-03-05 08:00 | 8 | 2 | 86.5461 | 18.0786 | 0 | 2018-03-05 08:00 | 8 | 2 | 86.8025 | 18.1322 | 0 | 2018-03-05 08:00 | 8 | 2 | 65.8725 | 13.7601 | 0
2018-03-05 09:00 | 9 | 2 | 86.3798 | 18.0439 | 0 | 2018-03-05 09:00 | 9 | 2 | 86.7262 | 18.1162 | 0 | 2018-03-05 09:00 | 9 | 2 | 86.8711 | 18.1465 | 0 | 2018-03-05 09:00 | 9 | 2 | 65.967 | 13.7798 | 0
2018-03-05 10:00 | 10 | 2 | 86.2272 | 18.012 | 0 | 2018-03-05 10:00 | 10 | 2 | 86.5156 | 18.0722 | 0 | 2018-03-05 10:00 | 10 | 2 | 86.714 | 18.1137 | 0 | 2018-03-05 10:00 | 10 | 2 | 65.8272 | 13.7507 | 0
2018-03-05 11:00 | 11 | 2 | 86.2119 | 18.0088 | 0 | 2018-03-05 11:00 | 11 | 2 | 86.5141 | 18.0719 | 0 | 2018-03-05 11:00 | 11 | 2 | 86.7201 | 18.115 | 0 | 2018-03-05 11:00 | 11 | 2 | 65.829 | 13.751 | 0
2018-03-05 12:00 | 12 | 2 | 86.389 | 18.0458 | 0 | 2018-03-05 12:00 | 12 | 2 | 86.6835 | 18.1073 | 0 | 2018-03-05 12:00 | 12 | 2 | 86.8574 | 18.1436 | 0 | 2018-03-05 12:00 | 12 | 2 | 65.9455 | 13.7754 | 0
2018-03-05 13:00 | 13 | 2 | 86.4027 | 18.0487 | 0 | 2018-03-05 13:00 | 13 | 2 | 86.6224 | 18.0946 | 0 | 2018-03-05 13:00 | 13 | 2 | 86.7475 | 18.1207 | 0 | 2018-03-05 13:00 | 13 | 2 | 65.8806 | 13.7618 | 0
2018-03-05 14:00 | 14 | 2 | 86.3783 | 18.0436 | 0 | 2018-03-05 14:00 | 14 | 2 | 86.6606 | 18.1025 | 0 | 2018-03-05 14:00 | 14 | 2 | 86.7903 | 18.1296 | 0 | 2018-03-05 14:00 | 14 | 2 | 65.9113 | 13.7682 | 0
2018-03-05 15:00 | 15 | 2 | 86.3355 | 18.0346 | 0 | 2018-03-05 15:00 | 15 | 2 | 86.5248 | 18.0742 | 0 | 2018-03-05 15:00 | 15 | 2 | 86.7384 | 18.1188 | 0 | 2018-03-05 15:00 | 15 | 2 | 65.84 | 13.7533 | 0
2018-03-05 16:00 | 16 | 2 | 86.3493 | 18.0375 | 0 | 2018-03-05 16:00 | 16 | 2 | 86.4912 | 18.0671 | 0 | 2018-03-05 16:00 | 16 | 2 | 86.685 | 18.1076 | 0 | 2018-03-05 16:00 | 16 | 2 | 65.807 | 13.7464 | 0
2018-03-05 17:00 | 17 | 2 | 86.244 | 18.0155 | 0 | 2018-03-05 17:00 | 17 | 2 | 86.4683 | 18.0624 | 0 | 2018-03-05 17:00 | 17 | 2 | 86.6743 | 18.1054 | 0 | 2018-03-05 17:00 | 17 | 2 | 65.7942 | 13.7437 | 0
2018-03-05 18:00 | 18 | 2 | 86.3142 | 18.0302 | 0 | 2018-03-05 18:00 | 18 | 2 | 86.4378 | 18.056 | 0 | 2018-03-05 18:00 | 18 | 2 | 86.5934 | 18.0885 | 0 | 2018-03-05 18:00 | 18 | 2 | 65.7519 | 13.7349 | 0
2018-03-05 19:00 | 19 | 2 | 86.2089 | 18.0082 | 0 | 2018-03-05 19:00 | 19 | 2 | 86.3508 | 18.0378 | 0 | 2018-03-05 19:00 | 19 | 2 | 86.5583 | 18.0812 | 0 | 2018-03-05 19:00 | 19 | 2 | 65.7055 | 13.7252 | 0
2018-03-05 20:00 | 20 | 2 | 86.2181 | 18.0101 | 0 | 2018-03-05 20:00 | 20 | 2 | 86.4836 | 18.0656 | 0 | 2018-03-05 20:00 | 20 | 2 | 86.6896 | 18.1086 | 0 | 2018-03-05 20:00 | 20 | 2 | 65.8058 | 13.7462 | 0
2018-03-05 21:00 | 21 | 2 | 86.1494 | 17.9957 | 0 | 2018-03-05 21:00 | 21 | 2 | 86.4759 | 18.064 | 0 | 2018-03-05 21:00 | 21 | 2 | 86.63 | 18.0961 | 0 | 2018-03-05 21:00 | 21 | 2 | 65.7802 | 13.7408 | 0
2018-03-05 22:00 | 22 | 2 | 86.2593 | 18.0187 | 0 | 2018-03-05 22:00 | 22 | 2 | 86.5522 | 18.0799 | 0 | 2018-03-05 22:00 | 22 | 2 | 86.6468 | 18.0997 | 0 | 2018-03-05 22:00 | 22 | 2 | 65.8156 | 13.7482 | 0
2018-03-05 23:00 | 23 | 2 | 86.4424 | 18.057 | 0 | 2018-03-05 23:00 | 23 | 2 | 86.8055 | 18.1328 | 0 | 2018-03-05 23:00 | 23 | 2 | 86.8864 | 18.1497 | 0 | 2018-03-05 23:00 | 23 | 2 | 66.0029 | 13.7874 | 0
2018-03-06 | 0 | 3 | 86.4637 | 18.0614 | 0 | 2018-03-06 | 0 | 3 | 0 | 0 | 0 | 2018-03-06 | 0 | 3 | 0 | 0 | 0 | 2018-03-06 | 0 | 3 | 0 | 0 | 0
2018-03-06 01:00 | 1 | 3 | 86.5629 | 18.0821 | 0 | 2018-03-06 01:00 | 1 | 3 | 0 | 0 | 0 | 2018-03-06 01:00 | 1 | 3 | 0 | 0 | 0 | 2018-03-06 01:00 | 1 | 3 | 0 | 0 | 0
2018-03-06 02:00 | 2 | 3 | 86.3706 | 18.042 | 0 | 2018-03-06 02:00 | 2 | 3 | 0 | 0 | 0 | 2018-03-06 02:00 | 2 | 3 | 0 | 0 | 0 | 2018-03-06 02:00 | 2 | 3 | 0 | 0 | 0
2018-03-06 03:00 | 3 | 3 | 86.3523 | 18.0381 | 0 | 2018-03-06 03:00 | 3 | 3 | 0 | 0 | 0 | 2018-03-06 03:00 | 3 | 3 | 0 | 0 | 0 | 2018-03-06 03:00 | 3 | 3 | 0 | 0 | 0
2018-03-06 04:00 | 4 | 3 | 86.3676 | 18.0413 | 0 | 2018-03-06 04:00 | 4 | 3 | 0 | 0 | 0 | 2018-03-06 04:00 | 4 | 3 | 0 | 0 | 0 | 2018-03-06 04:00 | 4 | 3 | 0 | 0 | 0
2018-03-06 05:00 | 5 | 3 | 86.4027 | 18.0487 | 0 | 2018-03-06 05:00 | 5 | 3 | 0 | 0 | 0 | 2018-03-06 05:00 | 5 | 3 | 0 | 0 | 0 | 2018-03-06 05:00 | 5 | 3 | 0 | 0 | 0
2018-03-06 06:00 | 6 | 3 | 86.4652 | 18.0617 | 0 | 2018-03-06 06:00 | 6 | 3 | 0 | 0 | 0 | 2018-03-06 06:00 | 6 | 3 | 0 | 0 | 0 | 2018-03-06 06:00 | 6 | 3 | 0 | 0 | 0
2018-03-06 07:00 | 7 | 3 | 86.4012 | 18.0483 | 0 | 2018-03-06 07:00 | 7 | 3 | 0 | 0 | 0 | 2018-03-06 07:00 | 7 | 3 | 0 | 0 | 0 | 2018-03-06 07:00 | 7 | 3 | 0 | 0 | 0
2018-03-06 08:00 | 8 | 3 | 86.4515 | 18.0589 | 0 | 2018-03-06 08:00 | 8 | 3 | 0 | 0 | 0 | 2018-03-06 08:00 | 8 | 3 | 0 | 0 | 0 | 2018-03-06 08:00 | 8 | 3 | 0 | 0 | 0
2018-03-06 09:00 | 9 | 3 | 86.2028 | 18.0069 | 0 | 2018-03-06 09:00 | 9 | 3 | 0 | 0 | 0 | 2018-03-06 09:00 | 9 | 3 | 0 | 0 | 0 | 2018-03-06 09:00 | 9 | 3 | 0 | 0 | 0
2018-03-06 10:00 | 10 | 3 | 86.2715 | 18.0213 | 0 | 2018-03-06 10:00 | 10 | 3 | 0 | 0 | 0 | 2018-03-06 10:00 | 10 | 3 | 0 | 0 | 0 | 2018-03-06 10:00 | 10 | 3 | 0 | 0 | 0
2018-03-06 11:00 | 11 | 3 | 86.7567 | 18.1226 | 0 | 2018-03-06 11:00 | 11 | 3 | 0 | 0 | 0 | 2018-03-06 11:00 | 11 | 3 | 0 | 0 | 0 | 2018-03-06 11:00 | 11 | 3 | 0 | 0 | 0
2018-03-06 12:00 | 12 | 3 | 86.6194 | 18.0939 | 0 | 2018-03-06 12:00 | 12 | 3 | 0 | 0 | 0 | 2018-03-06 12:00 | 12 | 3 | 0 | 0 | 0 | 2018-03-06 12:00 | 12 | 3 | 0 | 0 | 0
2018-03-06 13:00 | 13 | 3 | 86.6377 | 18.0977 | 0 | 2018-03-06 13:00 | 13 | 3 | 0 | 0 | 0 | 2018-03-06 13:00 | 13 | 3 | 0 | 0 | 0 | 2018-03-06 13:00 | 13 | 3 | 0 | 0 | 0
2018-03-06 14:00 | 14 | 3 | 86.8757 | 18.1475 | 0 | 2018-03-06 14:00 | 14 | 3 | 0 | 0 | 0 | 2018-03-06 14:00 | 14 | 3 | 0 | 0 | 0 | 2018-03-06 14:00 | 14 | 3 | 0 | 0 | 0
2018-03-06 15:00 | 15 | 3 | 86.7994 | 18.1315 | 0 | 2018-03-06 15:00 | 15 | 3 | 0 | 0 | 0 | 2018-03-06 15:00 | 15 | 3 | 0 | 0 | 0 | 2018-03-06 15:00 | 15 | 3 | 0 | 0 | 0
2018-03-06 16:00 | 16 | 3 | 86.7674 | 18.1248 | 0 | 2018-03-06 16:00 | 16 | 3 | 0 | 0 | 0 | 2018-03-06 16:00 | 16 | 3 | 0 | 0 | 0 | 2018-03-06 16:00 | 16 | 3 | 0 | 0 | 0
2018-03-06 17:00 | 17 | 3 | 86.7384 | 18.1188 | 0 | 2018-03-06 17:00 | 17 | 3 | 0 | 0 | 0 | 2018-03-06 17:00 | 17 | 3 | 0 | 0 | 0 | 2018-03-06 17:00 | 17 | 3 | 0 | 0 | 0
2018-03-06 18:00 | 18 | 3 | 86.7124 | 18.1134 | 0 | 2018-03-06 18:00 | 18 | 3 | 0 | 0 | 0 | 2018-03-06 18:00 | 18 | 3 | 0 | 0 | 0 | 2018-03-06 18:00 | 18 | 3 | 0 | 0 | 0
2018-03-06 19:00 | 19 | 3 | 86.8376 | 18.1395 | 0 | 2018-03-06 19:00 | 19 | 3 | 0 | 0 | 0 | 2018-03-06 19:00 | 19 | 3 | 0 | 0 | 0 | 2018-03-06 19:00 | 19 | 3 | 0 | 0 | 0
2018-03-06 20:00 | 20 | 3 | 86.627 | 18.0955 | 0 | 2018-03-06 20:00 | 20 | 3 | 0 | 0 | 0 | 2018-03-06 20:00 | 20 | 3 | 0 | 0 | 0 | 2018-03-06 20:00 | 20 | 3 | 0 | 0 | 0
2018-03-06 21:00 | 21 | 3 | 86.6239 | 18.0949 | 0 | 2018-03-06 21:00 | 21 | 3 | 0 | 0 | 0 | 2018-03-06 21:00 | 21 | 3 | 0 | 0 | 0 | 2018-03-06 21:00 | 21 | 3 | 0 | 0 | 0
2018-03-06 22:00 | 22 | 3 | 86.714 | 18.1137 | 0 | 2018-03-06 22:00 | 22 | 3 | 0 | 0 | 0 | 2018-03-06 22:00 | 22 | 3 | 0 | 0 | 0 | 2018-03-06 22:00 | 22 | 3 | 0 | 0 | 0
2018-03-06 23:00 | 23 | 3 | 86.8971 | 18.1519 | 0 | 2018-03-06 23:00 | 23 | 3 | 0 | 0 | 0 | 2018-03-06 23:00 | 23 | 3 | 0 | 0 | 0 | 2018-03-06 23:00 | 23 | 3 | 0 | 0 | 0
2018-03-07 | 0 | 4 | 0 | 0 | 0 | 2018-03-07 | 0 | 4 | 0 | 0 | 0 | 2018-03-07 | 0 | 4 | 86.6712 | 18.1047 | 0 | 2018-03-07 | 0 | 4 | 32.9351 | 6.8798 | 0
2018-03-07 01:00 | 1 | 4 | 0 | 0 | 0 | 2018-03-07 01:00 | 1 | 4 | 0 | 0 | 0 | 2018-03-07 01:00 | 1 | 4 | 86.511 | 18.0713 | 0 | 2018-03-07 01:00 | 1 | 4 | 32.8742 | 6.8671 | 0
2018-03-07 02:00 | 2 | 4 | 0 | 0 | 0 | 2018-03-07 02:00 | 2 | 4 | 0 | 0 | 0 | 2018-03-07 02:00 | 2 | 4 | 86.7628 | 18.1239 | 0 | 2018-03-07 02:00 | 2 | 4 | 32.9699 | 6.8871 | 0
2018-03-07 03:00 | 3 | 4 | 0 | 0 | 0 | 2018-03-07 03:00 | 3 | 4 | 0 | 0 | 0 | 2018-03-07 03:00 | 3 | 4 | 86.7384 | 18.1188 | 0 | 2018-03-07 03:00 | 3 | 4 | 32.9606 | 6.8851 | 0
2018-03-07 04:00 | 4 | 4 | 0 | 0 | 0 | 2018-03-07 04:00 | 4 | 4 | 0 | 0 | 0 | 2018-03-07 04:00 | 4 | 4 | 86.8376 | 18.1395 | 0 | 2018-03-07 04:00 | 4 | 4 | 32.9983 | 6.893 | 0
2018-03-07 05:00 | 5 | 4 | 0 | 0 | 0 | 2018-03-07 05:00 | 5 | 4 | 0 | 0 | 0 | 2018-03-07 05:00 | 5 | 4 | 87.0222 | 18.1781 | 0 | 2018-03-07 05:00 | 5 | 4 | 33.0684 | 6.9077 | 0
2018-03-07 06:00 | 6 | 4 | 0 | 0 | 0 | 2018-03-07 06:00 | 6 | 4 | 0 | 0 | 0 | 2018-03-07 06:00 | 6 | 4 | 86.9627 | 18.1656 | 0 | 2018-03-07 06:00 | 6 | 4 | 33.0458 | 6.9029 | 0
2018-03-07 07:00 | 7 | 4 | 0 | 0 | 0 | 2018-03-07 07:00 | 7 | 4 | 0 | 0 | 0 | 2018-03-07 07:00 | 7 | 4 | 87.1321 | 18.201 | 0 | 2018-03-07 07:00 | 7 | 4 | 33.1102 | 6.9164 | 0
2018-03-07 08:00 | 8 | 4 | 0 | 0 | 0 | 2018-03-07 08:00 | 8 | 4 | 0 | 0 | 0 | 2018-03-07 08:00 | 8 | 4 | 87.1931 | 18.2138 | 0 | 2018-03-07 08:00 | 8 | 4 | 33.1334 | 6.9212 | 0
2018-03-07 09:00 | 9 | 4 | 0 | 0 | 0 | 2018-03-07 09:00 | 9 | 4 | 0 | 0 | 0 | 2018-03-07 09:00 | 9 | 4 | 86.7155 | 18.114 | 0 | 2018-03-07 09:00 | 9 | 4 | 32.9519 | 6.8833 | 0
2018-03-07 10:00 | 10 | 4 | 0 | 0 | 0 | 2018-03-07 10:00 | 10 | 4 | 0 | 0 | 0 | 2018-03-07 10:00 | 10 | 4 | 86.6743 | 18.1054 | 0 | 2018-03-07 10:00 | 10 | 4 | 32.9362 | 6.88 | 0
2018-03-07 11:00 | 11 | 4 | 0 | 0 | 0 | 2018-03-07 11:00 | 11 | 4 | 0 | 0 | 0 | 2018-03-07 11:00 | 11 | 4 | 86.8956 | 18.1516 | 0 | 2018-03-07 11:00 | 11 | 4 | 33.0203 | 6.8976 | 0
2018-03-07 12:00 | 12 | 4 | 0 | 0 | 0 | 2018-03-07 12:00 | 12 | 4 | 0 | 0 | 0 | 2018-03-07 12:00 | 12 | 4 | 86.9276 | 18.1583 | 0 | 2018-03-07 12:00 | 12 | 4 | 33.0325 | 6.9002 | 0
2018-03-07 13:00 | 13 | 4 | 0 | 0 | 0 | 2018-03-07 13:00 | 13 | 4 | 0 | 0 | 0 | 2018-03-07 13:00 | 13 | 4 | 87.2541 | 18.2265 | 0 | 2018-03-07 13:00 | 13 | 4 | 33.1566 | 6.9261 | 0
2018-03-07 14:00 | 14 | 4 | 0 | 0 | 0 | 2018-03-07 14:00 | 14 | 4 | 0 | 0 | 0 | 2018-03-07 14:00 | 14 | 4 | 87.4037 | 18.2578 | 0 | 2018-03-07 14:00 | 14 | 4 | 33.2134 | 6.9379 | 0
2018-03-07 15:00 | 15 | 4 | 0 | 0 | 0 | 2018-03-07 15:00 | 15 | 4 | 0 | 0 | 0 | 2018-03-07 15:00 | 15 | 4 | 87.2129 | 18.2179 | 0 | 2018-03-07 15:00 | 15 | 4 | 33.1409 | 6.9228 | 0
2018-03-07 16:00 | 16 | 4 | 0 | 0 | 0 | 2018-03-07 16:00 | 16 | 4 | 0 | 0 | 0 | 2018-03-07 16:00 | 16 | 4 | 86.9718 | 18.1675 | 0 | 2018-03-07 16:00 | 16 | 4 | 33.0493 | 6.9037 | 0
2018-03-07 17:00 | 17 | 4 | 0 | 0 | 0 | 2018-03-07 17:00 | 17 | 4 | 0 | 0 | 0 | 2018-03-07 17:00 | 17 | 4 | 87.1397 | 18.2026 | 0 | 2018-03-07 17:00 | 17 | 4 | 33.1131 | 6.917 | 0
2018-03-07 18:00 | 18 | 4 | 0 | 0 | 0 | 2018-03-07 18:00 | 18 | 4 | 0 | 0 | 0 | 2018-03-07 18:00 | 18 | 4 | 87.2435 | 18.2243 | 0 | 2018-03-07 18:00 | 18 | 4 | 33.1525 | 6.9252 | 0
2018-03-07 19:00 | 19 | 4 | 0 | 0 | 0 | 2018-03-07 19:00 | 19 | 4 | 0 | 0 | 0 | 2018-03-07 19:00 | 19 | 4 | 86.8894 | 18.1503 | 0 | 2018-03-07 19:00 | 19 | 4 | 33.018 | 6.8971 | 0
2018-03-07 20:00 | 20 | 4 | 0 | 0 | 0 | 2018-03-07 20:00 | 20 | 4 | 0 | 0 | 0 | 2018-03-07 20:00 | 20 | 4 | 87.1839 | 18.2118 | 0 | 2018-03-07 20:00 | 20 | 4 | 33.1299 | 6.9205 | 0
2018-03-07 21:00 | 21 | 4 | 0 | 0 | 0 | 2018-03-07 21:00 | 21 | 4 | 0 | 0 | 0 | 2018-03-07 21:00 | 21 | 4 | 87.2419 | 18.224 | 0 | 2018-03-07 21:00 | 21 | 4 | 33.1519 | 6.9251 | 0
2018-03-07 22:00 | 22 | 4 | 0 | 0 | 0 | 2018-03-07 22:00 | 22 | 4 | 0 | 0 | 0 | 2018-03-07 22:00 | 22 | 4 | 87.1733 | 18.2096 | 0 | 2018-03-07 22:00 | 22 | 4 | 33.1259 | 6.9197 | 0
2018-03-07 23:00 | 23 | 4 | 0 | 0 | 0 | 2018-03-07 23:00 | 23 | 4 | 0 | 0 | 0 | 2018-03-07 23:00 | 23 | 4 | 87.2557 | 18.2268 | 0 | 2018-03-07 23:00 | 23 | 4 | 33.1572 | 6.9262 | 0
2018-03-08 | 0 | 5 | 86.5492 | 18.0793 | 0 | 2018-03-08 | 0 | 5 | 0 | 0 | 0 | 2018-03-08 | 0 | 5 | 0 | 0 | 0 | 2018-03-08 | 0 | 5 | 0 | 0 | 0
2018-03-08 01:00 | 1 | 5 | 86.7201 | 18.115 | 0 | 2018-03-08 01:00 | 1 | 5 | 0 | 0 | 0 | 2018-03-08 01:00 | 1 | 5 | 0 | 0 | 0 | 2018-03-08 01:00 | 1 | 5 | 0 | 0 | 0
2018-03-08 02:00 | 2 | 5 | 86.5095 | 18.071 | 0 | 2018-03-08 02:00 | 2 | 5 | 0 | 0 | 0 | 2018-03-08 02:00 | 2 | 5 | 0 | 0 | 0 | 2018-03-08 02:00 | 2 | 5 | 0 | 0 | 0
2018-03-08 03:00 | 3 | 5 | 86.4576 | 18.0601 | 0 | 2018-03-08 03:00 | 3 | 5 | 0 | 0 | 0 | 2018-03-08 03:00 | 3 | 5 | 0 | 0 | 0 | 2018-03-08 03:00 | 3 | 5 | 0 | 0 | 0
2018-03-08 04:00 | 4 | 5 | 86.6316 | 18.0965 | 0 | 2018-03-08 04:00 | 4 | 5 | 0 | 0 | 0 | 2018-03-08 04:00 | 4 | 5 | 0 | 0 | 0 | 2018-03-08 04:00 | 4 | 5 | 0 | 0 | 0
2018-03-08 05:00 | 5 | 5 | 86.569 | 18.0834 | 0 | 2018-03-08 05:00 | 5 | 5 | 0 | 0 | 0 | 2018-03-08 05:00 | 5 | 5 | 0 | 0 | 0 | 2018-03-08 05:00 | 5 | 5 | 0 | 0 | 0
2018-03-08 06:00 | 6 | 5 | 86.6468 | 18.0997 | 0 | 2018-03-08 06:00 | 6 | 5 | 0 | 0 | 0 | 2018-03-08 06:00 | 6 | 5 | 0 | 0 | 0 | 2018-03-08 06:00 | 6 | 5 | 0 | 0 | 0
2018-03-08 07:00 | 7 | 5 | 86.6361 | 18.0974 | 0 | 2018-03-08 07:00 | 7 | 5 | 0 | 0 | 0 | 2018-03-08 07:00 | 7 | 5 | 0 | 0 | 0 | 2018-03-08 07:00 | 7 | 5 | 0 | 0 | 0
2018-03-08 08:00 | 8 | 5 | 86.6819 | 18.107 | 0 | 2018-03-08 08:00 | 8 | 5 | 0 | 0 | 0 | 2018-03-08 08:00 | 8 | 5 | 0 | 0 | 0 | 2018-03-08 08:00 | 8 | 5 | 0 | 0 | 0
2018-03-08 09:00 | 9 | 5 | 86.7094 | 18.1127 | 0 | 2018-03-08 09:00 | 9 | 5 | 0 | 0 | 0 | 2018-03-08 09:00 | 9 | 5 | 0 | 0 | 0 | 2018-03-08 09:00 | 9 | 5 | 0 | 0 | 0
2018-03-08 10:00 | 10 | 5 | 86.7933 | 18.1303 | 0 | 2018-03-08 10:00 | 10 | 5 | 0 | 0 | 0 | 2018-03-08 10:00 | 10 | 5 | 0 | 0 | 0 | 2018-03-08 10:00 | 10 | 5 | 0 | 0 | 0
2018-03-08 11:00 | 11 | 5 | 86.8009 | 18.1318 | 0 | 2018-03-08 11:00 | 11 | 5 | 0 | 0 | 0 | 2018-03-08 11:00 | 11 | 5 | 0 | 0 | 0 | 2018-03-08 11:00 | 11 | 5 | 0 | 0 | 0
2018-03-08 12:00 | 12 | 5 | 86.6728 | 18.1051 | 0 | 2018-03-08 12:00 | 12 | 5 | 0 | 0 | 0 | 2018-03-08 12:00 | 12 | 5 | 0 | 0 | 0 | 2018-03-08 12:00 | 12 | 5 | 0 | 0 | 0
2018-03-08 13:00 | 13 | 5 | 86.6316 | 18.0965 | 0 | 2018-03-08 13:00 | 13 | 5 | 0 | 0 | 0 | 2018-03-08 13:00 | 13 | 5 | 0 | 0 | 0 | 2018-03-08 13:00 | 13 | 5 | 0 | 0 | 0
2018-03-08 14:00 | 14 | 5 | 86.6316 | 18.0965 | 0 | 2018-03-08 14:00 | 14 | 5 | 0 | 0 | 0 | 2018-03-08 14:00 | 14 | 5 | 0 | 0 | 0 | 2018-03-08 14:00 | 14 | 5 | 0 | 0 | 0
2018-03-08 15:00 | 15 | 5 | 86.6636 | 18.1032 | 0 | 2018-03-08 15:00 | 15 | 5 | 0 | 0 | 0 | 2018-03-08 15:00 | 15 | 5 | 0 | 0 | 0 | 2018-03-08 15:00 | 15 | 5 | 0 | 0 | 0
2018-03-08 16:00 | 16 | 5 | 86.5568 | 18.0808 | 0 | 2018-03-08 16:00 | 16 | 5 | 0 | 0 | 0 | 2018-03-08 16:00 | 16 | 5 | 0 | 0 | 0 | 2018-03-08 16:00 | 16 | 5 | 0 | 0 | 0
2018-03-08 17:00 | 17 | 5 | 86.6865 | 18.1079 | 0 | 2018-03-08 17:00 | 17 | 5 | 0 | 0 | 0 | 2018-03-08 17:00 | 17 | 5 | 0 | 0 | 0 | 2018-03-08 17:00 | 17 | 5 | 0 | 0 | 0
2018-03-08 18:00 | 18 | 5 | 86.7262 | 18.1162 | 0 | 2018-03-08 18:00 | 18 | 5 | 0 | 0 | 0 | 2018-03-08 18:00 | 18 | 5 | 0 | 0 | 0 | 2018-03-08 18:00 | 18 | 5 | 0 | 0 | 0
2018-03-08 19:00 | 19 | 5 | 86.5187 | 18.0729 | 0 | 2018-03-08 19:00 | 19 | 5 | 0 | 0 | 0 | 2018-03-08 19:00 | 19 | 5 | 0 | 0 | 0 | 2018-03-08 19:00 | 19 | 5 | 0 | 0 | 0
2018-03-08 20:00 | 20 | 5 | 86.5766 | 18.085 | 0 | 2018-03-08 20:00 | 20 | 5 | 0 | 0 | 0 | 2018-03-08 20:00 | 20 | 5 | 0 | 0 | 0 | 2018-03-08 20:00 | 20 | 5 | 0 | 0 | 0
2018-03-08 21:00 | 21 | 5 | 86.6194 | 18.0939 | 0 | 2018-03-08 21:00 | 21 | 5 | 0 | 0 | 0 | 2018-03-08 21:00 | 21 | 5 | 0 | 0 | 0 | 2018-03-08 21:00 | 21 | 5 | 0 | 0 | 0
2018-03-08 22:00 | 22 | 5 | 86.6743 | 18.1054 | 0 | 2018-03-08 22:00 | 22 | 5 | 0 | 0 | 0 | 2018-03-08 22:00 | 22 | 5 | 0 | 0 | 0 | 2018-03-08 22:00 | 22 | 5 | 0 | 0 | 0
2018-03-08 23:00 | 23 | 5 | 86.5644 | 18.0824 | 0 | 2018-03-08 23:00 | 23 | 5 | 0 | 0 | 0 | 2018-03-08 23:00 | 23 | 5 | 0 | 0 | 0 | 2018-03-08 23:00 | 23 | 5 | 0 | 0 | 0
2018-03-09 | 0 | 6 | 86.2226 | 18.011 | 0 | 2018-03-09 | 0 | 6 | 86.688 | 18.1083 | 0 | 2018-03-09 | 0 | 6 | 0 | 0 | 0 | 2018-03-09 | 0 | 6 | 32.9414 | 6.8811 | 0
2018-03-09 01:00 | 1 | 6 | 86.1128 | 17.9881 | 0 | 2018-03-09 01:00 | 1 | 6 | 86.5232 | 18.0738 | 0 | 2018-03-09 01:00 | 1 | 6 | 0 | 0 | 0 | 2018-03-09 01:00 | 1 | 6 | 32.8788 | 6.8681 | 0
2018-03-09 02:00 | 2 | 6 | 86.2791 | 18.0228 | 0 | 2018-03-09 02:00 | 2 | 6 | 86.6896 | 18.1086 | 0 | 2018-03-09 02:00 | 2 | 6 | 0 | 0 | 0 | 2018-03-09 02:00 | 2 | 6 | 32.942 | 6.8813 | 0
2018-03-09 03:00 | 3 | 6 | 86.0014 | 17.9648 | 0 | 2018-03-09 03:00 | 3 | 6 | 86.4485 | 18.0582 | 0 | 2018-03-09 03:00 | 3 | 6 | 0 | 0 | 0 | 2018-03-09 03:00 | 3 | 6 | 32.8504 | 6.8621 | 0
2018-03-09 04:00 | 4 | 6 | 86.0533 | 17.9757 | 0 | 2018-03-09 04:00 | 4 | 6 | 86.4347 | 18.0553 | 0 | 2018-03-09 04:00 | 4 | 6 | 0 | 0 | 0 | 2018-03-09 04:00 | 4 | 6 | 32.8452 | 6.861 | 0
2018-03-09 05:00 | 5 | 6 | 86.2257 | 18.0117 | 0 | 2018-03-09 05:00 | 5 | 6 | 86.6117 | 18.0923 | 0 | 2018-03-09 05:00 | 5 | 6 | 0 | 0 | 0 | 2018-03-09 05:00 | 5 | 6 | 32.9124 | 6.8751 | 0
2018-03-09 06:00 | 6 | 6 | 86.4332 | 18.055 | 0 | 2018-03-09 06:00 | 6 | 6 | 86.9352 | 18.1599 | 0 | 2018-03-09 06:00 | 6 | 6 | 0 | 0 | 0 | 2018-03-09 06:00 | 6 | 6 | 33.0354 | 6.9008 | 0
2018-03-09 07:00 | 7 | 6 | 86.5873 | 18.0872 | 0 | 2018-03-09 07:00 | 7 | 6 | 87.0619 | 18.1864 | 0 | 2018-03-09 07:00 | 7 | 6 | 0 | 0 | 0 | 2018-03-09 07:00 | 7 | 6 | 33.0835 | 6.9108 | 0
2018-03-09 08:00 | 8 | 6 | 86.3691 | 18.0416 | 0 | 2018-03-09 08:00 | 8 | 6 | 86.7811 | 18.1277 | 0 | 2018-03-09 08:00 | 8 | 6 | 0 | 0 | 0 | 2018-03-09 08:00 | 8 | 6 | 32.9768 | 6.8885 | 0
2018-03-09 09:00 | 9 | 6 | 86.334 | 18.0343 | 0 | 2018-03-09 09:00 | 9 | 6 | 86.7399 | 18.1191 | 0 | 2018-03-09 09:00 | 9 | 6 | 0 | 0 | 0 | 2018-03-09 09:00 | 9 | 6 | 32.9612 | 6.8853 | 0
2018-03-09 10:00 | 10 | 6 | 86.5126 | 18.0716 | 0 | 2018-03-09 10:00 | 10 | 6 | 86.862 | 18.1446 | 0 | 2018-03-09 10:00 | 10 | 6 | 0 | 0 | 0 | 2018-03-09 10:00 | 10 | 6 | 33.0076 | 6.8949 | 0
2018-03-09 11:00 | 11 | 6 | 86.5003 | 18.069 | 0 | 2018-03-09 11:00 | 11 | 6 | 86.9306 | 18.1589 | 0 | 2018-03-09 11:00 | 11 | 6 | 0 | 0 | 0 | 2018-03-09 11:00 | 11 | 6 | 33.0336 | 6.9004 | 0
2018-03-09 12:00 | 12 | 6 | 86.7002 | 18.1108 | 0 | 2018-03-09 12:00 | 12 | 6 | 87.1412 | 18.2029 | 0 | 2018-03-09 12:00 | 12 | 6 | 0 | 0 | 0 | 2018-03-09 12:00 | 12 | 6 | 33.1137 | 6.9171 | 0
2018-03-09 13:00 | 13 | 6 | 86.363 | 18.0404 | 0 | 2018-03-09 13:00 | 13 | 6 | 86.8009 | 18.1318 | 0 | 2018-03-09 13:00 | 13 | 6 | 0 | 0 | 0 | 2018-03-09 13:00 | 13 | 6 | 32.9843 | 6.8901 | 0
2018-03-09 14:00 | 14 | 6 | 86.4408 | 18.0566 | 0 | 2018-03-09 14:00 | 14 | 6 | 86.8635 | 18.1449 | 0 | 2018-03-09 14:00 | 14 | 6 | 0 | 0 | 0 | 2018-03-09 14:00 | 14 | 6 | 33.0081 | 6.8951 | 0
2018-03-09 15:00 | 15 | 6 | 86.2943 | 18.026 | 0 | 2018-03-09 15:00 | 15 | 6 | 86.6743 | 18.1054 | 0 | 2018-03-09 15:00 | 15 | 6 | 0 | 0 | 0 | 2018-03-09 15:00 | 15 | 6 | 32.9362 | 6.88 | 0
2018-03-09 16:00 | 16 | 6 | 86.3706 | 18.042 | 0 | 2018-03-09 16:00 | 16 | 6 | 86.7491 | 18.121 | 0 | 2018-03-09 16:00 | 16 | 6 | 0 | 0 | 0 | 2018-03-09 16:00 | 16 | 6 | 32.9647 | 6.886 | 0
2018-03-09 17:00 | 17 | 6 | 86.2882 | 18.0247 | 0 | 2018-03-09 17:00 | 17 | 6 | 86.7445 | 18.1201 | 0 | 2018-03-09 17:00 | 17 | 6 | 0 | 0 | 0 | 2018-03-09 17:00 | 17 | 6 | 32.9629 | 6.8856 | 0
2018-03-09 18:00 | 18 | 6 | 86.1875 | 18.0037 | 0 | 2018-03-09 18:00 | 18 | 6 | 86.6667 | 18.1038 | 0 | 2018-03-09 18:00 | 18 | 6 | 0 | 0 | 0 | 2018-03-09 18:00 | 18 | 6 | 32.9333 | 6.8794 | 0
2018-03-09 19:00 | 19 | 6 | 86.099 | 17.9852 | 0 | 2018-03-09 19:00 | 19 | 6 | 86.5431 | 18.078 | 0 | 2018-03-09 19:00 | 19 | 6 | 0 | 0 | 0 | 2018-03-09 19:00 | 19 | 6 | 32.8864 | 6.8696 | 0
2018-03-09 20:00 | 20 | 6 | 86.1997 | 18.0063 | 0 | 2018-03-09 20:00 | 20 | 6 | 86.5187 | 18.0729 | 0 | 2018-03-09 20:00 | 20 | 6 | 0 | 0 | 0 | 2018-03-09 20:00 | 20 | 6 | 32.8771 | 6.8677 | 0
2018-03-09 21:00 | 21 | 6 | 86.3767 | 18.0432 | 0 | 2018-03-09 21:00 | 21 | 6 | 86.7247 | 18.1159 | 0 | 2018-03-09 21:00 | 21 | 6 | 0 | 0 | 0 | 2018-03-09 21:00 | 21 | 6 | 32.9554 | 6.8841 | 0
2018-03-09 22:00 | 22 | 6 | 86.3691 | 18.0416 | 0 | 2018-03-09 22:00 | 22 | 6 | 86.7659 | 18.1245 | 0 | 2018-03-09 22:00 | 22 | 6 | 0 | 0 | 0 | 2018-03-09 22:00 | 22 | 6 | 32.971 | 6.8873 | 0
2018-03-09 23:00 | 23 | 6 | 86.4012 | 18.0483 | 0 | 2018-03-09 23:00 | 23 | 6 | 86.7918 | 18.1299 | 0 | 2018-03-09 23:00 | 23 | 6 | 0 | 0 | 0 | 2018-03-09 23:00 | 23 | 6 | 32.9809 | 6.8894 | 0
2018-03-10 | 0 | 7 | 86.0121 | 17.9671 | 0 | 2018-03-10 | 0 | 7 | 0 | 0 | 0 | 2018-03-10 | 0 | 7 | 86.5507 | 18.0796 | 0 | 2018-03-10 | 0 | 7 | 32.8893 | 6.8702 | 0
2018-03-10 01:00 | 1 | 7 | 85.919 | 17.9476 | 0 | 2018-03-10 01:00 | 1 | 7 | 0 | 0 | 0 | 2018-03-10 01:00 | 1 | 7 | 86.5324 | 18.0758 | 0 | 2018-03-10 01:00 | 1 | 7 | 32.8823 | 6.8688 | 0
2018-03-10 02:00 | 2 | 7 | 86.0533 | 17.9757 | 0 | 2018-03-10 02:00 | 2 | 7 | 0 | 0 | 0 | 2018-03-10 02:00 | 2 | 7 | 86.6453 | 18.0993 | 0 | 2018-03-10 02:00 | 2 | 7 | 32.9252 | 6.8777 | 0
2018-03-10 03:00 | 3 | 7 | 86.1677 | 17.9996 | 0 | 2018-03-10 03:00 | 3 | 7 | 0 | 0 | 0 | 2018-03-10 03:00 | 3 | 7 | 86.7002 | 18.1108 | 0 | 2018-03-10 03:00 | 3 | 7 | 32.9461 | 6.8821 | 0
2018-03-10 04:00 | 4 | 7 | 86.3081 | 18.0289 | 0 | 2018-03-10 04:00 | 4 | 7 | 0 | 0 | 0 | 2018-03-10 04:00 | 4 | 7 | 86.8513 | 18.1424 | 0 | 2018-03-10 04:00 | 4 | 7 | 33.0035 | 6.8941 | 0
2018-03-10 05:00 | 5 | 7 | 86.2562 | 18.0181 | 0 | 2018-03-10 05:00 | 5 | 7 | 0 | 0 | 0 | 2018-03-10 05:00 | 5 | 7 | 86.8605 | 18.1443 | 0 | 2018-03-10 05:00 | 5 | 7 | 33.007 | 6.8948 | 0
2018-03-10 06:00 | 6 | 7 | 86.1234 | 17.9903 | 0 | 2018-03-10 06:00 | 6 | 7 | 0 | 0 | 0 | 2018-03-10 06:00 | 6 | 7 | 86.6682 | 18.1041 | 0 | 2018-03-10 06:00 | 6 | 7 | 32.9339 | 6.8796 | 0
2018-03-10 07:00 | 7 | 7 | 86.1906 | 18.0044 | 0 | 2018-03-10 07:00 | 7 | 7 | 0 | 0 | 0 | 2018-03-10 07:00 | 7 | 7 | 86.7247 | 18.1159 | 0 | 2018-03-10 07:00 | 7 | 7 | 32.9554 | 6.8841 | 0
2018-03-10 08:00 | 8 | 7 | 86.36 | 18.0397 | 0 | 2018-03-10 08:00 | 8 | 7 | 0 | 0 | 0 | 2018-03-10 08:00 | 8 | 7 | 86.952 | 18.1634 | 0 | 2018-03-10 08:00 | 8 | 7 | 33.0418 | 6.9021 | 0
2018-03-10 09:00 | 9 | 7 | 86.4912 | 18.0671 | 0 | 2018-03-10 09:00 | 9 | 7 | 0 | 0 | 0 | 2018-03-10 09:00 | 9 | 7 | 87.0588 | 18.1857 | 0 | 2018-03-10 09:00 | 9 | 7 | 33.0823 | 6.9106 | 0
2018-03-10 10:00 | 10 | 7 | 86.1982 | 18.0059 | 0 | 2018-03-10 10:00 | 10 | 7 | 0 | 0 | 0 | 2018-03-10 10:00 | 10 | 7 | 86.6392 | 18.0981 | 0 | 2018-03-10 10:00 | 10 | 7 | 32.9229 | 6.8773 | 0
2018-03-10 11:00 | 11 | 7 | 86.1707 | 18.0002 | 0 | 2018-03-10 11:00 | 11 | 7 | 0 | 0 | 0 | 2018-03-10 11:00 | 11 | 7 | 86.8849 | 18.1494 | 0 | 2018-03-10 11:00 | 11 | 7 | 33.0163 | 6.8968 | 0
2018-03-10 12:00 | 12 | 7 | 86.5019 | 18.0694 | 0 | 2018-03-10 12:00 | 12 | 7 | 0 | 0 | 0 | 2018-03-10 12:00 | 12 | 7 | 87.1504 | 18.2048 | 0 | 2018-03-10 12:00 | 12 | 7 | 33.1172 | 6.9178 | 0
2018-03-10 13:00 | 13 | 7 | 86.6148 | 18.093 | 0 | 2018-03-10 13:00 | 13 | 7 | 0 | 0 | 0 | 2018-03-10 13:00 | 13 | 7 | 87.3167 | 18.2396 | 0 | 2018-03-10 13:00 | 13 | 7 | 33.1803 | 6.931 | 0
2018-03-10 14:00 | 14 | 7 | 86.4439 | 18.0573 | 0 | 2018-03-10 14:00 | 14 | 7 | 0 | 0 | 0 | 2018-03-10 14:00 | 14 | 7 | 87.0832 | 18.1908 | 0 | 2018-03-10 14:00 | 14 | 7 | 33.0916 | 6.9125 | 0
2018-03-10 15:00 | 15 | 7 | 86.5522 | 18.0799 | 0 | 2018-03-10 15:00 | 15 | 7 | 0 | 0 | 0 | 2018-03-10 15:00 | 15 | 7 | 87.2938 | 18.2348 | 0 | 2018-03-10 15:00 | 15 | 7 | 33.1716 | 6.9292 | 0
2018-03-10 16:00 | 16 | 7 | 86.5644 | 18.0824 | 0 | 2018-03-10 16:00 | 16 | 7 | 0 | 0 | 0 | 2018-03-10 16:00 | 16 | 7 | 87.3579 | 18.2482 | 0 | 2018-03-10 16:00 | 16 | 7 | 33.196 | 6.9343 | 0
2018-03-10 17:00 | 17 | 7 | 86.7445 | 18.1201 | 0 | 2018-03-10 17:00 | 17 | 7 | 0 | 0 | 0 | 2018-03-10 17:00 | 17 | 7 | 87.57 | 18.2925 | 0 | 2018-03-10 17:00 | 17 | 7 | 33.2766 | 6.9511 | 0
2018-03-10 18:00 | 18 | 7 | 86.4668 | 18.062 | 0 | 2018-03-10 18:00 | 18 | 7 | 0 | 0 | 0 | 2018-03-10 18:00 | 18 | 7 | 87.3014 | 18.2364 | 0 | 2018-03-10 18:00 | 18 | 7 | 33.1745 | 6.9298 | 0
2018-03-10 19:00 | 19 | 7 | 86.3661 | 18.041 | 0 | 2018-03-10 19:00 | 19 | 7 | 0 | 0 | 0 | 2018-03-10 19:00 | 19 | 7 | 87.0954 | 18.1934 | 0 | 2018-03-10 19:00 | 19 | 7 | 33.0963 | 6.9135 | 0
2018-03-10 20:00 | 20 | 7 | 86.1173 | 17.989 | 0 | 2018-03-10 20:00 | 20 | 7 | 0 | 0 | 0 | 2018-03-10 20:00 | 20 | 7 | 86.891 | 18.1507 | 0 | 2018-03-10 20:00 | 20 | 7 | 33.0186 | 6.8973 | 0
2018-03-10 21:00 | 21 | 7 | 86.1555 | 17.997 | 0 | 2018-03-10 21:00 | 21 | 7 | 0 | 0 | 0 | 2018-03-10 21:00 | 21 | 7 | 86.9245 | 18.1577 | 0 | 2018-03-10 21:00 | 21 | 7 | 33.0313 | 6.8999 | 0
2018-03-10 22:00 | 22 | 7 | 86.2211 | 18.0107 | 0 | 2018-03-10 22:00 | 22 | 7 | 0 | 0 | 0 | 2018-03-10 22:00 | 22 | 7 | 87.0054 | 18.1746 | 0 | 2018-03-10 22:00 | 22 | 7 | 33.0621 | 6.9063 | 0
2018-03-10 23:00 | 23 | 7 | 86.2226 | 18.011 | 0 | 2018-03-10 23:00 | 23 | 7 | 0 | 0 | 0 | 2018-03-10 23:00 | 23 | 7 | 87.0787 | 18.1899 | 0 | 2018-03-10 23:00 | 23 | 7 | 33.0899 | 6.9122 | 0
2018-03-11 | 0 | 1 | 86.2364 | 18.0139 | 0 | 2018-03-11 | 0 | 1 | 86.7994 | 18.1315 | 0 | 2018-03-11 | 0 | 1 | 0 | 0 | 0 | 2018-03-11 | 0 | 1 | 32.9838 | 6.89 | 0
2018-03-11 01:00 | 1 | 1 | 86.3188 | 18.0311 | 0 | 2018-03-11 01:00 | 1 | 1 | 86.952 | 18.1634 | 0 | 2018-03-11 01:00 | 1 | 1 | 0 | 0 | 0 | 2018-03-11 01:00 | 1 | 1 | 33.0418 | 6.9021 | 0
2018-03-11 02:00 | 2 | 1 | 86.2119 | 18.0088 | 0 | 2018-03-11 02:00 | 2 | 1 | 86.8177 | 18.1353 | 0 | 2018-03-11 02:00 | 2 | 1 | 0 | 0 | 0 | 2018-03-11 02:00 | 2 | 1 | 32.9907 | 6.8914 | 0
2018-03-11 03:00 | 3 | 1 | 86.1845 | 18.0031 | 0 | 2018-03-11 03:00 | 3 | 1 | 86.7857 | 18.1287 | 0 | 2018-03-11 03:00 | 3 | 1 | 0 | 0 | 0 | 2018-03-11 03:00 | 3 | 1 | 32.9786 | 6.8889 | 0
2018-03-11 04:00 | 4 | 1 | 86.2455 | 18.0158 | 0 | 2018-03-11 04:00 | 4 | 1 | 86.833 | 18.1385 | 0 | 2018-03-11 04:00 | 4 | 1 | 0 | 0 | 0 | 2018-03-11 04:00 | 4 | 1 | 32.9965 | 6.8926 | 0
2018-03-11 05:00 | 5 | 1 | 86.2333 | 18.0133 | 0 | 2018-03-11 05:00 | 5 | 1 | 86.833 | 18.1385 | 0 | 2018-03-11 05:00 | 5 | 1 | 0 | 0 | 0 | 2018-03-11 05:00 | 5 | 1 | 32.9965 | 6.8926 | 0
2018-03-11 06:00 | 6 | 1 | 86.2776 | 18.0225 | 0 | 2018-03-11 06:00 | 6 | 1 | 86.8528 | 18.1427 | 0 | 2018-03-11 06:00 | 6 | 1 | 0 | 0 | 0 | 2018-03-11 06:00 | 6 | 1 | 33.0041 | 6.8942 | 0
2018-03-11 07:00 | 7 | 1 | 86.2867 | 18.0244 | 0 | 2018-03-11 07:00 | 7 | 1 | 86.8452 | 18.1411 | 0 | 2018-03-11 07:00 | 7 | 1 | 0 | 0 | 0 | 2018-03-11 07:00 | 7 | 1 | 33.0012 | 6.8936 | 0
2018-03-11 08:00 | 8 | 1 | 86.2989 | 18.027 | 0 | 2018-03-11 08:00 | 8 | 1 | 86.9032 | 18.1532 | 0 | 2018-03-11 08:00 | 8 | 1 | 0 | 0 | 0 | 2018-03-11 08:00 | 8 | 1 | 33.0232 | 6.8982 | 0
2018-03-11 09:00 | 9 | 1 | 86.2867 | 18.0244 | 0 | 2018-03-11 09:00 | 9 | 1 | 86.8162 | 18.135 | 0 | 2018-03-11 09:00 | 9 | 1 | 0 | 0 | 0 | 2018-03-11 09:00 | 9 | 1 | 32.9902 | 6.8913 | 0
2018-03-11 10:00 | 10 | 1 | 86.2882 | 18.0247 | 0 | 2018-03-11 10:00 | 10 | 1 | 86.8528 | 18.1427 | 0 | 2018-03-11 10:00 | 10 | 1 | 0 | 0 | 0 | 2018-03-11 10:00 | 10 | 1 | 33.0041 | 6.8942 | 0
2018-03-11 11:00 | 11 | 1 | 86.1845 | 18.0031 | 0 | 2018-03-11 11:00 | 11 | 1 | 86.743 | 18.1197 | 0 | 2018-03-11 11:00 | 11 | 1 | 0 | 0 | 0 | 2018-03-11 11:00 | 11 | 1 | 32.9623 | 6.8855 | 0
2018-03-11 12:00 | 12 | 1 | 86.1418 | 17.9942 | 0 | 2018-03-11 12:00 | 12 | 1 | 86.714 | 18.1137 | 0 | 2018-03-11 12:00 | 12 | 1 | 0 | 0 | 0 | 2018-03-11 12:00 | 12 | 1 | 32.9513 | 6.8832 | 0
2018-03-11 13:00 | 13 | 1 | 86.1479 | 17.9954 | 0 | 2018-03-11 13:00 | 13 | 1 | 86.7659 | 18.1245 | 0 | 2018-03-11 13:00 | 13 | 1 | 0 | 0 | 0 | 2018-03-11 13:00 | 13 | 1 | 32.971 | 6.8873 | 0
2018-03-11 14:00 | 14 | 1 | 86.1112 | 17.9878 | 0 | 2018-03-11 14:00 | 14 | 1 | 86.7018 | 18.1111 | 0 | 2018-03-11 14:00 | 14 | 1 | 0 | 0 | 0 | 2018-03-11 14:00 | 14 | 1 | 32.9467 | 6.8822 | 0
2018-03-11 15:00 | 15 | 1 | 86.2455 | 18.0158 | 0 | 2018-03-11 15:00 | 15 | 1 | 86.8482 | 18.1417 | 0 | 2018-03-11 15:00 | 15 | 1 | 0 | 0 | 0 | 2018-03-11 15:00 | 15 | 1 | 33.0023 | 6.8939 | 0
2018-03-11 16:00 | 16 | 1 | 86.3447 | 18.0365 | 0 | 2018-03-11 16:00 | 16 | 1 | 86.9398 | 18.1609 | 0 | 2018-03-11 16:00 | 16 | 1 | 0 | 0 | 0 | 2018-03-11 16:00 | 16 | 1 | 33.0371 | 6.9011 | 0
2018-03-11 17:00 | 17 | 1 | 86.4805 | 18.0649 | 0 | 2018-03-11 17:00 | 17 | 1 | 86.9856 | 18.1704 | 0 | 2018-03-11 17:00 | 17 | 1 | 0 | 0 | 0 | 2018-03-11 17:00 | 17 | 1 | 33.0545 | 6.9048 | 0
2018-03-11 18:00 | 18 | 1 | 86.4332 | 18.055 | 0 | 2018-03-11 18:00 | 18 | 1 | 86.92 | 18.1567 | 0 | 2018-03-11 18:00 | 18 | 1 | 0 | 0 | 0 | 2018-03-11 18:00 | 18 | 1 | 33.0296 | 6.8996 | 0
2018-03-11 19:00 | 19 | 1 | 85.6794 | 17.8976 | 0 | 2018-03-11 19:00 | 19 | 1 | 85.9266 | 17.9492 | 0 | 2018-03-11 19:00 | 19 | 1 | 0 | 0 | 0 | 2018-03-11 19:00 | 19 | 1 | 32.6521 | 6.8207 | 0
2018-03-11 20:00 | 20 | 1 | 86.3294 | 18.0333 | 0 | 2018-03-11 20:00 | 20 | 1 | 86.5888 | 18.0875 | 0 | 2018-03-11 20:00 | 20 | 1 | 0 | 0 | 0 | 2018-03-11 20:00 | 20 | 1 | 32.9037 | 6.8733 | 0
2018-03-11 21:00 | 21 | 1 | 86.3569 | 18.0391 | 0 | 2018-03-11 21:00 | 21 | 1 | 86.6728 | 18.1051 | 0 | 2018-03-11 21:00 | 21 | 1 | 0 | 0 | 0 | 2018-03-11 21:00 | 21 | 1 | 32.9357 | 6.8799 | 0
2018-03-11 22:00 | 22 | 1 | 86.4881 | 18.0665 | 0 | 2018-03-11 22:00 | 22 | 1 | 86.8086 | 18.1334 | 0 | 2018-03-11 22:00 | 22 | 1 | 0 | 0 | 0 | 2018-03-11 22:00 | 22 | 1 | 32.9873 | 6.8907 | 0
2018-03-11 23:00 | 23 | 1 | 86.4332 | 18.055 | 0 | 2018-03-11 23:00 | 23 | 1 | 86.7353 | 18.1181 | 0 | 2018-03-11 23:00 | 23 | 1 | 0 | 0 | 0 | 2018-03-11 23:00 | 23 | 1 | 32.9594 | 6.8849 | 0
2018-03-12 | 0 | 2 | 86.4088 | 18.0499 | 0 | 2018-03-12 | 0 | 2 | 86.7002 | 18.1108 | 0 | 2018-03-12 | 0 | 2 | 86.9352 | 18.1599 | 0 | 2018-03-12 | 0 | 2 | 65.9815 | 13.7829 | 0
2018-03-12 01:00 | 1 | 2 | 86.0426 | 17.9734 | 0 | 2018-03-12 01:00 | 1 | 2 | 86.3127 | 18.0299 | 0 | 2018-03-12 01:00 | 1 | 2 | 86.5278 | 18.0748 | 0 | 2018-03-12 01:00 | 1 | 2 | 65.6794 | 13.7198 | 0
2018-03-12 02:00 | 2 | 2 | 86.392 | 18.0464 | 0 | 2018-03-12 02:00 | 2 | 2 | 86.6392 | 18.0981 | 0 | 2018-03-12 02:00 | 2 | 2 | 86.8421 | 18.1404 | 0 | 2018-03-12 02:00 | 2 | 2 | 65.9229 | 13.7706 | 0
2018-03-12 03:00 | 3 | 2 | 86.2776 | 18.0225 | 0 | 2018-03-12 03:00 | 3 | 2 | 86.5766 | 18.085 | 0 | 2018-03-12 03:00 | 3 | 2 | 86.7536 | 18.122 | 0 | 2018-03-12 03:00 | 3 | 2 | 65.8655 | 13.7586 | 0
2018-03-12 04:00 | 4 | 2 | 86.5034 | 18.0697 | 0 | 2018-03-12 04:00 | 4 | 2 | 86.8849 | 18.1494 | 0 | 2018-03-12 04:00 | 4 | 2 | 87.0283 | 18.1793 | 0 | 2018-03-12 04:00 | 4 | 2 | 66.087 | 13.8049 | 0
2018-03-12 05:00 | 5 | 2 | 86.3661 | 18.041 | 0 | 2018-03-12 05:00 | 5 | 2 | 86.772 | 18.1258 | 0 | 2018-03-12 05:00 | 5 | 2 | 87.0054 | 18.1746 | 0 | 2018-03-12 05:00 | 5 | 2 | 66.0354 | 13.7941 | 0
2018-03-12 06:00 | 6 | 2 | 86.2898 | 18.0251 | 0 | 2018-03-12 06:00 | 6 | 2 | 86.6499 | 18.1003 | 0 | 2018-03-12 06:00 | 6 | 2 | 86.8147 | 18.1347 | 0 | 2018-03-12 06:00 | 6 | 2 | 65.9165 | 13.7693 | 0
2018-03-12 07:00 | 7 | 2 | 86.2043 | 18.0072 | 0 | 2018-03-12 07:00 | 7 | 2 | 86.5278 | 18.0748 | 0 | 2018-03-12 07:00 | 7 | 2 | 86.7079 | 18.1124 | 0 | 2018-03-12 07:00 | 7 | 2 | 65.8296 | 13.7511 | 0
2018-03-12 08:00 | 8 | 2 | 86.3355 | 18.0346 | 0 | 2018-03-12 08:00 | 8 | 2 | 86.5461 | 18.0786 | 0 | 2018-03-12 08:00 | 8 | 2 | 86.8025 | 18.1322 | 0 | 2018-03-12 08:00 | 8 | 2 | 65.8725 | 13.7601 | 0
2018-03-12 09:00 | 9 | 2 | 86.3798 | 18.0439 | 0 | 2018-03-12 09:00 | 9 | 2 | 86.7262 | 18.1162 | 0 | 2018-03-12 09:00 | 9 | 2 | 86.8711 | 18.1465 | 0 | 2018-03-12 09:00 | 9 | 2 | 65.967 | 13.7798 | 0
2018-03-12 10:00 | 10 | 2 | 86.2272 | 18.012 | 0 | 2018-03-12 10:00 | 10 | 2 | 86.5156 | 18.0722 | 0 | 2018-03-12 10:00 | 10 | 2 | 86.714 | 18.1137 | 0 | 2018-03-12 10:00 | 10 | 2 | 65.8272 | 13.7507 | 0
2018-03-12 11:00 | 11 | 2 | 86.2119 | 18.0088 | 0 | 2018-03-12 11:00 | 11 | 2 | 86.5141 | 18.0719 | 0 | 2018-03-12 11:00 | 11 | 2 | 86.7201 | 18.115 | 0 | 2018-03-12 11:00 | 11 | 2 | 65.829 | 13.751 | 0
2018-03-12 12:00 | 12 | 2 | 86.389 | 18.0458 | 0 | 2018-03-12 12:00 | 12 | 2 | 86.6835 | 18.1073 | 0 | 2018-03-12 12:00 | 12 | 2 | 86.8574 | 18.1436 | 0 | 2018-03-12 12:00 | 12 | 2 | 65.9455 | 13.7754 | 0
2018-03-12 13:00 | 13 | 2 | 86.4027 | 18.0487 | 0 | 2018-03-12 13:00 | 13 | 2 | 86.6224 | 18.0946 | 0 | 2018-03-12 13:00 | 13 | 2 | 86.7475 | 18.1207 | 0 | 2018-03-12 13:00 | 13 | 2 | 65.8806 | 13.7618 | 0
2018-03-12 14:00 | 14 | 2 | 86.3783 | 18.0436 | 0 | 2018-03-12 14:00 | 14 | 2 | 86.6606 | 18.1025 | 0 | 2018-03-12 14:00 | 14 | 2 | 86.7903 | 18.1296 | 0 | 2018-03-12 14:00 | 14 | 2 | 65.9113 | 13.7682 | 0
2018-03-12 15:00 | 15 | 2 | 86.3355 | 18.0346 | 0 | 2018-03-12 15:00 | 15 | 2 | 86.5248 | 18.0742 | 0 | 2018-03-12 15:00 | 15 | 2 | 86.7384 | 18.1188 | 0 | 2018-03-12 15:00 | 15 | 2 | 65.84 | 13.7533 | 0
2018-03-12 16:00 | 16 | 2 | 86.3493 | 18.0375 | 0 | 2018-03-12 16:00 | 16 | 2 | 86.4912 | 18.0671 | 0 | 2018-03-12 16:00 | 16 | 2 | 86.685 | 18.1076 | 0 | 2018-03-12 16:00 | 16 | 2 | 65.807 | 13.7464 | 0
2018-03-12 17:00 | 17 | 2 | 86.244 | 18.0155 | 0 | 2018-03-12 17:00 | 17 | 2 | 86.4683 | 18.0624 | 0 | 2018-03-12 17:00 | 17 | 2 | 86.6743 | 18.1054 | 0 | 2018-03-12 17:00 | 17 | 2 | 65.7942 | 13.7437 | 0
2018-03-12 18:00 | 18 | 2 | 86.3142 | 18.0302 | 0 | 2018-03-12 18:00 | 18 | 2 | 86.4378 | 18.056 | 0 | 2018-03-12 18:00 | 18 | 2 | 86.5934 | 18.0885 | 0 | 2018-03-12 18:00 | 18 | 2 | 65.7519 | 13.7349 | 0
2018-03-12 19:00 | 19 | 2 | 86.2089 | 18.0082 | 0 | 2018-03-12 19:00 | 19 | 2 | 86.3508 | 18.0378 | 0 | 2018-03-12 19:00 | 19 | 2 | 86.5583 | 18.0812 | 0 | 2018-03-12 19:00 | 19 | 2 | 65.7055 | 13.7252 | 0
2018-03-12 20:00 | 20 | 2 | 86.2181 | 18.0101 | 0 | 2018-03-12 20:00 | 20 | 2 | 86.4836 | 18.0656 | 0 | 2018-03-12 20:00 | 20 | 2 | 86.6896 | 18.1086 | 0 | 2018-03-12 20:00 | 20 | 2 | 65.8058 | 13.7462 | 0
2018-03-12 21:00 | 21 | 2 | 86.1494 | 17.9957 | 0 | 2018-03-12 21:00 | 21 | 2 | 86.4759 | 18.064 | 0 | 2018-03-12 21:00 | 21 | 2 | 86.63 | 18.0961 | 0 | 2018-03-12 21:00 | 21 | 2 | 65.7802 | 13.7408 | 0
2018-03-12 22:00 | 22 | 2 | 86.2593 | 18.0187 | 0 | 2018-03-12 22:00 | 22 | 2 | 86.5522 | 18.0799 | 0 | 2018-03-12 22:00 | 22 | 2 | 86.6468 | 18.0997 | 0 | 2018-03-12 22:00 | 22 | 2 | 65.8156 | 13.7482 | 0
2018-03-12 23:00 | 23 | 2 | 86.4424 | 18.057 | 0 | 2018-03-12 23:00 | 23 | 2 | 86.8055 | 18.1328 | 0 | 2018-03-12 23:00 | 23 | 2 | 86.8864 | 18.1497 | 0 | 2018-03-12 23:00 | 23 | 2 | 66.0029 | 13.7874 | 0
2018-03-13 | 0 | 3 | 86.4637 | 18.0614 | 0 | 2018-03-13 | 0 | 3 | 0 | 0 | 0 | 2018-03-13 | 0 | 3 | 0 | 0 | 0 | 2018-03-13 | 0 | 3 | 0 | 0 | 0
2018-03-13 01:00 | 1 | 3 | 86.5629 | 18.0821 | 0 | 2018-03-13 01:00 | 1 | 3 | 0 | 0 | 0 | 2018-03-13 01:00 | 1 | 3 | 0 | 0 | 0 | 2018-03-13 01:00 | 1 | 3 | 0 | 0 | 0
2018-03-13 02:00 | 2 | 3 | 86.3706 | 18.042 | 0 | 2018-03-13 02:00 | 2 | 3 | 0 | 0 | 0 | 2018-03-13 02:00 | 2 | 3 | 0 | 0 | 0 | 2018-03-13 02:00 | 2 | 3 | 0 | 0 | 0
2018-03-13 03:00 | 3 | 3 | 86.3523 | 18.0381 | 0 | 2018-03-13 03:00 | 3 | 3 | 0 | 0 | 0 | 2018-03-13 03:00 | 3 | 3 | 0 | 0 | 0 | 2018-03-13 03:00 | 3 | 3 | 0 | 0 | 0
2018-03-13 04:00 | 4 | 3 | 86.3676 | 18.0413 | 0 | 2018-03-13 04:00 | 4 | 3 | 0 | 0 | 0 | 2018-03-13 04:00 | 4 | 3 | 0 | 0 | 0 | 2018-03-13 04:00 | 4 | 3 | 0 | 0 | 0
2018-03-13 05:00 | 5 | 3 | 86.4027 | 18.0487 | 0 | 2018-03-13 05:00 | 5 | 3 | 0 | 0 | 0 | 2018-03-13 05:00 | 5 | 3 | 0 | 0 | 0 | 2018-03-13 05:00 | 5 | 3 | 0 | 0 | 0
2018-03-13 06:00 | 6 | 3 | 86.4652 | 18.0617 | 0 | 2018-03-13 06:00 | 6 | 3 | 0 | 0 | 0 | 2018-03-13 06:00 | 6 | 3 | 0 | 0 | 0 | 2018-03-13 06:00 | 6 | 3 | 0 | 0 | 0
2018-03-13 07:00 | 7 | 3 | 86.4012 | 18.0483 | 0 | 2018-03-13 07:00 | 7 | 3 | 0 | 0 | 0 | 2018-03-13 07:00 | 7 | 3 | 0 | 0 | 0 | 2018-03-13 07:00 | 7 | 3 | 0 | 0 | 0
2018-03-13 08:00 | 8 | 3 | 86.4515 | 18.0589 | 0 | 2018-03-13 08:00 | 8 | 3 | 0 | 0 | 0 | 2018-03-13 08:00 | 8 | 3 | 0 | 0 | 0 | 2018-03-13 08:00 | 8 | 3 | 0 | 0 | 0
2018-03-13 09:00 | 9 | 3 | 86.2028 | 18.0069 | 0 | 2018-03-13 09:00 | 9 | 3 | 0 | 0 | 0 | 2018-03-13 09:00 | 9 | 3 | 0 | 0 | 0 | 2018-03-13 09:00 | 9 | 3 | 0 | 0 | 0
2018-03-13 10:00 | 10 | 3 | 86.2715 | 18.0213 | 0 | 2018-03-13 10:00 | 10 | 3 | 0 | 0 | 0 | 2018-03-13 10:00 | 10 | 3 | 0 | 0 | 0 | 2018-03-13 10:00 | 10 | 3 | 0 | 0 | 0
2018-03-13 11:00 | 11 | 3 | 86.7567 | 18.1226 | 0 | 2018-03-13 11:00 | 11 | 3 | 0 | 0 | 0 | 2018-03-13 11:00 | 11 | 3 | 0 | 0 | 0 | 2018-03-13 11:00 | 11 | 3 | 0 | 0 | 0
2018-03-13 12:00 | 12 | 3 | 86.6194 | 18.0939 | 0 | 2018-03-13 12:00 | 12 | 3 | 0 | 0 | 0 | 2018-03-13 12:00 | 12 | 3 | 0 | 0 | 0 | 2018-03-13 12:00 | 12 | 3 | 0 | 0 | 0
2018-03-13 13:00 | 13 | 3 | 86.6377 | 18.0977 | 0 | 2018-03-13 13:00 | 13 | 3 | 0 | 0 | 0 | 2018-03-13 13:00 | 13 | 3 | 0 | 0 | 0 | 2018-03-13 13:00 | 13 | 3 | 0 | 0 | 0
2018-03-13 14:00 | 14 | 3 | 86.8757 | 18.1475 | 0 | 2018-03-13 14:00 | 14 | 3 | 0 | 0 | 0 | 2018-03-13 14:00 | 14 | 3 | 0 | 0 | 0 | 2018-03-13 14:00 | 14 | 3 | 0 | 0 | 0
2018-03-13 15:00 | 15 | 3 | 86.7994 | 18.1315 | 0 | 2018-03-13 15:00 | 15 | 3 | 0 | 0 | 0 | 2018-03-13 15:00 | 15 | 3 | 0 | 0 | 0 | 2018-03-13 15:00 | 15 | 3 | 0 | 0 | 0
2018-03-13 16:00 | 16 | 3 | 86.7674 | 18.1248 | 0 | 2018-03-13 16:00 | 16 | 3 | 0 | 0 | 0 | 2018-03-13 16:00 | 16 | 3 | 0 | 0 | 0 | 2018-03-13 16:00 | 16 | 3 | 0 | 0 | 0
2018-03-13 17:00 | 17 | 3 | 86.7384 | 18.1188 | 0 | 2018-03-13 17:00 | 17 | 3 | 0 | 0 | 0 | 2018-03-13 17:00 | 17 | 3 | 0 | 0 | 0 | 2018-03-13 17:00 | 17 | 3 | 0 | 0 | 0
2018-03-13 18:00 | 18 | 3 | 86.7124 | 18.1134 | 0 | 2018-03-13 18:00 | 18 | 3 | 0 | 0 | 0 | 2018-03-13 18:00 | 18 | 3 | 0 | 0 | 0 | 2018-03-13 18:00 | 18 | 3 | 0 | 0 | 0
2018-03-13 19:00 | 19 | 3 | 86.8376 | 18.1395 | 0 | 2018-03-13 19:00 | 19 | 3 | 0 | 0 | 0 | 2018-03-13 19:00 | 19 | 3 | 0 | 0 | 0 | 2018-03-13 19:00 | 19 | 3 | 0 | 0 | 0
2018-03-13 20:00 | 20 | 3 | 86.627 | 18.0955 | 0 | 2018-03-13 20:00 | 20 | 3 | 0 | 0 | 0 | 2018-03-13 20:00 | 20 | 3 | 0 | 0 | 0 | 2018-03-13 20:00 | 20 | 3 | 0 | 0 | 0
2018-03-13 21:00 | 21 | 3 | 86.6239 | 18.0949 | 0 | 2018-03-13 21:00 | 21 | 3 | 0 | 0 | 0 | 2018-03-13 21:00 | 21 | 3 | 0 | 0 | 0 | 2018-03-13 21:00 | 21 | 3 | 0 | 0 | 0
2018-03-13 22:00 | 22 | 3 | 86.714 | 18.1137 | 0 | 2018-03-13 22:00 | 22 | 3 | 0 | 0 | 0 | 2018-03-13 22:00 | 22 | 3 | 0 | 0 | 0 | 2018-03-13 22:00 | 22 | 3 | 0 | 0 | 0
2018-03-13 23:00 | 23 | 3 | 86.8971 | 18.1519 | 0 | 2018-03-13 23:00 | 23 | 3 | 0 | 0 | 0 | 2018-03-13 23:00 | 23 | 3 | 0 | 0 | 0 | 2018-03-13 23:00 | 23 | 3 | 0 | 0 | 0
2018-03-14 | 0 | 4 | 0 | 0 | 0 | 2018-03-14 | 0 | 4 | 0 | 0 | 0 | 2018-03-14 | 0 | 4 | 86.6712 | 18.1047 | 0 | 2018-03-14 | 0 | 4 | 32.9351 | 6.8798 | 0
2018-03-14 01:00 | 1 | 4 | 0 | 0 | 0 | 2018-03-14 01:00 | 1 | 4 | 0 | 0 | 0 | 2018-03-14 01:00 | 1 | 4 | 86.511 | 18.0713 | 0 | 2018-03-14 01:00 | 1 | 4 | 32.8742 | 6.8671 | 0
2018-03-14 02:00 | 2 | 4 | 0 | 0 | 0 | 2018-03-14 02:00 | 2 | 4 | 0 | 0 | 0 | 2018-03-14 02:00 | 2 | 4 | 86.7628 | 18.1239 | 0 | 2018-03-14 02:00 | 2 | 4 | 32.9699 | 6.8871 | 0
2018-03-14 03:00 | 3 | 4 | 0 | 0 | 0 | 2018-03-14 03:00 | 3 | 4 | 0 | 0 | 0 | 2018-03-14 03:00 | 3 | 4 | 86.7384 | 18.1188 | 0 | 2018-03-14 03:00 | 3 | 4 | 32.9606 | 6.8851 | 0
2018-03-14 04:00 | 4 | 4 | 0 | 0 | 0 | 2018-03-14 04:00 | 4 | 4 | 0 | 0 | 0 | 2018-03-14 04:00 | 4 | 4 | 86.8376 | 18.1395 | 0 | 2018-03-14 04:00 | 4 | 4 | 32.9983 | 6.893 | 0
2018-03-14 05:00 | 5 | 4 | 0 | 0 | 0 | 2018-03-14 05:00 | 5 | 4 | 0 | 0 | 0 | 2018-03-14 05:00 | 5 | 4 | 87.0222 | 18.1781 | 0 | 2018-03-14 05:00 | 5 | 4 | 33.0684 | 6.9077 | 0
2018-03-14 06:00 | 6 | 4 | 0 | 0 | 0 | 2018-03-14 06:00 | 6 | 4 | 0 | 0 | 0 | 2018-03-14 06:00 | 6 | 4 | 86.9627 | 18.1656 | 0 | 2018-03-14 06:00 | 6 | 4 | 33.0458 | 6.9029 | 0
2018-03-14 07:00 | 7 | 4 | 0 | 0 | 0 | 2018-03-14 07:00 | 7 | 4 | 0 | 0 | 0 | 2018-03-14 07:00 | 7 | 4 | 87.1321 | 18.201 | 0 | 2018-03-14 07:00 | 7 | 4 | 33.1102 | 6.9164 | 0
2018-03-14 08:00 | 8 | 4 | 0 | 0 | 0 | 2018-03-14 08:00 | 8 | 4 | 0 | 0 | 0 | 2018-03-14 08:00 | 8 | 4 | 87.1931 | 18.2138 | 0 | 2018-03-14 08:00 | 8 | 4 | 33.1334 | 6.9212 | 0
2018-03-14 09:00 | 9 | 4 | 0 | 0 | 0 | 2018-03-14 09:00 | 9 | 4 | 0 | 0 | 0 | 2018-03-14 09:00 | 9 | 4 | 86.7155 | 18.114 | 0 | 2018-03-14 09:00 | 9 | 4 | 32.9519 | 6.8833 | 0
2018-03-14 10:00 | 10 | 4 | 0 | 0 | 0 | 2018-03-14 10:00 | 10 | 4 | 0 | 0 | 0 | 2018-03-14 10:00 | 10 | 4 | 86.6743 | 18.1054 | 0 | 2018-03-14 10:00 | 10 | 4 | 32.9362 | 6.88 | 0
2018-03-14 11:00 | 11 | 4 | 0 | 0 | 0 | 2018-03-14 11:00 | 11 | 4 | 0 | 0 | 0 | 2018-03-14 11:00 | 11 | 4 | 86.8956 | 18.1516 | 0 | 2018-03-14 11:00 | 11 | 4 | 33.0203 | 6.8976 | 0
2018-03-14 12:00 | 12 | 4 | 0 | 0 | 0 | 2018-03-14 12:00 | 12 | 4 | 0 | 0 | 0 | 2018-03-14 12:00 | 12 | 4 | 86.9276 | 18.1583 | 0 | 2018-03-14 12:00 | 12 | 4 | 33.0325 | 6.9002 | 0
2018-03-14 13:00 | 13 | 4 | 0 | 0 | 0 | 2018-03-14 13:00 | 13 | 4 | 0 | 0 | 0 | 2018-03-14 13:00 | 13 | 4 | 87.2541 | 18.2265 | 0 | 2018-03-14 13:00 | 13 | 4 | 33.1566 | 6.9261 | 0
2018-03-14 14:00 | 14 | 4 | 0 | 0 | 0 | 2018-03-14 14:00 | 14 | 4 | 0 | 0 | 0 | 2018-03-14 14:00 | 14 | 4 | 87.4037 | 18.2578 | 0 | 2018-03-14 14:00 | 14 | 4 | 33.2134 | 6.9379 | 0
2018-03-14 15:00 | 15 | 4 | 0 | 0 | 0 | 2018-03-14 15:00 | 15 | 4 | 0 | 0 | 0 | 2018-03-14 15:00 | 15 | 4 | 87.2129 | 18.2179 | 0 | 2018-03-14 15:00 | 15 | 4 | 33.1409 | 6.9228 | 0
2018-03-14 16:00 | 16 | 4 | 0 | 0 | 0 | 2018-03-14 16:00 | 16 | 4 | 0 | 0 | 0 | 2018-03-14 16:00 | 16 | 4 | 86.9718 | 18.1675 | 0 | 2018-03-14 16:00 | 16 | 4 | 33.0493 | 6.9037 | 0
2018-03-14 17:00 | 17 | 4 | 0 | 0 | 0 | 2018-03-14 17:00 | 17 | 4 | 0 | 0 | 0 | 2018-03-14 17:00 | 17 | 4 | 87.1397 | 18.2026 | 0 | 2018-03-14 17:00 | 17 | 4 | 33.1131 | 6.917 | 0
2018-03-14 18:00 | 18 | 4 | 0 | 0 | 0 | 2018-03-14 18:00 | 18 | 4 | 0 | 0 | 0 | 2018-03-14 18:00 | 18 | 4 | 87.2435 | 18.2243 | 0 | 2018-03-14 18:00 | 18 | 4 | 33.1525 | 6.9252 | 0
2018-03-14 19:00 | 19 | 4 | 0 | 0 | 0 | 2018-03-14 19:00 | 19 | 4 | 0 | 0 | 0 | 2018-03-14 19:00 | 19 | 4 | 86.8894 | 18.1503 | 0 | 2018-03-14 19:00 | 19 | 4 | 33.018 | 6.8971 | 0
2018-03-14 20:00 | 20 | 4 | 0 | 0 | 0 | 2018-03-14 20:00 | 20 | 4 | 0 | 0 | 0 | 2018-03-14 20:00 | 20 | 4 | 87.1839 | 18.2118 | 0 | 2018-03-14 20:00 | 20 | 4 | 33.1299 | 6.9205 | 0
2018-03-14 21:00 | 21 | 4 | 0 | 0 | 0 | 2018-03-14 21:00 | 21 | 4 | 0 | 0 | 0 | 2018-03-14 21:00 | 21 | 4 | 87.2419 | 18.224 | 0 | 2018-03-14 21:00 | 21 | 4 | 33.1519 | 6.9251 | 0
2018-03-14 22:00 | 22 | 4 | 0 | 0 | 0 | 2018-03-14 22:00 | 22 | 4 | 0 | 0 | 0 | 2018-03-14 22:00 | 22 | 4 | 87.1733 | 18.2096 | 0 | 2018-03-14 22:00 | 22 | 4 | 33.1259 | 6.9197 | 0
2018-03-14 23:00 | 23 | 4 | 0 | 0 | 0 | 2018-03-14 23:00 | 23 | 4 | 0 | 0 | 0 | 2018-03-14 23:00 | 23 | 4 | 87.2557 | 18.2268 | 0 | 2018-03-14 23:00 | 23 | 4 | 33.1572 | 6.9262 | 0
2018-03-15 | 0 | 5 | 86.5492 | 18.0793 | 0 | 2018-03-15 | 0 | 5 | 0 | 0 | 0 | 2018-03-15 | 0 | 5 | 0 | 0 | 0 | 2018-03-15 | 0 | 5 | 0 | 0 | 0
2018-03-15 01:00 | 1 | 5 | 86.7201 | 18.115 | 0 | 2018-03-15 01:00 | 1 | 5 | 0 | 0 | 0 | 2018-03-15 01:00 | 1 | 5 | 0 | 0 | 0 | 2018-03-15 01:00 | 1 | 5 | 0 | 0 | 0
2018-03-15 02:00 | 2 | 5 | 86.5095 | 18.071 | 0 | 2018-03-15 02:00 | 2 | 5 | 0 | 0 | 0 | 2018-03-15 02:00 | 2 | 5 | 0 | 0 | 0 | 2018-03-15 02:00 | 2 | 5 | 0 | 0 | 0
2018-03-15 03:00 | 3 | 5 | 86.4576 | 18.0601 | 0 | 2018-03-15 03:00 | 3 | 5 | 0 | 0 | 0 | 2018-03-15 03:00 | 3 | 5 | 0 | 0 | 0 | 2018-03-15 03:00 | 3 | 5 | 0 | 0 | 0
2018-03-15 04:00 | 4 | 5 | 86.6316 | 18.0965 | 0 | 2018-03-15 04:00 | 4 | 5 | 0 | 0 | 0 | 2018-03-15 04:00 | 4 | 5 | 0 | 0 | 0 | 2018-03-15 04:00 | 4 | 5 | 0 | 0 | 0
2018-03-15 05:00 | 5 | 5 | 86.569 | 18.0834 | 0 | 2018-03-15 05:00 | 5 | 5 | 0 | 0 | 0 | 2018-03-15 05:00 | 5 | 5 | 0 | 0 | 0 | 2018-03-15 05:00 | 5 | 5 | 0 | 0 | 0
2018-03-15 06:00 | 6 | 5 | 86.6468 | 18.0997 | 0 | 2018-03-15 06:00 | 6 | 5 | 0 | 0 | 0 | 2018-03-15 06:00 | 6 | 5 | 0 | 0 | 0 | 2018-03-15 06:00 | 6 | 5 | 0 | 0 | 0
2018-03-15 07:00 | 7 | 5 | 86.6361 | 18.0974 | 0 | 2018-03-15 07:00 | 7 | 5 | 0 | 0 | 0 | 2018-03-15 07:00 | 7 | 5 | 0 | 0 | 0 | 2018-03-15 07:00 | 7 | 5 | 0 | 0 | 0
2018-03-15 08:00 | 8 | 5 | 86.6819 | 18.107 | 0 | 2018-03-15 08:00 | 8 | 5 | 0 | 0 | 0 | 2018-03-15 08:00 | 8 | 5 | 0 | 0 | 0 | 2018-03-15 08:00 | 8 | 5 | 0 | 0 | 0
2018-03-15 09:00 | 9 | 5 | 86.7094 | 18.1127 | 0 | 2018-03-15 09:00 | 9 | 5 | 0 | 0 | 0 | 2018-03-15 09:00 | 9 | 5 | 0 | 0 | 0 | 2018-03-15 09:00 | 9 | 5 | 0 | 0 | 0
2018-03-15 10:00 | 10 | 5 | 86.7933 | 18.1303 | 0 | 2018-03-15 10:00 | 10 | 5 | 0 | 0 | 0 | 2018-03-15 10:00 | 10 | 5 | 0 | 0 | 0 | 2018-03-15 10:00 | 10 | 5 | 0 | 0 | 0
2018-03-15 11:00 | 11 | 5 | 86.8009 | 18.1318 | 0 | 2018-03-15 11:00 | 11 | 5 | 0 | 0 | 0 | 2018-03-15 11:00 | 11 | 5 | 0 | 0 | 0 | 2018-03-15 11:00 | 11 | 5 | 0 | 0 | 0
2018-03-15 12:00 | 12 | 5 | 86.6728 | 18.1051 | 0 | 2018-03-15 12:00 | 12 | 5 | 0 | 0 | 0 | 2018-03-15 12:00 | 12 | 5 | 0 | 0 | 0 | 2018-03-15 12:00 | 12 | 5 | 0 | 0 | 0
2018-03-15 13:00 | 13 | 5 | 86.6316 | 18.0965 | 0 | 2018-03-15 13:00 | 13 | 5 | 0 | 0 | 0 | 2018-03-15 13:00 | 13 | 5 | 0 | 0 | 0 | 2018-03-15 13:00 | 13 | 5 | 0 | 0 | 0
2018-03-15 14:00 | 14 | 5 | 86.6316 | 18.0965 | 0 | 2018-03-15 14:00 | 14 | 5 | 0 | 0 | 0 | 2018-03-15 14:00 | 14 | 5 | 0 | 0 | 0 | 2018-03-15 14:00 | 14 | 5 | 0 | 0 | 0
2018-03-15 15:00 | 15 | 5 | 86.6636 | 18.1032 | 0 | 2018-03-15 15:00 | 15 | 5 | 0 | 0 | 0 | 2018-03-15 15:00 | 15 | 5 | 0 | 0 | 0 | 2018-03-15 15:00 | 15 | 5 | 0 | 0 | 0
2018-03-15 16:00 | 16 | 5 | 86.5568 | 18.0808 | 0 | 2018-03-15 16:00 | 16 | 5 | 0 | 0 | 0 | 2018-03-15 16:00 | 16 | 5 | 0 | 0 | 0 | 2018-03-15 16:00 | 16 | 5 | 0 | 0 | 0
2018-03-15 17:00 | 17 | 5 | 86.6865 | 18.1079 | 0 | 2018-03-15 17:00 | 17 | 5 | 0 | 0 | 0 | 2018-03-15 17:00 | 17 | 5 | 0 | 0 | 0 | 2018-03-15 17:00 | 17 | 5 | 0 | 0 | 0
2018-03-15 18:00 | 18 | 5 | 86.7262 | 18.1162 | 0 | 2018-03-15 18:00 | 18 | 5 | 0 | 0 | 0 | 2018-03-15 18:00 | 18 | 5 | 0 | 0 | 0 | 2018-03-15 18:00 | 18 | 5 | 0 | 0 | 0
2018-03-15 19:00 | 19 | 5 | 86.5187 | 18.0729 | 0 | 2018-03-15 19:00 | 19 | 5 | 0 | 0 | 0 | 2018-03-15 19:00 | 19 | 5 | 0 | 0 | 0 | 2018-03-15 19:00 | 19 | 5 | 0 | 0 | 0
2018-03-15 20:00 | 20 | 5 | 86.5766 | 18.085 | 0 | 2018-03-15 20:00 | 20 | 5 | 0 | 0 | 0 | 2018-03-15 20:00 | 20 | 5 | 0 | 0 | 0 | 2018-03-15 20:00 | 20 | 5 | 0 | 0 | 0
2018-03-15 21:00 | 21 | 5 | 86.6194 | 18.0939 | 0 | 2018-03-15 21:00 | 21 | 5 | 0 | 0 | 0 | 2018-03-15 21:00 | 21 | 5 | 0 | 0 | 0 | 2018-03-15 21:00 | 21 | 5 | 0 | 0 | 0
2018-03-15 22:00 | 22 | 5 | 86.6743 | 18.1054 | 0 | 2018-03-15 22:00 | 22 | 5 | 0 | 0 | 0 | 2018-03-15 22:00 | 22 | 5 | 0 | 0 | 0 | 2018-03-15 22:00 | 22 | 5 | 0 | 0 | 0
2018-03-15 23:00 | 23 | 5 | 86.5644 | 18.0824 | 0 | 2018-03-15 23:00 | 23 | 5 | 0 | 0 | 0 | 2018-03-15 23:00 | 23 | 5 | 0 | 0 | 0 | 2018-03-15 23:00 | 23 | 5 | 0 | 0 | 0
2018-03-16 | 0 | 6 | 86.2226 | 18.011 | 0 | 2018-03-16 | 0 | 6 | 86.688 | 18.1083 | 0 | 2018-03-16 | 0 | 6 | 0 | 0 | 0 | 2018-03-16 | 0 | 6 | 32.9414 | 6.8811 | 0
2018-03-16 01:00 | 1 | 6 | 86.1128 | 17.9881 | 0 | 2018-03-16 01:00 | 1 | 6 | 86.5232 | 18.0738 | 0 | 2018-03-16 01:00 | 1 | 6 | 0 | 0 | 0 | 2018-03-16 01:00 | 1 | 6 | 32.8788 | 6.8681 | 0
2018-03-16 02:00 | 2 | 6 | 86.2791 | 18.0228 | 0 | 2018-03-16 02:00 | 2 | 6 | 86.6896 | 18.1086 | 0 | 2018-03-16 02:00 | 2 | 6 | 0 | 0 | 0 | 2018-03-16 02:00 | 2 | 6 | 32.942 | 6.8813 | 0
2018-03-16 03:00 | 3 | 6 | 86.0014 | 17.9648 | 0 | 2018-03-16 03:00 | 3 | 6 | 86.4485 | 18.0582 | 0 | 2018-03-16 03:00 | 3 | 6 | 0 | 0 | 0 | 2018-03-16 03:00 | 3 | 6 | 32.8504 | 6.8621 | 0
2018-03-16 04:00 | 4 | 6 | 86.0533 | 17.9757 | 0 | 2018-03-16 04:00 | 4 | 6 | 86.4347 | 18.0553 | 0 | 2018-03-16 04:00 | 4 | 6 | 0 | 0 | 0 | 2018-03-16 04:00 | 4 | 6 | 32.8452 | 6.861 | 0
2018-03-16 05:00 | 5 | 6 | 86.2257 | 18.0117 | 0 | 2018-03-16 05:00 | 5 | 6 | 86.6117 | 18.0923 | 0 | 2018-03-16 05:00 | 5 | 6 | 0 | 0 | 0 | 2018-03-16 05:00 | 5 | 6 | 32.9124 | 6.8751 | 0
2018-03-16 06:00 | 6 | 6 | 86.4332 | 18.055 | 0 | 2018-03-16 06:00 | 6 | 6 | 86.9352 | 18.1599 | 0 | 2018-03-16 06:00 | 6 | 6 | 0 | 0 | 0 | 2018-03-16 06:00 | 6 | 6 | 33.0354 | 6.9008 | 0
2018-03-16 07:00 | 7 | 6 | 86.5873 | 18.0872 | 0 | 2018-03-16 07:00 | 7 | 6 | 87.0619 | 18.1864 | 0 | 2018-03-16 07:00 | 7 | 6 | 0 | 0 | 0 | 2018-03-16 07:00 | 7 | 6 | 33.0835 | 6.9108 | 0
2018-03-16 08:00 | 8 | 6 | 86.3691 | 18.0416 | 0 | 2018-03-16 08:00 | 8 | 6 | 86.7811 | 18.1277 | 0 | 2018-03-16 08:00 | 8 | 6 | 0 | 0 | 0 | 2018-03-16 08:00 | 8 | 6 | 32.9768 | 6.8885 | 0
2018-03-16 09:00 | 9 | 6 | 86.334 | 18.0343 | 0 | 2018-03-16 09:00 | 9 | 6 | 86.7399 | 18.1191 | 0 | 2018-03-16 09:00 | 9 | 6 | 0 | 0 | 0 | 2018-03-16 09:00 | 9 | 6 | 32.9612 | 6.8853 | 0
2018-03-16 10:00 | 10 | 6 | 86.5126 | 18.0716 | 0 | 2018-03-16 10:00 | 10 | 6 | 86.862 | 18.1446 | 0 | 2018-03-16 10:00 | 10 | 6 | 0 | 0 | 0 | 2018-03-16 10:00 | 10 | 6 | 33.0076 | 6.8949 | 0
2018-03-16 11:00 | 11 | 6 | 86.5003 | 18.069 | 0 | 2018-03-16 11:00 | 11 | 6 | 86.9306 | 18.1589 | 0 | 2018-03-16 11:00 | 11 | 6 | 0 | 0 | 0 | 2018-03-16 11:00 | 11 | 6 | 33.0336 | 6.9004 | 0
2018-03-16 12:00 | 12 | 6 | 86.7002 | 18.1108 | 0 | 2018-03-16 12:00 | 12 | 6 | 87.1412 | 18.2029 | 0 | 2018-03-16 12:00 | 12 | 6 | 0 | 0 | 0 | 2018-03-16 12:00 | 12 | 6 | 33.1137 | 6.9171 | 0
2018-03-16 13:00 | 13 | 6 | 86.363 | 18.0404 | 0 | 2018-03-16 13:00 | 13 | 6 | 86.8009 | 18.1318 | 0 | 2018-03-16 13:00 | 13 | 6 | 0 | 0 | 0 | 2018-03-16 13:00 | 13 | 6 | 32.9843 | 6.8901 | 0
2018-03-16 14:00 | 14 | 6 | 86.4408 | 18.0566 | 0 | 2018-03-16 14:00 | 14 | 6 | 86.8635 | 18.1449 | 0 | 2018-03-16 14:00 | 14 | 6 | 0 | 0 | 0 | 2018-03-16 14:00 | 14 | 6 | 33.0081 | 6.8951 | 0
2018-03-16 15:00 | 15 | 6 | 86.2943 | 18.026 | 0 | 2018-03-16 15:00 | 15 | 6 | 86.6743 | 18.1054 | 0 | 2018-03-16 15:00 | 15 | 6 | 0 | 0 | 0 | 2018-03-16 15:00 | 15 | 6 | 32.9362 | 6.88 | 0
2018-03-16 16:00 | 16 | 6 | 86.3706 | 18.042 | 0 | 2018-03-16 16:00 | 16 | 6 | 86.7491 | 18.121 | 0 | 2018-03-16 16:00 | 16 | 6 | 0 | 0 | 0 | 2018-03-16 16:00 | 16 | 6 | 32.9647 | 6.886 | 0
2018-03-16 17:00 | 17 | 6 | 86.2882 | 18.0247 | 0 | 2018-03-16 17:00 | 17 | 6 | 86.7445 | 18.1201 | 0 | 2018-03-16 17:00 | 17 | 6 | 0 | 0 | 0 | 2018-03-16 17:00 | 17 | 6 | 32.9629 | 6.8856 | 0
2018-03-16 18:00 | 18 | 6 | 86.1875 | 18.0037 | 0 | 2018-03-16 18:00 | 18 | 6 | 86.6667 | 18.1038 | 0 | 2018-03-16 18:00 | 18 | 6 | 0 | 0 | 0 | 2018-03-16 18:00 | 18 | 6 | 32.9333 | 6.8794 | 0
2018-03-16 19:00 | 19 | 6 | 86.099 | 17.9852 | 0 | 2018-03-16 19:00 | 19 | 6 | 86.5431 | 18.078 | 0 | 2018-03-16 19:00 | 19 | 6 | 0 | 0 | 0 | 2018-03-16 19:00 | 19 | 6 | 32.8864 | 6.8696 | 0
2018-03-16 20:00 | 20 | 6 | 86.1997 | 18.0063 | 0 | 2018-03-16 20:00 | 20 | 6 | 86.5187 | 18.0729 | 0 | 2018-03-16 20:00 | 20 | 6 | 0 | 0 | 0 | 2018-03-16 20:00 | 20 | 6 | 32.8771 | 6.8677 | 0
2018-03-16 21:00 | 21 | 6 | 86.3767 | 18.0432 | 0 | 2018-03-16 21:00 | 21 | 6 | 86.7247 | 18.1159 | 0 | 2018-03-16 21:00 | 21 | 6 | 0 | 0 | 0 | 2018-03-16 21:00 | 21 | 6 | 32.9554 | 6.8841 | 0
2018-03-16 22:00 | 22 | 6 | 86.3691 | 18.0416 | 0 | 2018-03-16 22:00 | 22 | 6 | 86.7659 | 18.1245 | 0 | 2018-03-16 22:00 | 22 | 6 | 0 | 0 | 0 | 2018-03-16 22:00 | 22 | 6 | 32.971 | 6.8873 | 0
2018-03-16 23:00 | 23 | 6 | 86.4012 | 18.0483 | 0 | 2018-03-16 23:00 | 23 | 6 | 86.7918 | 18.1299 | 0 | 2018-03-16 23:00 | 23 | 6 | 0 | 0 | 0 | 2018-03-16 23:00 | 23 | 6 | 32.9809 | 6.8894 | 0
2018-03-17 | 0 | 7 | 86.0121 | 17.9671 | 0 | 2018-03-17 | 0 | 7 | 0 | 0 | 0 | 2018-03-17 | 0 | 7 | 86.5507 | 18.0796 | 0 | 2018-03-17 | 0 | 7 | 32.8893 | 6.8702 | 0
2018-03-17 01:00 | 1 | 7 | 85.919 | 17.9476 | 0 | 2018-03-17 01:00 | 1 | 7 | 0 | 0 | 0 | 2018-03-17 01:00 | 1 | 7 | 86.5324 | 18.0758 | 0 | 2018-03-17 01:00 | 1 | 7 | 32.8823 | 6.8688 | 0
2018-03-17 02:00 | 2 | 7 | 86.0533 | 17.9757 | 0 | 2018-03-17 02:00 | 2 | 7 | 0 | 0 | 0 | 2018-03-17 02:00 | 2 | 7 | 86.6453 | 18.0993 | 0 | 2018-03-17 02:00 | 2 | 7 | 32.9252 | 6.8777 | 0
2018-03-17 03:00 | 3 | 7 | 86.1677 | 17.9996 | 0 | 2018-03-17 03:00 | 3 | 7 | 0 | 0 | 0 | 2018-03-17 03:00 | 3 | 7 | 86.7002 | 18.1108 | 0 | 2018-03-17 03:00 | 3 | 7 | 32.9461 | 6.8821 | 0
2018-03-17 04:00 | 4 | 7 | 86.3081 | 18.0289 | 0 | 2018-03-17 04:00 | 4 | 7 | 0 | 0 | 0 | 2018-03-17 04:00 | 4 | 7 | 86.8513 | 18.1424 | 0 | 2018-03-17 04:00 | 4 | 7 | 33.0035 | 6.8941 | 0
2018-03-17 05:00 | 5 | 7 | 86.2562 | 18.0181 | 0 | 2018-03-17 05:00 | 5 | 7 | 0 | 0 | 0 | 2018-03-17 05:00 | 5 | 7 | 86.8605 | 18.1443 | 0 | 2018-03-17 05:00 | 5 | 7 | 33.007 | 6.8948 | 0
2018-03-17 06:00 | 6 | 7 | 86.1234 | 17.9903 | 0 | 2018-03-17 06:00 | 6 | 7 | 0 | 0 | 0 | 2018-03-17 06:00 | 6 | 7 | 86.6682 | 18.1041 | 0 | 2018-03-17 06:00 | 6 | 7 | 32.9339 | 6.8796 | 0
2018-03-17 07:00 | 7 | 7 | 86.1906 | 18.0044 | 0 | 2018-03-17 07:00 | 7 | 7 | 0 | 0 | 0 | 2018-03-17 07:00 | 7 | 7 | 86.7247 | 18.1159 | 0 | 2018-03-17 07:00 | 7 | 7 | 32.9554 | 6.8841 | 0
2018-03-17 08:00 | 8 | 7 | 86.36 | 18.0397 | 0 | 2018-03-17 08:00 | 8 | 7 | 0 | 0 | 0 | 2018-03-17 08:00 | 8 | 7 | 86.952 | 18.1634 | 0 | 2018-03-17 08:00 | 8 | 7 | 33.0418 | 6.9021 | 0
2018-03-17 09:00 | 9 | 7 | 86.4912 | 18.0671 | 0 | 2018-03-17 09:00 | 9 | 7 | 0 | 0 | 0 | 2018-03-17 09:00 | 9 | 7 | 87.0588 | 18.1857 | 0 | 2018-03-17 09:00 | 9 | 7 | 33.0823 | 6.9106 | 0
2018-03-17 10:00 | 10 | 7 | 86.1982 | 18.0059 | 0 | 2018-03-17 10:00 | 10 | 7 | 0 | 0 | 0 | 2018-03-17 10:00 | 10 | 7 | 86.6392 | 18.0981 | 0 | 2018-03-17 10:00 | 10 | 7 | 32.9229 | 6.8773 | 0
2018-03-17 11:00 | 11 | 7 | 86.1707 | 18.0002 | 0 | 2018-03-17 11:00 | 11 | 7 | 0 | 0 | 0 | 2018-03-17 11:00 | 11 | 7 | 86.8849 | 18.1494 | 0 | 2018-03-17 11:00 | 11 | 7 | 33.0163 | 6.8968 | 0
2018-03-17 12:00 | 12 | 7 | 86.5019 | 18.0694 | 0 | 2018-03-17 12:00 | 12 | 7 | 0 | 0 | 0 | 2018-03-17 12:00 | 12 | 7 | 87.1504 | 18.2048 | 0 | 2018-03-17 12:00 | 12 | 7 | 33.1172 | 6.9178 | 0
2018-03-17 13:00 | 13 | 7 | 86.6148 | 18.093 | 0 | 2018-03-17 13:00 | 13 | 7 | 0 | 0 | 0 | 2018-03-17 13:00 | 13 | 7 | 87.3167 | 18.2396 | 0 | 2018-03-17 13:00 | 13 | 7 | 33.1803 | 6.931 | 0
2018-03-17 14:00 | 14 | 7 | 86.4439 | 18.0573 | 0 | 2018-03-17 14:00 | 14 | 7 | 0 | 0 | 0 | 2018-03-17 14:00 | 14 | 7 | 87.0832 | 18.1908 | 0 | 2018-03-17 14:00 | 14 | 7 | 33.0916 | 6.9125 | 0
2018-03-17 15:00 | 15 | 7 | 86.5522 | 18.0799 | 0 | 2018-03-17 15:00 | 15 | 7 | 0 | 0 | 0 | 2018-03-17 15:00 | 15 | 7 | 87.2938 | 18.2348 | 0 | 2018-03-17 15:00 | 15 | 7 | 33.1716 | 6.9292 | 0
2018-03-17 16:00 | 16 | 7 | 86.5644 | 18.0824 | 0 | 2018-03-17 16:00 | 16 | 7 | 0 | 0 | 0 | 2018-03-17 16:00 | 16 | 7 | 87.3579 | 18.2482 | 0 | 2018-03-17 16:00 | 16 | 7 | 33.196 | 6.9343 | 0
2018-03-17 17:00 | 17 | 7 | 86.7445 | 18.1201 | 0 | 2018-03-17 17:00 | 17 | 7 | 0 | 0 | 0 | 2018-03-17 17:00 | 17 | 7 | 87.57 | 18.2925 | 0 | 2018-03-17 17:00 | 17 | 7 | 33.2766 | 6.9511 | 0
2018-03-17 18:00 | 18 | 7 | 86.4668 | 18.062 | 0 | 2018-03-17 18:00 | 18 | 7 | 0 | 0 | 0 | 2018-03-17 18:00 | 18 | 7 | 87.3014 | 18.2364 | 0 | 2018-03-17 18:00 | 18 | 7 | 33.1745 | 6.9298 | 0
2018-03-17 19:00 | 19 | 7 | 86.3661 | 18.041 | 0 | 2018-03-17 19:00 | 19 | 7 | 0 | 0 | 0 | 2018-03-17 19:00 | 19 | 7 | 87.0954 | 18.1934 | 0 | 2018-03-17 19:00 | 19 | 7 | 33.0963 | 6.9135 | 0
2018-03-17 20:00 | 20 | 7 | 86.1173 | 17.989 | 0 | 2018-03-17 20:00 | 20 | 7 | 0 | 0 | 0 | 2018-03-17 20:00 | 20 | 7 | 86.891 | 18.1507 | 0 | 2018-03-17 20:00 | 20 | 7 | 33.0186 | 6.8973 | 0
2018-03-17 21:00 | 21 | 7 | 86.1555 | 17.997 | 0 | 2018-03-17 21:00 | 21 | 7 | 0 | 0 | 0 | 2018-03-17 21:00 | 21 | 7 | 86.9245 | 18.1577 | 0 | 2018-03-17 21:00 | 21 | 7 | 33.0313 | 6.8999 | 0
2018-03-17 22:00 | 22 | 7 | 86.2211 | 18.0107 | 0 | 2018-03-17 22:00 | 22 | 7 | 0 | 0 | 0 | 2018-03-17 22:00 | 22 | 7 | 87.0054 | 18.1746 | 0 | 2018-03-17 22:00 | 22 | 7 | 33.0621 | 6.9063 | 0
2018-03-17 23:00 | 23 | 7 | 86.2226 | 18.011 | 0 | 2018-03-17 23:00 | 23 | 7 | 0 | 0 | 0 | 2018-03-17 23:00 | 23 | 7 | 87.0787 | 18.1899 | 0 | 2018-03-17 23:00 | 23 | 7 | 33.0899 | 6.9122 | 0
2018-03-18 | 0 | 1 | 86.2364 | 18.0139 | 0 | 2018-03-18 | 0 | 1 | 86.7994 | 18.1315 | 0 | 2018-03-18 | 0 | 1 | 0 | 0 | 0 | 2018-03-18 | 0 | 1 | 32.9838 | 6.89 | 0
2018-03-18 01:00 | 1 | 1 | 86.3188 | 18.0311 | 0 | 2018-03-18 01:00 | 1 | 1 | 86.952 | 18.1634 | 0 | 2018-03-18 01:00 | 1 | 1 | 0 | 0 | 0 | 2018-03-18 01:00 | 1 | 1 | 33.0418 | 6.9021 | 0
2018-03-18 02:00 | 2 | 1 | 86.2119 | 18.0088 | 0 | 2018-03-18 02:00 | 2 | 1 | 86.8177 | 18.1353 | 0 | 2018-03-18 02:00 | 2 | 1 | 0 | 0 | 0 | 2018-03-18 02:00 | 2 | 1 | 32.9907 | 6.8914 | 0
2018-03-18 03:00 | 3 | 1 | 86.1845 | 18.0031 | 0 | 2018-03-18 03:00 | 3 | 1 | 86.7857 | 18.1287 | 0 | 2018-03-18 03:00 | 3 | 1 | 0 | 0 | 0 | 2018-03-18 03:00 | 3 | 1 | 32.9786 | 6.8889 | 0
2018-03-18 04:00 | 4 | 1 | 86.2455 | 18.0158 | 0 | 2018-03-18 04:00 | 4 | 1 | 86.833 | 18.1385 | 0 | 2018-03-18 04:00 | 4 | 1 | 0 | 0 | 0 | 2018-03-18 04:00 | 4 | 1 | 32.9965 | 6.8926 | 0
2018-03-18 05:00 | 5 | 1 | 86.2333 | 18.0133 | 0 | 2018-03-18 05:00 | 5 | 1 | 86.833 | 18.1385 | 0 | 2018-03-18 05:00 | 5 | 1 | 0 | 0 | 0 | 2018-03-18 05:00 | 5 | 1 | 32.9965 | 6.8926 | 0
2018-03-18 06:00 | 6 | 1 | 86.2776 | 18.0225 | 0 | 2018-03-18 06:00 | 6 | 1 | 86.8528 | 18.1427 | 0 | 2018-03-18 06:00 | 6 | 1 | 0 | 0 | 0 | 2018-03-18 06:00 | 6 | 1 | 33.0041 | 6.8942 | 0
2018-03-18 07:00 | 7 | 1 | 86.2867 | 18.0244 | 0 | 2018-03-18 07:00 | 7 | 1 | 86.8452 | 18.1411 | 0 | 2018-03-18 07:00 | 7 | 1 | 0 | 0 | 0 | 2018-03-18 07:00 | 7 | 1 | 33.0012 | 6.8936 | 0
2018-03-18 08:00 | 8 | 1 | 86.2989 | 18.027 | 0 | 2018-03-18 08:00 | 8 | 1 | 86.9032 | 18.1532 | 0 | 2018-03-18 08:00 | 8 | 1 | 0 | 0 | 0 | 2018-03-18 08:00 | 8 | 1 | 33.0232 | 6.8982 | 0
2018-03-18 09:00 | 9 | 1 | 86.2867 | 18.0244 | 0 | 2018-03-18 09:00 | 9 | 1 | 86.8162 | 18.135 | 0 | 2018-03-18 09:00 | 9 | 1 | 0 | 0 | 0 | 2018-03-18 09:00 | 9 | 1 | 32.9902 | 6.8913 | 0
2018-03-18 10:00 | 10 | 1 | 86.2882 | 18.0247 | 0 | 2018-03-18 10:00 | 10 | 1 | 86.8528 | 18.1427 | 0 | 2018-03-18 10:00 | 10 | 1 | 0 | 0 | 0 | 2018-03-18 10:00 | 10 | 1 | 33.0041 | 6.8942 | 0
2018-03-18 11:00 | 11 | 1 | 86.1845 | 18.0031 | 0 | 2018-03-18 11:00 | 11 | 1 | 86.743 | 18.1197 | 0 | 2018-03-18 11:00 | 11 | 1 | 0 | 0 | 0 | 2018-03-18 11:00 | 11 | 1 | 32.9623 | 6.8855 | 0
2018-03-18 12:00 | 12 | 1 | 86.1418 | 17.9942 | 0 | 2018-03-18 12:00 | 12 | 1 | 86.714 | 18.1137 | 0 | 2018-03-18 12:00 | 12 | 1 | 0 | 0 | 0 | 2018-03-18 12:00 | 12 | 1 | 32.9513 | 6.8832 | 0
2018-03-18 13:00 | 13 | 1 | 86.1479 | 17.9954 | 0 | 2018-03-18 13:00 | 13 | 1 | 86.7659 | 18.1245 | 0 | 2018-03-18 13:00 | 13 | 1 | 0 | 0 | 0 | 2018-03-18 13:00 | 13 | 1 | 32.971 | 6.8873 | 0
2018-03-18 14:00 | 14 | 1 | 86.1112 | 17.9878 | 0 | 2018-03-18 14:00 | 14 | 1 | 86.7018 | 18.1111 | 0 | 2018-03-18 14:00 | 14 | 1 | 0 | 0 | 0 | 2018-03-18 14:00 | 14 | 1 | 32.9467 | 6.8822 | 0
2018-03-18 15:00 | 15 | 1 | 86.2455 | 18.0158 | 0 | 2018-03-18 15:00 | 15 | 1 | 86.8482 | 18.1417 | 0 | 2018-03-18 15:00 | 15 | 1 | 0 | 0 | 0 | 2018-03-18 15:00 | 15 | 1 | 33.0023 | 6.8939 | 0
2018-03-18 16:00 | 16 | 1 | 86.3447 | 18.0365 | 0 | 2018-03-18 16:00 | 16 | 1 | 86.9398 | 18.1609 | 0 | 2018-03-18 16:00 | 16 | 1 | 0 | 0 | 0 | 2018-03-18 16:00 | 16 | 1 | 33.0371 | 6.9011 | 0
2018-03-18 17:00 | 17 | 1 | 86.4805 | 18.0649 | 0 | 2018-03-18 17:00 | 17 | 1 | 86.9856 | 18.1704 | 0 | 2018-03-18 17:00 | 17 | 1 | 0 | 0 | 0 | 2018-03-18 17:00 | 17 | 1 | 33.0545 | 6.9048 | 0
2018-03-18 18:00 | 18 | 1 | 86.4332 | 18.055 | 0 | 2018-03-18 18:00 | 18 | 1 | 86.92 | 18.1567 | 0 | 2018-03-18 18:00 | 18 | 1 | 0 | 0 | 0 | 2018-03-18 18:00 | 18 | 1 | 33.0296 | 6.8996 | 0
2018-03-18 19:00 | 19 | 1 | 85.6794 | 17.8976 | 0 | 2018-03-18 19:00 | 19 | 1 | 85.9266 | 17.9492 | 0 | 2018-03-18 19:00 | 19 | 1 | 0 | 0 | 0 | 2018-03-18 19:00 | 19 | 1 | 32.6521 | 6.8207 | 0
2018-03-18 20:00 | 20 | 1 | 86.3294 | 18.0333 | 0 | 2018-03-18 20:00 | 20 | 1 | 86.5888 | 18.0875 | 0 | 2018-03-18 20:00 | 20 | 1 | 0 | 0 | 0 | 2018-03-18 20:00 | 20 | 1 | 32.9037 | 6.8733 | 0
2018-03-18 21:00 | 21 | 1 | 86.3569 | 18.0391 | 0 | 2018-03-18 21:00 | 21 | 1 | 86.6728 | 18.1051 | 0 | 2018-03-18 21:00 | 21 | 1 | 0 | 0 | 0 | 2018-03-18 21:00 | 21 | 1 | 32.9357 | 6.8799 | 0
2018-03-18 22:00 | 22 | 1 | 86.4881 | 18.0665 | 0 | 2018-03-18 22:00 | 22 | 1 | 86.8086 | 18.1334 | 0 | 2018-03-18 22:00 | 22 | 1 | 0 | 0 | 0 | 2018-03-18 22:00 | 22 | 1 | 32.9873 | 6.8907 | 0
2018-03-18 23:00 | 23 | 1 | 86.4332 | 18.055 | 0 | 2018-03-18 23:00 | 23 | 1 | 86.7353 | 18.1181 | 0 | 2018-03-18 23:00 | 23 | 1 | 0 | 0 | 0 | 2018-03-18 23:00 | 23 | 1 | 32.9594 | 6.8849 | 0
2018-03-19 | 0 | 2 | 86.4088 | 18.0499 | 0 | 2018-03-19 | 0 | 2 | 86.7002 | 18.1108 | 0 | 2018-03-19 | 0 | 2 | 86.9352 | 18.1599 | 0 | 2018-03-19 | 0 | 2 | 65.9815 | 13.7829 | 0
2018-03-19 01:00 | 1 | 2 | 86.0426 | 17.9734 | 0 | 2018-03-19 01:00 | 1 | 2 | 86.3127 | 18.0299 | 0 | 2018-03-19 01:00 | 1 | 2 | 86.5278 | 18.0748 | 0 | 2018-03-19 01:00 | 1 | 2 | 65.6794 | 13.7198 | 0
2018-03-19 02:00 | 2 | 2 | 86.392 | 18.0464 | 0 | 2018-03-19 02:00 | 2 | 2 | 86.6392 | 18.0981 | 0 | 2018-03-19 02:00 | 2 | 2 | 86.8421 | 18.1404 | 0 | 2018-03-19 02:00 | 2 | 2 | 65.9229 | 13.7706 | 0
2018-03-19 03:00 | 3 | 2 | 86.2776 | 18.0225 | 0 | 2018-03-19 03:00 | 3 | 2 | 86.5766 | 18.085 | 0 | 2018-03-19 03:00 | 3 | 2 | 86.7536 | 18.122 | 0 | 2018-03-19 03:00 | 3 | 2 | 65.8655 | 13.7586 | 0
2018-03-19 04:00 | 4 | 2 | 86.5034 | 18.0697 | 0 | 2018-03-19 04:00 | 4 | 2 | 86.8849 | 18.1494 | 0 | 2018-03-19 04:00 | 4 | 2 | 87.0283 | 18.1793 | 0 | 2018-03-19 04:00 | 4 | 2 | 66.087 | 13.8049 | 0
2018-03-19 05:00 | 5 | 2 | 86.3661 | 18.041 | 0 | 2018-03-19 05:00 | 5 | 2 | 86.772 | 18.1258 | 0 | 2018-03-19 05:00 | 5 | 2 | 87.0054 | 18.1746 | 0 | 2018-03-19 05:00 | 5 | 2 | 66.0354 | 13.7941 | 0
2018-03-19 06:00 | 6 | 2 | 86.2898 | 18.0251 | 0 | 2018-03-19 06:00 | 6 | 2 | 86.6499 | 18.1003 | 0 | 2018-03-19 06:00 | 6 | 2 | 86.8147 | 18.1347 | 0 | 2018-03-19 06:00 | 6 | 2 | 65.9165 | 13.7693 | 0
2018-03-19 07:00 | 7 | 2 | 86.2043 | 18.0072 | 0 | 2018-03-19 07:00 | 7 | 2 | 86.5278 | 18.0748 | 0 | 2018-03-19 07:00 | 7 | 2 | 86.7079 | 18.1124 | 0 | 2018-03-19 07:00 | 7 | 2 | 65.8296 | 13.7511 | 0
2018-03-19 08:00 | 8 | 2 | 86.3355 | 18.0346 | 0 | 2018-03-19 08:00 | 8 | 2 | 86.5461 | 18.0786 | 0 | 2018-03-19 08:00 | 8 | 2 | 86.8025 | 18.1322 | 0 | 2018-03-19 08:00 | 8 | 2 | 65.8725 | 13.7601 | 0
2018-03-19 09:00 | 9 | 2 | 86.3798 | 18.0439 | 0 | 2018-03-19 09:00 | 9 | 2 | 86.7262 | 18.1162 | 0 | 2018-03-19 09:00 | 9 | 2 | 86.8711 | 18.1465 | 0 | 2018-03-19 09:00 | 9 | 2 | 65.967 | 13.7798 | 0
2018-03-19 10:00 | 10 | 2 | 86.2272 | 18.012 | 0 | 2018-03-19 10:00 | 10 | 2 | 86.5156 | 18.0722 | 0 | 2018-03-19 10:00 | 10 | 2 | 86.714 | 18.1137 | 0 | 2018-03-19 10:00 | 10 | 2 | 65.8272 | 13.7507 | 0
2018-03-19 11:00 | 11 | 2 | 86.2119 | 18.0088 | 0 | 2018-03-19 11:00 | 11 | 2 | 86.5141 | 18.0719 | 0 | 2018-03-19 11:00 | 11 | 2 | 86.7201 | 18.115 | 0 | 2018-03-19 11:00 | 11 | 2 | 65.829 | 13.751 | 0
2018-03-19 12:00 | 12 | 2 | 86.389 | 18.0458 | 0 | 2018-03-19 12:00 | 12 | 2 | 86.6835 | 18.1073 | 0 | 2018-03-19 12:00 | 12 | 2 | 86.8574 | 18.1436 | 0 | 2018-03-19 12:00 | 12 | 2 | 65.9455 | 13.7754 | 0
2018-03-19 13:00 | 13 | 2 | 86.4027 | 18.0487 | 0 | 2018-03-19 13:00 | 13 | 2 | 86.6224 | 18.0946 | 0 | 2018-03-19 13:00 | 13 | 2 | 86.7475 | 18.1207 | 0 | 2018-03-19 13:00 | 13 | 2 | 65.8806 | 13.7618 | 0
2018-03-19 14:00 | 14 | 2 | 86.3783 | 18.0436 | 0 | 2018-03-19 14:00 | 14 | 2 | 86.6606 | 18.1025 | 0 | 2018-03-19 14:00 | 14 | 2 | 86.7903 | 18.1296 | 0 | 2018-03-19 14:00 | 14 | 2 | 65.9113 | 13.7682 | 0
2018-03-19 15:00 | 15 | 2 | 86.3355 | 18.0346 | 0 | 2018-03-19 15:00 | 15 | 2 | 86.5248 | 18.0742 | 0 | 2018-03-19 15:00 | 15 | 2 | 86.7384 | 18.1188 | 0 | 2018-03-19 15:00 | 15 | 2 | 65.84 | 13.7533 | 0
2018-03-19 16:00 | 16 | 2 | 86.3493 | 18.0375 | 0 | 2018-03-19 16:00 | 16 | 2 | 86.4912 | 18.0671 | 0 | 2018-03-19 16:00 | 16 | 2 | 86.685 | 18.1076 | 0 | 2018-03-19 16:00 | 16 | 2 | 65.807 | 13.7464 | 0
2018-03-19 17:00 | 17 | 2 | 86.244 | 18.0155 | 0 | 2018-03-19 17:00 | 17 | 2 | 86.4683 | 18.0624 | 0 | 2018-03-19 17:00 | 17 | 2 | 86.6743 | 18.1054 | 0 | 2018-03-19 17:00 | 17 | 2 | 65.7942 | 13.7437 | 0
2018-03-19 18:00 | 18 | 2 | 86.3142 | 18.0302 | 0 | 2018-03-19 18:00 | 18 | 2 | 86.4378 | 18.056 | 0 | 2018-03-19 18:00 | 18 | 2 | 86.5934 | 18.0885 | 0 | 2018-03-19 18:00 | 18 | 2 | 65.7519 | 13.7349 | 0
2018-03-19 19:00 | 19 | 2 | 86.2089 | 18.0082 | 0 | 2018-03-19 19:00 | 19 | 2 | 86.3508 | 18.0378 | 0 | 2018-03-19 19:00 | 19 | 2 | 86.5583 | 18.0812 | 0 | 2018-03-19 19:00 | 19 | 2 | 65.7055 | 13.7252 | 0
2018-03-19 20:00 | 20 | 2 | 86.2181 | 18.0101 | 0 | 2018-03-19 20:00 | 20 | 2 | 86.4836 | 18.0656 | 0 | 2018-03-19 20:00 | 20 | 2 | 86.6896 | 18.1086 | 0 | 2018-03-19 20:00 | 20 | 2 | 65.8058 | 13.7462 | 0
2018-03-19 21:00 | 21 | 2 | 86.1494 | 17.9957 | 0 | 2018-03-19 21:00 | 21 | 2 | 86.4759 | 18.064 | 0 | 2018-03-19 21:00 | 21 | 2 | 86.63 | 18.0961 | 0 | 2018-03-19 21:00 | 21 | 2 | 65.7802 | 13.7408 | 0
2018-03-19 22:00 | 22 | 2 | 86.2593 | 18.0187 | 0 | 2018-03-19 22:00 | 22 | 2 | 86.5522 | 18.0799 | 0 | 2018-03-19 22:00 | 22 | 2 | 86.6468 | 18.0997 | 0 | 2018-03-19 22:00 | 22 | 2 | 65.8156 | 13.7482 | 0
2018-03-19 23:00 | 23 | 2 | 86.4424 | 18.057 | 0 | 2018-03-19 23:00 | 23 | 2 | 86.8055 | 18.1328 | 0 | 2018-03-19 23:00 | 23 | 2 | 86.8864 | 18.1497 | 0 | 2018-03-19 23:00 | 23 | 2 | 66.0029 | 13.7874 | 0
2018-03-20 | 0 | 3 | 86.4637 | 18.0614 | 0 | 2018-03-20 | 0 | 3 | 0 | 0 | 0 | 2018-03-20 | 0 | 3 | 0 | 0 | 0 | 2018-03-20 | 0 | 3 | 0 | 0 | 0
2018-03-20 01:00 | 1 | 3 | 86.5629 | 18.0821 | 0 | 2018-03-20 01:00 | 1 | 3 | 0 | 0 | 0 | 2018-03-20 01:00 | 1 | 3 | 0 | 0 | 0 | 2018-03-20 01:00 | 1 | 3 | 0 | 0 | 0
2018-03-20 02:00 | 2 | 3 | 86.3706 | 18.042 | 0 | 2018-03-20 02:00 | 2 | 3 | 0 | 0 | 0 | 2018-03-20 02:00 | 2 | 3 | 0 | 0 | 0 | 2018-03-20 02:00 | 2 | 3 | 0 | 0 | 0
2018-03-20 03:00 | 3 | 3 | 86.3523 | 18.0381 | 0 | 2018-03-20 03:00 | 3 | 3 | 0 | 0 | 0 | 2018-03-20 03:00 | 3 | 3 | 0 | 0 | 0 | 2018-03-20 03:00 | 3 | 3 | 0 | 0 | 0
2018-03-20 04:00 | 4 | 3 | 86.3676 | 18.0413 | 0 | 2018-03-20 04:00 | 4 | 3 | 0 | 0 | 0 | 2018-03-20 04:00 | 4 | 3 | 0 | 0 | 0 | 2018-03-20 04:00 | 4 | 3 | 0 | 0 | 0
2018-03-20 05:00 | 5 | 3 | 86.4027 | 18.0487 | 0 | 2018-03-20 05:00 | 5 | 3 | 0 | 0 | 0 | 2018-03-20 05:00 | 5 | 3 | 0 | 0 | 0 | 2018-03-20 05:00 | 5 | 3 | 0 | 0 | 0
2018-03-20 06:00 | 6 | 3 | 86.4652 | 18.0617 | 0 | 2018-03-20 06:00 | 6 | 3 | 0 | 0 | 0 | 2018-03-20 06:00 | 6 | 3 | 0 | 0 | 0 | 2018-03-20 06:00 | 6 | 3 | 0 | 0 | 0
2018-03-20 07:00 | 7 | 3 | 86.4012 | 18.0483 | 0 | 2018-03-20 07:00 | 7 | 3 | 0 | 0 | 0 | 2018-03-20 07:00 | 7 | 3 | 0 | 0 | 0 | 2018-03-20 07:00 | 7 | 3 | 0 | 0 | 0
2018-03-20 08:00 | 8 | 3 | 86.4515 | 18.0589 | 0 | 2018-03-20 08:00 | 8 | 3 | 0 | 0 | 0 | 2018-03-20 08:00 | 8 | 3 | 0 | 0 | 0 | 2018-03-20 08:00 | 8 | 3 | 0 | 0 | 0
2018-03-20 09:00 | 9 | 3 | 86.2028 | 18.0069 | 0 | 2018-03-20 09:00 | 9 | 3 | 0 | 0 | 0 | 2018-03-20 09:00 | 9 | 3 | 0 | 0 | 0 | 2018-03-20 09:00 | 9 | 3 | 0 | 0 | 0
2018-03-20 10:00 | 10 | 3 | 86.2715 | 18.0213 | 0 | 2018-03-20 10:00 | 10 | 3 | 0 | 0 | 0 | 2018-03-20 10:00 | 10 | 3 | 0 | 0 | 0 | 2018-03-20 10:00 | 10 | 3 | 0 | 0 | 0
2018-03-20 11:00 | 11 | 3 | 86.7567 | 18.1226 | 0 | 2018-03-20 11:00 | 11 | 3 | 0 | 0 | 0 | 2018-03-20 11:00 | 11 | 3 | 0 | 0 | 0 | 2018-03-20 11:00 | 11 | 3 | 0 | 0 | 0
2018-03-20 12:00 | 12 | 3 | 86.6194 | 18.0939 | 0 | 2018-03-20 12:00 | 12 | 3 | 0 | 0 | 0 | 2018-03-20 12:00 | 12 | 3 | 0 | 0 | 0 | 2018-03-20 12:00 | 12 | 3 | 0 | 0 | 0
2018-03-20 13:00 | 13 | 3 | 86.6377 | 18.0977 | 0 | 2018-03-20 13:00 | 13 | 3 | 0 | 0 | 0 | 2018-03-20 13:00 | 13 | 3 | 0 | 0 | 0 | 2018-03-20 13:00 | 13 | 3 | 0 | 0 | 0
2018-03-20 14:00 | 14 | 3 | 86.8757 | 18.1475 | 0 | 2018-03-20 14:00 | 14 | 3 | 0 | 0 | 0 | 2018-03-20 14:00 | 14 | 3 | 0 | 0 | 0 | 2018-03-20 14:00 | 14 | 3 | 0 | 0 | 0
2018-03-20 15:00 | 15 | 3 | 86.7994 | 18.1315 | 0 | 2018-03-20 15:00 | 15 | 3 | 0 | 0 | 0 | 2018-03-20 15:00 | 15 | 3 | 0 | 0 | 0 | 2018-03-20 15:00 | 15 | 3 | 0 | 0 | 0
2018-03-20 16:00 | 16 | 3 | 86.7674 | 18.1248 | 0 | 2018-03-20 16:00 | 16 | 3 | 0 | 0 | 0 | 2018-03-20 16:00 | 16 | 3 | 0 | 0 | 0 | 2018-03-20 16:00 | 16 | 3 | 0 | 0 | 0
2018-03-20 17:00 | 17 | 3 | 86.7384 | 18.1188 | 0 | 2018-03-20 17:00 | 17 | 3 | 0 | 0 | 0 | 2018-03-20 17:00 | 17 | 3 | 0 | 0 | 0 | 2018-03-20 17:00 | 17 | 3 | 0 | 0 | 0
2018-03-20 18:00 | 18 | 3 | 86.7124 | 18.1134 | 0 | 2018-03-20 18:00 | 18 | 3 | 0 | 0 | 0 | 2018-03-20 18:00 | 18 | 3 | 0 | 0 | 0 | 2018-03-20 18:00 | 18 | 3 | 0 | 0 | 0
2018-03-20 19:00 | 19 | 3 | 86.8376 | 18.1395 | 0 | 2018-03-20 19:00 | 19 | 3 | 0 | 0 | 0 | 2018-03-20 19:00 | 19 | 3 | 0 | 0 | 0 | 2018-03-20 19:00 | 19 | 3 | 0 | 0 | 0
2018-03-20 20:00 | 20 | 3 | 86.627 | 18.0955 | 0 | 2018-03-20 20:00 | 20 | 3 | 0 | 0 | 0 | 2018-03-20 20:00 | 20 | 3 | 0 | 0 | 0 | 2018-03-20 20:00 | 20 | 3 | 0 | 0 | 0
2018-03-20 21:00 | 21 | 3 | 86.6239 | 18.0949 | 0 | 2018-03-20 21:00 | 21 | 3 | 0 | 0 | 0 | 2018-03-20 21:00 | 21 | 3 | 0 | 0 | 0 | 2018-03-20 21:00 | 21 | 3 | 0 | 0 | 0
2018-03-20 22:00 | 22 | 3 | 86.714 | 18.1137 | 0 | 2018-03-20 22:00 | 22 | 3 | 0 | 0 | 0 | 2018-03-20 22:00 | 22 | 3 | 0 | 0 | 0 | 2018-03-20 22:00 | 22 | 3 | 0 | 0 | 0
2018-03-20 23:00 | 23 | 3 | 86.8971 | 18.1519 | 0 | 2018-03-20 23:00 | 23 | 3 | 0 | 0 | 0 | 2018-03-20 23:00 | 23 | 3 | 0 | 0 | 0 | 2018-03-20 23:00 | 23 | 3 | 0 | 0 | 0
2018-03-21 | 0 | 4 | 0 | 0 | 0 | 2018-03-21 | 0 | 4 | 0 | 0 | 0 | 2018-03-21 | 0 | 4 | 86.6712 | 18.1047 | 0 | 2018-03-21 | 0 | 4 | 32.9351 | 6.8798 | 0
2018-03-21 01:00 | 1 | 4 | 0 | 0 | 0 | 2018-03-21 01:00 | 1 | 4 | 0 | 0 | 0 | 2018-03-21 01:00 | 1 | 4 | 86.511 | 18.0713 | 0 | 2018-03-21 01:00 | 1 | 4 | 32.8742 | 6.8671 | 0
2018-03-21 02:00 | 2 | 4 | 0 | 0 | 0 | 2018-03-21 02:00 | 2 | 4 | 0 | 0 | 0 | 2018-03-21 02:00 | 2 | 4 | 86.7628 | 18.1239 | 0 | 2018-03-21 02:00 | 2 | 4 | 32.9699 | 6.8871 | 0
2018-03-21 03:00 | 3 | 4 | 0 | 0 | 0 | 2018-03-21 03:00 | 3 | 4 | 0 | 0 | 0 | 2018-03-21 03:00 | 3 | 4 | 86.7384 | 18.1188 | 0 | 2018-03-21 03:00 | 3 | 4 | 32.9606 | 6.8851 | 0
2018-03-21 04:00 | 4 | 4 | 0 | 0 | 0 | 2018-03-21 04:00 | 4 | 4 | 0 | 0 | 0 | 2018-03-21 04:00 | 4 | 4 | 86.8376 | 18.1395 | 0 | 2018-03-21 04:00 | 4 | 4 | 32.9983 | 6.893 | 0
2018-03-21 05:00 | 5 | 4 | 0 | 0 | 0 | 2018-03-21 05:00 | 5 | 4 | 0 | 0 | 0 | 2018-03-21 05:00 | 5 | 4 | 87.0222 | 18.1781 | 0 | 2018-03-21 05:00 | 5 | 4 | 33.0684 | 6.9077 | 0
2018-03-21 06:00 | 6 | 4 | 0 | 0 | 0 | 2018-03-21 06:00 | 6 | 4 | 0 | 0 | 0 | 2018-03-21 06:00 | 6 | 4 | 86.9627 | 18.1656 | 0 | 2018-03-21 06:00 | 6 | 4 | 33.0458 | 6.9029 | 0
2018-03-21 07:00 | 7 | 4 | 0 | 0 | 0 | 2018-03-21 07:00 | 7 | 4 | 0 | 0 | 0 | 2018-03-21 07:00 | 7 | 4 | 87.1321 | 18.201 | 0 | 2018-03-21 07:00 | 7 | 4 | 33.1102 | 6.9164 | 0
2018-03-21 08:00 | 8 | 4 | 0 | 0 | 0 | 2018-03-21 08:00 | 8 | 4 | 0 | 0 | 0 | 2018-03-21 08:00 | 8 | 4 | 87.1931 | 18.2138 | 0 | 2018-03-21 08:00 | 8 | 4 | 33.1334 | 6.9212 | 0
2018-03-21 09:00 | 9 | 4 | 0 | 0 | 0 | 2018-03-21 09:00 | 9 | 4 | 0 | 0 | 0 | 2018-03-21 09:00 | 9 | 4 | 86.7155 | 18.114 | 0 | 2018-03-21 09:00 | 9 | 4 | 32.9519 | 6.8833 | 0
2018-03-21 10:00 | 10 | 4 | 0 | 0 | 0 | 2018-03-21 10:00 | 10 | 4 | 0 | 0 | 0 | 2018-03-21 10:00 | 10 | 4 | 86.6743 | 18.1054 | 0 | 2018-03-21 10:00 | 10 | 4 | 32.9362 | 6.88 | 0
2018-03-21 11:00 | 11 | 4 | 0 | 0 | 0 | 2018-03-21 11:00 | 11 | 4 | 0 | 0 | 0 | 2018-03-21 11:00 | 11 | 4 | 86.8956 | 18.1516 | 0 | 2018-03-21 11:00 | 11 | 4 | 33.0203 | 6.8976 | 0
2018-03-21 12:00 | 12 | 4 | 0 | 0 | 0 | 2018-03-21 12:00 | 12 | 4 | 0 | 0 | 0 | 2018-03-21 12:00 | 12 | 4 | 86.9276 | 18.1583 | 0 | 2018-03-21 12:00 | 12 | 4 | 33.0325 | 6.9002 | 0
2018-03-21 13:00 | 13 | 4 | 0 | 0 | 0 | 2018-03-21 13:00 | 13 | 4 | 0 | 0 | 0 | 2018-03-21 13:00 | 13 | 4 | 87.2541 | 18.2265 | 0 | 2018-03-21 13:00 | 13 | 4 | 33.1566 | 6.9261 | 0
2018-03-21 14:00 | 14 | 4 | 0 | 0 | 0 | 2018-03-21 14:00 | 14 | 4 | 0 | 0 | 0 | 2018-03-21 14:00 | 14 | 4 | 87.4037 | 18.2578 | 0 | 2018-03-21 14:00 | 14 | 4 | 33.2134 | 6.9379 | 0
2018-03-21 15:00 | 15 | 4 | 0 | 0 | 0 | 2018-03-21 15:00 | 15 | 4 | 0 | 0 | 0 | 2018-03-21 15:00 | 15 | 4 | 87.2129 | 18.2179 | 0 | 2018-03-21 15:00 | 15 | 4 | 33.1409 | 6.9228 | 0
2018-03-21 16:00 | 16 | 4 | 0 | 0 | 0 | 2018-03-21 16:00 | 16 | 4 | 0 | 0 | 0 | 2018-03-21 16:00 | 16 | 4 | 86.9718 | 18.1675 | 0 | 2018-03-21 16:00 | 16 | 4 | 33.0493 | 6.9037 | 0
2018-03-21 17:00 | 17 | 4 | 0 | 0 | 0 | 2018-03-21 17:00 | 17 | 4 | 0 | 0 | 0 | 2018-03-21 17:00 | 17 | 4 | 87.1397 | 18.2026 | 0 | 2018-03-21 17:00 | 17 | 4 | 33.1131 | 6.917 | 0
2018-03-21 18:00 | 18 | 4 | 0 | 0 | 0 | 2018-03-21 18:00 | 18 | 4 | 0 | 0 | 0 | 2018-03-21 18:00 | 18 | 4 | 87.2435 | 18.2243 | 0 | 2018-03-21 18:00 | 18 | 4 | 33.1525 | 6.9252 | 0
2018-03-21 19:00 | 19 | 4 | 0 | 0 | 0 | 2018-03-21 19:00 | 19 | 4 | 0 | 0 | 0 | 2018-03-21 19:00 | 19 | 4 | 86.8894 | 18.1503 | 0 | 2018-03-21 19:00 | 19 | 4 | 33.018 | 6.8971 | 0
2018-03-21 20:00 | 20 | 4 | 0 | 0 | 0 | 2018-03-21 20:00 | 20 | 4 | 0 | 0 | 0 | 2018-03-21 20:00 | 20 | 4 | 87.1839 | 18.2118 | 0 | 2018-03-21 20:00 | 20 | 4 | 33.1299 | 6.9205 | 0
2018-03-21 21:00 | 21 | 4 | 0 | 0 | 0 | 2018-03-21 21:00 | 21 | 4 | 0 | 0 | 0 | 2018-03-21 21:00 | 21 | 4 | 87.2419 | 18.224 | 0 | 2018-03-21 21:00 | 21 | 4 | 33.1519 | 6.9251 | 0
2018-03-21 22:00 | 22 | 4 | 0 | 0 | 0 | 2018-03-21 22:00 | 22 | 4 | 0 | 0 | 0 | 2018-03-21 22:00 | 22 | 4 | 87.1733 | 18.2096 | 0 | 2018-03-21 22:00 | 22 | 4 | 33.1259 | 6.9197 | 0
2018-03-21 23:00 | 23 | 4 | 0 | 0 | 0 | 2018-03-21 23:00 | 23 | 4 | 0 | 0 | 0 | 2018-03-21 23:00 | 23 | 4 | 87.2557 | 18.2268 | 0 | 2018-03-21 23:00 | 23 | 4 | 33.1572 | 6.9262 | 0
2018-03-22 | 0 | 5 | 86.5492 | 18.0793 | 0 | 2018-03-22 | 0 | 5 | 0 | 0 | 0 | 2018-03-22 | 0 | 5 | 0 | 0 | 0 | 2018-03-22 | 0 | 5 | 0 | 0 | 0
2018-03-22 01:00 | 1 | 5 | 86.7201 | 18.115 | 0 | 2018-03-22 01:00 | 1 | 5 | 0 | 0 | 0 | 2018-03-22 01:00 | 1 | 5 | 0 | 0 | 0 | 2018-03-22 01:00 | 1 | 5 | 0 | 0 | 0
2018-03-22 02:00 | 2 | 5 | 86.5095 | 18.071 | 0 | 2018-03-22 02:00 | 2 | 5 | 0 | 0 | 0 | 2018-03-22 02:00 | 2 | 5 | 0 | 0 | 0 | 2018-03-22 02:00 | 2 | 5 | 0 | 0 | 0
2018-03-22 03:00 | 3 | 5 | 86.4576 | 18.0601 | 0 | 2018-03-22 03:00 | 3 | 5 | 0 | 0 | 0 | 2018-03-22 03:00 | 3 | 5 | 0 | 0 | 0 | 2018-03-22 03:00 | 3 | 5 | 0 | 0 | 0
2018-03-22 04:00 | 4 | 5 | 86.6316 | 18.0965 | 0 | 2018-03-22 04:00 | 4 | 5 | 0 | 0 | 0 | 2018-03-22 04:00 | 4 | 5 | 0 | 0 | 0 | 2018-03-22 04:00 | 4 | 5 | 0 | 0 | 0
2018-03-22 05:00 | 5 | 5 | 86.569 | 18.0834 | 0 | 2018-03-22 05:00 | 5 | 5 | 0 | 0 | 0 | 2018-03-22 05:00 | 5 | 5 | 0 | 0 | 0 | 2018-03-22 05:00 | 5 | 5 | 0 | 0 | 0
2018-03-22 06:00 | 6 | 5 | 86.6468 | 18.0997 | 0 | 2018-03-22 06:00 | 6 | 5 | 0 | 0 | 0 | 2018-03-22 06:00 | 6 | 5 | 0 | 0 | 0 | 2018-03-22 06:00 | 6 | 5 | 0 | 0 | 0
2018-03-22 07:00 | 7 | 5 | 86.6361 | 18.0974 | 0 | 2018-03-22 07:00 | 7 | 5 | 0 | 0 | 0 | 2018-03-22 07:00 | 7 | 5 | 0 | 0 | 0 | 2018-03-22 07:00 | 7 | 5 | 0 | 0 | 0
2018-03-22 08:00 | 8 | 5 | 86.6819 | 18.107 | 0 | 2018-03-22 08:00 | 8 | 5 | 0 | 0 | 0 | 2018-03-22 08:00 | 8 | 5 | 0 | 0 | 0 | 2018-03-22 08:00 | 8 | 5 | 0 | 0 | 0
2018-03-22 09:00 | 9 | 5 | 86.7094 | 18.1127 | 0 | 2018-03-22 09:00 | 9 | 5 | 0 | 0 | 0 | 2018-03-22 09:00 | 9 | 5 | 0 | 0 | 0 | 2018-03-22 09:00 | 9 | 5 | 0 | 0 | 0
2018-03-22 10:00 | 10 | 5 | 86.7933 | 18.1303 | 0 | 2018-03-22 10:00 | 10 | 5 | 0 | 0 | 0 | 2018-03-22 10:00 | 10 | 5 | 0 | 0 | 0 | 2018-03-22 10:00 | 10 | 5 | 0 | 0 | 0
2018-03-22 11:00 | 11 | 5 | 86.8009 | 18.1318 | 0 | 2018-03-22 11:00 | 11 | 5 | 0 | 0 | 0 | 2018-03-22 11:00 | 11 | 5 | 0 | 0 | 0 | 2018-03-22 11:00 | 11 | 5 | 0 | 0 | 0
2018-03-22 12:00 | 12 | 5 | 86.6728 | 18.1051 | 0 | 2018-03-22 12:00 | 12 | 5 | 0 | 0 | 0 | 2018-03-22 12:00 | 12 | 5 | 0 | 0 | 0 | 2018-03-22 12:00 | 12 | 5 | 0 | 0 | 0
2018-03-22 13:00 | 13 | 5 | 86.6316 | 18.0965 | 0 | 2018-03-22 13:00 | 13 | 5 | 0 | 0 | 0 | 2018-03-22 13:00 | 13 | 5 | 0 | 0 | 0 | 2018-03-22 13:00 | 13 | 5 | 0 | 0 | 0
2018-03-22 14:00 | 14 | 5 | 86.6316 | 18.0965 | 0 | 2018-03-22 14:00 | 14 | 5 | 0 | 0 | 0 | 2018-03-22 14:00 | 14 | 5 | 0 | 0 | 0 | 2018-03-22 14:00 | 14 | 5 | 0 | 0 | 0
2018-03-22 15:00 | 15 | 5 | 86.6636 | 18.1032 | 0 | 2018-03-22 15:00 | 15 | 5 | 0 | 0 | 0 | 2018-03-22 15:00 | 15 | 5 | 0 | 0 | 0 | 2018-03-22 15:00 | 15 | 5 | 0 | 0 | 0
2018-03-22 16:00 | 16 | 5 | 86.5568 | 18.0808 | 0 | 2018-03-22 16:00 | 16 | 5 | 0 | 0 | 0 | 2018-03-22 16:00 | 16 | 5 | 0 | 0 | 0 | 2018-03-22 16:00 | 16 | 5 | 0 | 0 | 0
2018-03-22 17:00 | 17 | 5 | 86.6865 | 18.1079 | 0 | 2018-03-22 17:00 | 17 | 5 | 0 | 0 | 0 | 2018-03-22 17:00 | 17 | 5 | 0 | 0 | 0 | 2018-03-22 17:00 | 17 | 5 | 0 | 0 | 0
2018-03-22 18:00 | 18 | 5 | 86.7262 | 18.1162 | 0 | 2018-03-22 18:00 | 18 | 5 | 0 | 0 | 0 | 2018-03-22 18:00 | 18 | 5 | 0 | 0 | 0 | 2018-03-22 18:00 | 18 | 5 | 0 | 0 | 0
2018-03-22 19:00 | 19 | 5 | 86.5187 | 18.0729 | 0 | 2018-03-22 19:00 | 19 | 5 | 0 | 0 | 0 | 2018-03-22 19:00 | 19 | 5 | 0 | 0 | 0 | 2018-03-22 19:00 | 19 | 5 | 0 | 0 | 0
2018-03-22 20:00 | 20 | 5 | 86.5766 | 18.085 | 0 | 2018-03-22 20:00 | 20 | 5 | 0 | 0 | 0 | 2018-03-22 20:00 | 20 | 5 | 0 | 0 | 0 | 2018-03-22 20:00 | 20 | 5 | 0 | 0 | 0
2018-03-22 21:00 | 21 | 5 | 86.6194 | 18.0939 | 0 | 2018-03-22 21:00 | 21 | 5 | 0 | 0 | 0 | 2018-03-22 21:00 | 21 | 5 | 0 | 0 | 0 | 2018-03-22 21:00 | 21 | 5 | 0 | 0 | 0
2018-03-22 22:00 | 22 | 5 | 86.6743 | 18.1054 | 0 | 2018-03-22 22:00 | 22 | 5 | 0 | 0 | 0 | 2018-03-22 22:00 | 22 | 5 | 0 | 0 | 0 | 2018-03-22 22:00 | 22 | 5 | 0 | 0 | 0
2018-03-22 23:00 | 23 | 5 | 86.5644 | 18.0824 | 0 | 2018-03-22 23:00 | 23 | 5 | 0 | 0 | 0 | 2018-03-22 23:00 | 23 | 5 | 0 | 0 | 0 | 2018-03-22 23:00 | 23 | 5 | 0 | 0 | 0
2018-03-23 | 0 | 6 | 86.2226 | 18.011 | 0 | 2018-03-23 | 0 | 6 | 86.688 | 18.1083 | 0 | 2018-03-23 | 0 | 6 | 0 | 0 | 0 | 2018-03-23 | 0 | 6 | 32.9414 | 6.8811 | 0
2018-03-23 01:00 | 1 | 6 | 86.1128 | 17.9881 | 0 | 2018-03-23 01:00 | 1 | 6 | 86.5232 | 18.0738 | 0 | 2018-03-23 01:00 | 1 | 6 | 0 | 0 | 0 | 2018-03-23 01:00 | 1 | 6 | 32.8788 | 6.8681 | 0
2018-03-23 02:00 | 2 | 6 | 86.2791 | 18.0228 | 0 | 2018-03-23 02:00 | 2 | 6 | 86.6896 | 18.1086 | 0 | 2018-03-23 02:00 | 2 | 6 | 0 | 0 | 0 | 2018-03-23 02:00 | 2 | 6 | 32.942 | 6.8813 | 0
2018-03-23 03:00 | 3 | 6 | 86.0014 | 17.9648 | 0 | 2018-03-23 03:00 | 3 | 6 | 86.4485 | 18.0582 | 0 | 2018-03-23 03:00 | 3 | 6 | 0 | 0 | 0 | 2018-03-23 03:00 | 3 | 6 | 32.8504 | 6.8621 | 0
2018-03-23 04:00 | 4 | 6 | 86.0533 | 17.9757 | 0 | 2018-03-23 04:00 | 4 | 6 | 86.4347 | 18.0553 | 0 | 2018-03-23 04:00 | 4 | 6 | 0 | 0 | 0 | 2018-03-23 04:00 | 4 | 6 | 32.8452 | 6.861 | 0
2018-03-23 05:00 | 5 | 6 | 86.2257 | 18.0117 | 0 | 2018-03-23 05:00 | 5 | 6 | 86.6117 | 18.0923 | 0 | 2018-03-23 05:00 | 5 | 6 | 0 | 0 | 0 | 2018-03-23 05:00 | 5 | 6 | 32.9124 | 6.8751 | 0
2018-03-23 06:00 | 6 | 6 | 86.4332 | 18.055 | 0 | 2018-03-23 06:00 | 6 | 6 | 86.9352 | 18.1599 | 0 | 2018-03-23 06:00 | 6 | 6 | 0 | 0 | 0 | 2018-03-23 06:00 | 6 | 6 | 33.0354 | 6.9008 | 0
2018-03-23 07:00 | 7 | 6 | 86.5873 | 18.0872 | 0 | 2018-03-23 07:00 | 7 | 6 | 87.0619 | 18.1864 | 0 | 2018-03-23 07:00 | 7 | 6 | 0 | 0 | 0 | 2018-03-23 07:00 | 7 | 6 | 33.0835 | 6.9108 | 0
2018-03-23 08:00 | 8 | 6 | 86.3691 | 18.0416 | 0 | 2018-03-23 08:00 | 8 | 6 | 86.7811 | 18.1277 | 0 | 2018-03-23 08:00 | 8 | 6 | 0 | 0 | 0 | 2018-03-23 08:00 | 8 | 6 | 32.9768 | 6.8885 | 0
2018-03-23 09:00 | 9 | 6 | 86.334 | 18.0343 | 0 | 2018-03-23 09:00 | 9 | 6 | 86.7399 | 18.1191 | 0 | 2018-03-23 09:00 | 9 | 6 | 0 | 0 | 0 | 2018-03-23 09:00 | 9 | 6 | 32.9612 | 6.8853 | 0
2018-03-23 10:00 | 10 | 6 | 86.5126 | 18.0716 | 0 | 2018-03-23 10:00 | 10 | 6 | 86.862 | 18.1446 | 0 | 2018-03-23 10:00 | 10 | 6 | 0 | 0 | 0 | 2018-03-23 10:00 | 10 | 6 | 33.0076 | 6.8949 | 0
2018-03-23 11:00 | 11 | 6 | 86.5003 | 18.069 | 0 | 2018-03-23 11:00 | 11 | 6 | 86.9306 | 18.1589 | 0 | 2018-03-23 11:00 | 11 | 6 | 0 | 0 | 0 | 2018-03-23 11:00 | 11 | 6 | 33.0336 | 6.9004 | 0
2018-03-23 12:00 | 12 | 6 | 86.7002 | 18.1108 | 0 | 2018-03-23 12:00 | 12 | 6 | 87.1412 | 18.2029 | 0 | 2018-03-23 12:00 | 12 | 6 | 0 | 0 | 0 | 2018-03-23 12:00 | 12 | 6 | 33.1137 | 6.9171 | 0
2018-03-23 13:00 | 13 | 6 | 86.363 | 18.0404 | 0 | 2018-03-23 13:00 | 13 | 6 | 86.8009 | 18.1318 | 0 | 2018-03-23 13:00 | 13 | 6 | 0 | 0 | 0 | 2018-03-23 13:00 | 13 | 6 | 32.9843 | 6.8901 | 0
2018-03-23 14:00 | 14 | 6 | 86.4408 | 18.0566 | 0 | 2018-03-23 14:00 | 14 | 6 | 86.8635 | 18.1449 | 0 | 2018-03-23 14:00 | 14 | 6 | 0 | 0 | 0 | 2018-03-23 14:00 | 14 | 6 | 33.0081 | 6.8951 | 0
2018-03-23 15:00 | 15 | 6 | 86.2943 | 18.026 | 0 | 2018-03-23 15:00 | 15 | 6 | 86.6743 | 18.1054 | 0 | 2018-03-23 15:00 | 15 | 6 | 0 | 0 | 0 | 2018-03-23 15:00 | 15 | 6 | 32.9362 | 6.88 | 0
2018-03-23 16:00 | 16 | 6 | 86.3706 | 18.042 | 0 | 2018-03-23 16:00 | 16 | 6 | 86.7491 | 18.121 | 0 | 2018-03-23 16:00 | 16 | 6 | 0 | 0 | 0 | 2018-03-23 16:00 | 16 | 6 | 32.9647 | 6.886 | 0
2018-03-23 17:00 | 17 | 6 | 86.2882 | 18.0247 | 0 | 2018-03-23 17:00 | 17 | 6 | 86.7445 | 18.1201 | 0 | 2018-03-23 17:00 | 17 | 6 | 0 | 0 | 0 | 2018-03-23 17:00 | 17 | 6 | 32.9629 | 6.8856 | 0
2018-03-23 18:00 | 18 | 6 | 86.1875 | 18.0037 | 0 | 2018-03-23 18:00 | 18 | 6 | 86.6667 | 18.1038 | 0 | 2018-03-23 18:00 | 18 | 6 | 0 | 0 | 0 | 2018-03-23 18:00 | 18 | 6 | 32.9333 | 6.8794 | 0
2018-03-23 19:00 | 19 | 6 | 86.099 | 17.9852 | 0 | 2018-03-23 19:00 | 19 | 6 | 86.5431 | 18.078 | 0 | 2018-03-23 19:00 | 19 | 6 | 0 | 0 | 0 | 2018-03-23 19:00 | 19 | 6 | 32.8864 | 6.8696 | 0
2018-03-23 20:00 | 20 | 6 | 86.1997 | 18.0063 | 0 | 2018-03-23 20:00 | 20 | 6 | 86.5187 | 18.0729 | 0 | 2018-03-23 20:00 | 20 | 6 | 0 | 0 | 0 | 2018-03-23 20:00 | 20 | 6 | 32.8771 | 6.8677 | 0
2018-03-23 21:00 | 21 | 6 | 86.3767 | 18.0432 | 0 | 2018-03-23 21:00 | 21 | 6 | 86.7247 | 18.1159 | 0 | 2018-03-23 21:00 | 21 | 6 | 0 | 0 | 0 | 2018-03-23 21:00 | 21 | 6 | 32.9554 | 6.8841 | 0
2018-03-23 22:00 | 22 | 6 | 86.3691 | 18.0416 | 0 | 2018-03-23 22:00 | 22 | 6 | 86.7659 | 18.1245 | 0 | 2018-03-23 22:00 | 22 | 6 | 0 | 0 | 0 | 2018-03-23 22:00 | 22 | 6 | 32.971 | 6.8873 | 0
2018-03-23 23:00 | 23 | 6 | 86.4012 | 18.0483 | 0 | 2018-03-23 23:00 | 23 | 6 | 86.7918 | 18.1299 | 0 | 2018-03-23 23:00 | 23 | 6 | 0 | 0 | 0 | 2018-03-23 23:00 | 23 | 6 | 32.9809 | 6.8894 | 0
2018-03-24 | 0 | 7 | 86.0121 | 17.9671 | 0 | 2018-03-24 | 0 | 7 | 0 | 0 | 0 | 2018-03-24 | 0 | 7 | 86.5507 | 18.0796 | 0 | 2018-03-24 | 0 | 7 | 32.8893 | 6.8702 | 0
2018-03-24 01:00 | 1 | 7 | 85.919 | 17.9476 | 0 | 2018-03-24 01:00 | 1 | 7 | 0 | 0 | 0 | 2018-03-24 01:00 | 1 | 7 | 86.5324 | 18.0758 | 0 | 2018-03-24 01:00 | 1 | 7 | 32.8823 | 6.8688 | 0
2018-03-24 02:00 | 2 | 7 | 86.0533 | 17.9757 | 0 | 2018-03-24 02:00 | 2 | 7 | 0 | 0 | 0 | 2018-03-24 02:00 | 2 | 7 | 86.6453 | 18.0993 | 0 | 2018-03-24 02:00 | 2 | 7 | 32.9252 | 6.8777 | 0
2018-03-24 03:00 | 3 | 7 | 86.1677 | 17.9996 | 0 | 2018-03-24 03:00 | 3 | 7 | 0 | 0 | 0 | 2018-03-24 03:00 | 3 | 7 | 86.7002 | 18.1108 | 0 | 2018-03-24 03:00 | 3 | 7 | 32.9461 | 6.8821 | 0
2018-03-24 04:00 | 4 | 7 | 86.3081 | 18.0289 | 0 | 2018-03-24 04:00 | 4 | 7 | 0 | 0 | 0 | 2018-03-24 04:00 | 4 | 7 | 86.8513 | 18.1424 | 0 | 2018-03-24 04:00 | 4 | 7 | 33.0035 | 6.8941 | 0
2018-03-24 05:00 | 5 | 7 | 86.2562 | 18.0181 | 0 | 2018-03-24 05:00 | 5 | 7 | 0 | 0 | 0 | 2018-03-24 05:00 | 5 | 7 | 86.8605 | 18.1443 | 0 | 2018-03-24 05:00 | 5 | 7 | 33.007 | 6.8948 | 0
2018-03-24 06:00 | 6 | 7 | 86.1234 | 17.9903 | 0 | 2018-03-24 06:00 | 6 | 7 | 0 | 0 | 0 | 2018-03-24 06:00 | 6 | 7 | 86.6682 | 18.1041 | 0 | 2018-03-24 06:00 | 6 | 7 | 32.9339 | 6.8796 | 0
2018-03-24 07:00 | 7 | 7 | 86.1906 | 18.0044 | 0 | 2018-03-24 07:00 | 7 | 7 | 0 | 0 | 0 | 2018-03-24 07:00 | 7 | 7 | 86.7247 | 18.1159 | 0 | 2018-03-24 07:00 | 7 | 7 | 32.9554 | 6.8841 | 0
2018-03-24 08:00 | 8 | 7 | 86.36 | 18.0397 | 0 | 2018-03-24 08:00 | 8 | 7 | 0 | 0 | 0 | 2018-03-24 08:00 | 8 | 7 | 86.952 | 18.1634 | 0 | 2018-03-24 08:00 | 8 | 7 | 33.0418 | 6.9021 | 0
2018-03-24 09:00 | 9 | 7 | 86.4912 | 18.0671 | 0 | 2018-03-24 09:00 | 9 | 7 | 0 | 0 | 0 | 2018-03-24 09:00 | 9 | 7 | 87.0588 | 18.1857 | 0 | 2018-03-24 09:00 | 9 | 7 | 33.0823 | 6.9106 | 0
2018-03-24 10:00 | 10 | 7 | 86.1982 | 18.0059 | 0 | 2018-03-24 10:00 | 10 | 7 | 0 | 0 | 0 | 2018-03-24 10:00 | 10 | 7 | 86.6392 | 18.0981 | 0 | 2018-03-24 10:00 | 10 | 7 | 32.9229 | 6.8773 | 0
2018-03-24 11:00 | 11 | 7 | 86.1707 | 18.0002 | 0 | 2018-03-24 11:00 | 11 | 7 | 0 | 0 | 0 | 2018-03-24 11:00 | 11 | 7 | 86.8849 | 18.1494 | 0 | 2018-03-24 11:00 | 11 | 7 | 33.0163 | 6.8968 | 0
2018-03-24 12:00 | 12 | 7 | 86.5019 | 18.0694 | 0 | 2018-03-24 12:00 | 12 | 7 | 0 | 0 | 0 | 2018-03-24 12:00 | 12 | 7 | 87.1504 | 18.2048 | 0 | 2018-03-24 12:00 | 12 | 7 | 33.1172 | 6.9178 | 0
2018-03-24 13:00 | 13 | 7 | 86.6148 | 18.093 | 0 | 2018-03-24 13:00 | 13 | 7 | 0 | 0 | 0 | 2018-03-24 13:00 | 13 | 7 | 87.3167 | 18.2396 | 0 | 2018-03-24 13:00 | 13 | 7 | 33.1803 | 6.931 | 0
2018-03-24 14:00 | 14 | 7 | 86.4439 | 18.0573 | 0 | 2018-03-24 14:00 | 14 | 7 | 0 | 0 | 0 | 2018-03-24 14:00 | 14 | 7 | 87.0832 | 18.1908 | 0 | 2018-03-24 14:00 | 14 | 7 | 33.0916 | 6.9125 | 0
2018-03-24 15:00 | 15 | 7 | 86.5522 | 18.0799 | 0 | 2018-03-24 15:00 | 15 | 7 | 0 | 0 | 0 | 2018-03-24 15:00 | 15 | 7 | 87.2938 | 18.2348 | 0 | 2018-03-24 15:00 | 15 | 7 | 33.1716 | 6.9292 | 0
2018-03-24 16:00 | 16 | 7 | 86.5644 | 18.0824 | 0 | 2018-03-24 16:00 | 16 | 7 | 0 | 0 | 0 | 2018-03-24 16:00 | 16 | 7 | 87.3579 | 18.2482 | 0 | 2018-03-24 16:00 | 16 | 7 | 33.196 | 6.9343 | 0
2018-03-24 17:00 | 17 | 7 | 86.7445 | 18.1201 | 0 | 2018-03-24 17:00 | 17 | 7 | 0 | 0 | 0 | 2018-03-24 17:00 | 17 | 7 | 87.57 | 18.2925 | 0 | 2018-03-24 17:00 | 17 | 7 | 33.2766 | 6.9511 | 0
2018-03-24 18:00 | 18 | 7 | 86.4668 | 18.062 | 0 | 2018-03-24 18:00 | 18 | 7 | 0 | 0 | 0 | 2018-03-24 18:00 | 18 | 7 | 87.3014 | 18.2364 | 0 | 2018-03-24 18:00 | 18 | 7 | 33.1745 | 6.9298 | 0
2018-03-24 19:00 | 19 | 7 | 86.3661 | 18.041 | 0 | 2018-03-24 19:00 | 19 | 7 | 0 | 0 | 0 | 2018-03-24 19:00 | 19 | 7 | 87.0954 | 18.1934 | 0 | 2018-03-24 19:00 | 19 | 7 | 33.0963 | 6.9135 | 0
2018-03-24 20:00 | 20 | 7 | 86.1173 | 17.989 | 0 | 2018-03-24 20:00 | 20 | 7 | 0 | 0 | 0 | 2018-03-24 20:00 | 20 | 7 | 86.891 | 18.1507 | 0 | 2018-03-24 20:00 | 20 | 7 | 33.0186 | 6.8973 | 0
2018-03-24 21:00 | 21 | 7 | 86.1555 | 17.997 | 0 | 2018-03-24 21:00 | 21 | 7 | 0 | 0 | 0 | 2018-03-24 21:00 | 21 | 7 | 86.9245 | 18.1577 | 0 | 2018-03-24 21:00 | 21 | 7 | 33.0313 | 6.8999 | 0
2018-03-24 22:00 | 22 | 7 | 86.2211 | 18.0107 | 0 | 2018-03-24 22:00 | 22 | 7 | 0 | 0 | 0 | 2018-03-24 22:00 | 22 | 7 | 87.0054 | 18.1746 | 0 | 2018-03-24 22:00 | 22 | 7 | 33.0621 | 6.9063 | 0
2018-03-24 23:00 | 23 | 7 | 86.2226 | 18.011 | 0 | 2018-03-24 23:00 | 23 | 7 | 0 | 0 | 0 | 2018-03-24 23:00 | 23 | 7 | 87.0787 | 18.1899 | 0 | 2018-03-24 23:00 | 23 | 7 | 33.0899 | 6.9122 | 0
2018-03-25 | 0 | 1 | 86.2364 | 18.0139 | 0 | 2018-03-25 | 0 | 1 | 86.7994 | 18.1315 | 0 | 2018-03-25 | 0 | 1 | 0 | 0 | 0 | 2018-03-25 | 0 | 1 | 32.9838 | 6.89 | 0
2018-03-25 01:00 | 1 | 1 | 86.3188 | 18.0311 | 0 | 2018-03-25 01:00 | 1 | 1 | 86.952 | 18.1634 | 0 | 2018-03-25 01:00 | 1 | 1 | 0 | 0 | 0 | 2018-03-25 01:00 | 1 | 1 | 33.0418 | 6.9021 | 0
2018-03-25 02:00 | 2 | 1 | 86.2119 | 18.0088 | 0 | 2018-03-25 02:00 | 2 | 1 | 86.8177 | 18.1353 | 0 | 2018-03-25 02:00 | 2 | 1 | 0 | 0 | 0 | 2018-03-25 02:00 | 2 | 1 | 32.9907 | 6.8914 | 0
2018-03-25 03:00 | 3 | 1 | 86.1845 | 18.0031 | 0 | 2018-03-25 03:00 | 3 | 1 | 86.7857 | 18.1287 | 0 | 2018-03-25 03:00 | 3 | 1 | 0 | 0 | 0 | 2018-03-25 03:00 | 3 | 1 | 32.9786 | 6.8889 | 0
2018-03-25 04:00 | 4 | 1 | 86.2455 | 18.0158 | 0 | 2018-03-25 04:00 | 4 | 1 | 86.833 | 18.1385 | 0 | 2018-03-25 04:00 | 4 | 1 | 0 | 0 | 0 | 2018-03-25 04:00 | 4 | 1 | 32.9965 | 6.8926 | 0
2018-03-25 05:00 | 5 | 1 | 86.2333 | 18.0133 | 0 | 2018-03-25 05:00 | 5 | 1 | 86.833 | 18.1385 | 0 | 2018-03-25 05:00 | 5 | 1 | 0 | 0 | 0 | 2018-03-25 05:00 | 5 | 1 | 32.9965 | 6.8926 | 0
2018-03-25 06:00 | 6 | 1 | 86.2776 | 18.0225 | 0 | 2018-03-25 06:00 | 6 | 1 | 86.8528 | 18.1427 | 0 | 2018-03-25 06:00 | 6 | 1 | 0 | 0 | 0 | 2018-03-25 06:00 | 6 | 1 | 33.0041 | 6.8942 | 0
2018-03-25 07:00 | 7 | 1 | 86.2867 | 18.0244 | 0 | 2018-03-25 07:00 | 7 | 1 | 86.8452 | 18.1411 | 0 | 2018-03-25 07:00 | 7 | 1 | 0 | 0 | 0 | 2018-03-25 07:00 | 7 | 1 | 33.0012 | 6.8936 | 0
2018-03-25 08:00 | 8 | 1 | 86.2989 | 18.027 | 0 | 2018-03-25 08:00 | 8 | 1 | 86.9032 | 18.1532 | 0 | 2018-03-25 08:00 | 8 | 1 | 0 | 0 | 0 | 2018-03-25 08:00 | 8 | 1 | 33.0232 | 6.8982 | 0
2018-03-25 09:00 | 9 | 1 | 86.2867 | 18.0244 | 0 | 2018-03-25 09:00 | 9 | 1 | 86.8162 | 18.135 | 0 | 2018-03-25 09:00 | 9 | 1 | 0 | 0 | 0 | 2018-03-25 09:00 | 9 | 1 | 32.9902 | 6.8913 | 0
2018-03-25 10:00 | 10 | 1 | 86.2882 | 18.0247 | 0 | 2018-03-25 10:00 | 10 | 1 | 86.8528 | 18.1427 | 0 | 2018-03-25 10:00 | 10 | 1 | 0 | 0 | 0 | 2018-03-25 10:00 | 10 | 1 | 33.0041 | 6.8942 | 0
2018-03-25 11:00 | 11 | 1 | 86.1845 | 18.0031 | 0 | 2018-03-25 11:00 | 11 | 1 | 86.743 | 18.1197 | 0 | 2018-03-25 11:00 | 11 | 1 | 0 | 0 | 0 | 2018-03-25 11:00 | 11 | 1 | 32.9623 | 6.8855 | 0
2018-03-25 12:00 | 12 | 1 | 86.1418 | 17.9942 | 0 | 2018-03-25 12:00 | 12 | 1 | 86.714 | 18.1137 | 0 | 2018-03-25 12:00 | 12 | 1 | 0 | 0 | 0 | 2018-03-25 12:00 | 12 | 1 | 32.9513 | 6.8832 | 0
2018-03-25 13:00 | 13 | 1 | 86.1479 | 17.9954 | 0 | 2018-03-25 13:00 | 13 | 1 | 86.7659 | 18.1245 | 0 | 2018-03-25 13:00 | 13 | 1 | 0 | 0 | 0 | 2018-03-25 13:00 | 13 | 1 | 32.971 | 6.8873 | 0
2018-03-25 14:00 | 14 | 1 | 86.1112 | 17.9878 | 0 | 2018-03-25 14:00 | 14 | 1 | 86.7018 | 18.1111 | 0 | 2018-03-25 14:00 | 14 | 1 | 0 | 0 | 0 | 2018-03-25 14:00 | 14 | 1 | 32.9467 | 6.8822 | 0
2018-03-25 15:00 | 15 | 1 | 86.2455 | 18.0158 | 0 | 2018-03-25 15:00 | 15 | 1 | 86.8482 | 18.1417 | 0 | 2018-03-25 15:00 | 15 | 1 | 0 | 0 | 0 | 2018-03-25 15:00 | 15 | 1 | 33.0023 | 6.8939 | 0
2018-03-25 16:00 | 16 | 1 | 86.3447 | 18.0365 | 0 | 2018-03-25 16:00 | 16 | 1 | 86.9398 | 18.1609 | 0 | 2018-03-25 16:00 | 16 | 1 | 0 | 0 | 0 | 2018-03-25 16:00 | 16 | 1 | 33.0371 | 6.9011 | 0
2018-03-25 17:00 | 17 | 1 | 86.4805 | 18.0649 | 0 | 2018-03-25 17:00 | 17 | 1 | 86.9856 | 18.1704 | 0 | 2018-03-25 17:00 | 17 | 1 | 0 | 0 | 0 | 2018-03-25 17:00 | 17 | 1 | 33.0545 | 6.9048 | 0
2018-03-25 18:00 | 18 | 1 | 86.4332 | 18.055 | 0 | 2018-03-25 18:00 | 18 | 1 | 86.92 | 18.1567 | 0 | 2018-03-25 18:00 | 18 | 1 | 0 | 0 | 0 | 2018-03-25 18:00 | 18 | 1 | 33.0296 | 6.8996 | 0
2018-03-25 19:00 | 19 | 1 | 85.6794 | 17.8976 | 0 | 2018-03-25 19:00 | 19 | 1 | 85.9266 | 17.9492 | 0 | 2018-03-25 19:00 | 19 | 1 | 0 | 0 | 0 | 2018-03-25 19:00 | 19 | 1 | 32.6521 | 6.8207 | 0
2018-03-25 20:00 | 20 | 1 | 86.3294 | 18.0333 | 0 | 2018-03-25 20:00 | 20 | 1 | 86.5888 | 18.0875 | 0 | 2018-03-25 20:00 | 20 | 1 | 0 | 0 | 0 | 2018-03-25 20:00 | 20 | 1 | 32.9037 | 6.8733 | 0
2018-03-25 21:00 | 21 | 1 | 86.3569 | 18.0391 | 0 | 2018-03-25 21:00 | 21 | 1 | 86.6728 | 18.1051 | 0 | 2018-03-25 21:00 | 21 | 1 | 0 | 0 | 0 | 2018-03-25 21:00 | 21 | 1 | 32.9357 | 6.8799 | 0
2018-03-25 22:00 | 22 | 1 | 86.4881 | 18.0665 | 0 | 2018-03-25 22:00 | 22 | 1 | 86.8086 | 18.1334 | 0 | 2018-03-25 22:00 | 22 | 1 | 0 | 0 | 0 | 2018-03-25 22:00 | 22 | 1 | 32.9873 | 6.8907 | 0
2018-03-25 23:00 | 23 | 1 | 86.4332 | 18.055 | 0 | 2018-03-25 23:00 | 23 | 1 | 86.7353 | 18.1181 | 0 | 2018-03-25 23:00 | 23 | 1 | 0 | 0 | 0 | 2018-03-25 23:00 | 23 | 1 | 32.9594 | 6.8849 | 0
2018-03-26 | 0 | 2 | 86.4088 | 18.0499 | 0 | 2018-03-26 | 0 | 2 | 86.7002 | 18.1108 | 0 | 2018-03-26 | 0 | 2 | 86.9352 | 18.1599 | 0 | 2018-03-26 | 0 | 2 | 65.9815 | 13.7829 | 0
2018-03-26 01:00 | 1 | 2 | 86.0426 | 17.9734 | 0 | 2018-03-26 01:00 | 1 | 2 | 86.3127 | 18.0299 | 0 | 2018-03-26 01:00 | 1 | 2 | 86.5278 | 18.0748 | 0 | 2018-03-26 01:00 | 1 | 2 | 65.6794 | 13.7198 | 0
2018-03-26 02:00 | 2 | 2 | 86.392 | 18.0464 | 0 | 2018-03-26 02:00 | 2 | 2 | 86.6392 | 18.0981 | 0 | 2018-03-26 02:00 | 2 | 2 | 86.8421 | 18.1404 | 0 | 2018-03-26 02:00 | 2 | 2 | 65.9229 | 13.7706 | 0
2018-03-26 03:00 | 3 | 2 | 86.2776 | 18.0225 | 0 | 2018-03-26 03:00 | 3 | 2 | 86.5766 | 18.085 | 0 | 2018-03-26 03:00 | 3 | 2 | 86.7536 | 18.122 | 0 | 2018-03-26 03:00 | 3 | 2 | 65.8655 | 13.7586 | 0
2018-03-26 04:00 | 4 | 2 | 86.5034 | 18.0697 | 0 | 2018-03-26 04:00 | 4 | 2 | 86.8849 | 18.1494 | 0 | 2018-03-26 04:00 | 4 | 2 | 87.0283 | 18.1793 | 0 | 2018-03-26 04:00 | 4 | 2 | 66.087 | 13.8049 | 0
2018-03-26 05:00 | 5 | 2 | 86.3661 | 18.041 | 0 | 2018-03-26 05:00 | 5 | 2 | 86.772 | 18.1258 | 0 | 2018-03-26 05:00 | 5 | 2 | 87.0054 | 18.1746 | 0 | 2018-03-26 05:00 | 5 | 2 | 66.0354 | 13.7941 | 0
2018-03-26 06:00 | 6 | 2 | 86.2898 | 18.0251 | 0 | 2018-03-26 06:00 | 6 | 2 | 86.6499 | 18.1003 | 0 | 2018-03-26 06:00 | 6 | 2 | 86.8147 | 18.1347 | 0 | 2018-03-26 06:00 | 6 | 2 | 65.9165 | 13.7693 | 0
2018-03-26 07:00 | 7 | 2 | 86.2043 | 18.0072 | 0 | 2018-03-26 07:00 | 7 | 2 | 86.5278 | 18.0748 | 0 | 2018-03-26 07:00 | 7 | 2 | 86.7079 | 18.1124 | 0 | 2018-03-26 07:00 | 7 | 2 | 65.8296 | 13.7511 | 0
2018-03-26 08:00 | 8 | 2 | 86.3355 | 18.0346 | 0 | 2018-03-26 08:00 | 8 | 2 | 86.5461 | 18.0786 | 0 | 2018-03-26 08:00 | 8 | 2 | 86.8025 | 18.1322 | 0 | 2018-03-26 08:00 | 8 | 2 | 65.8725 | 13.7601 | 0
2018-03-26 09:00 | 9 | 2 | 86.3798 | 18.0439 | 0 | 2018-03-26 09:00 | 9 | 2 | 86.7262 | 18.1162 | 0 | 2018-03-26 09:00 | 9 | 2 | 86.8711 | 18.1465 | 0 | 2018-03-26 09:00 | 9 | 2 | 65.967 | 13.7798 | 0
2018-03-26 10:00 | 10 | 2 | 86.2272 | 18.012 | 0 | 2018-03-26 10:00 | 10 | 2 | 86.5156 | 18.0722 | 0 | 2018-03-26 10:00 | 10 | 2 | 86.714 | 18.1137 | 0 | 2018-03-26 10:00 | 10 | 2 | 65.8272 | 13.7507 | 0
2018-03-26 11:00 | 11 | 2 | 86.2119 | 18.0088 | 0 | 2018-03-26 11:00 | 11 | 2 | 86.5141 | 18.0719 | 0 | 2018-03-26 11:00 | 11 | 2 | 86.7201 | 18.115 | 0 | 2018-03-26 11:00 | 11 | 2 | 65.829 | 13.751 | 0
2018-03-26 12:00 | 12 | 2 | 86.389 | 18.0458 | 0 | 2018-03-26 12:00 | 12 | 2 | 86.6835 | 18.1073 | 0 | 2018-03-26 12:00 | 12 | 2 | 86.8574 | 18.1436 | 0 | 2018-03-26 12:00 | 12 | 2 | 65.9455 | 13.7754 | 0
2018-03-26 13:00 | 13 | 2 | 86.4027 | 18.0487 | 0 | 2018-03-26 13:00 | 13 | 2 | 86.6224 | 18.0946 | 0 | 2018-03-26 13:00 | 13 | 2 | 86.7475 | 18.1207 | 0 | 2018-03-26 13:00 | 13 | 2 | 65.8806 | 13.7618 | 0
2018-03-26 14:00 | 14 | 2 | 86.3783 | 18.0436 | 0 | 2018-03-26 14:00 | 14 | 2 | 86.6606 | 18.1025 | 0 | 2018-03-26 14:00 | 14 | 2 | 86.7903 | 18.1296 | 0 | 2018-03-26 14:00 | 14 | 2 | 65.9113 | 13.7682 | 0
2018-03-26 15:00 | 15 | 2 | 86.3355 | 18.0346 | 0 | 2018-03-26 15:00 | 15 | 2 | 86.5248 | 18.0742 | 0 | 2018-03-26 15:00 | 15 | 2 | 86.7384 | 18.1188 | 0 | 2018-03-26 15:00 | 15 | 2 | 65.84 | 13.7533 | 0
2018-03-26 16:00 | 16 | 2 | 86.3493 | 18.0375 | 0 | 2018-03-26 16:00 | 16 | 2 | 86.4912 | 18.0671 | 0 | 2018-03-26 16:00 | 16 | 2 | 86.685 | 18.1076 | 0 | 2018-03-26 16:00 | 16 | 2 | 65.807 | 13.7464 | 0
2018-03-26 17:00 | 17 | 2 | 86.244 | 18.0155 | 0 | 2018-03-26 17:00 | 17 | 2 | 86.4683 | 18.0624 | 0 | 2018-03-26 17:00 | 17 | 2 | 86.6743 | 18.1054 | 0 | 2018-03-26 17:00 | 17 | 2 | 65.7942 | 13.7437 | 0
2018-03-26 18:00 | 18 | 2 | 86.3142 | 18.0302 | 0 | 2018-03-26 18:00 | 18 | 2 | 86.4378 | 18.056 | 0 | 2018-03-26 18:00 | 18 | 2 | 86.5934 | 18.0885 | 0 | 2018-03-26 18:00 | 18 | 2 | 65.7519 | 13.7349 | 0
2018-03-26 19:00 | 19 | 2 | 86.2089 | 18.0082 | 0 | 2018-03-26 19:00 | 19 | 2 | 86.3508 | 18.0378 | 0 | 2018-03-26 19:00 | 19 | 2 | 86.5583 | 18.0812 | 0 | 2018-03-26 19:00 | 19 | 2 | 65.7055 | 13.7252 | 0
2018-03-26 20:00 | 20 | 2 | 86.2181 | 18.0101 | 0 | 2018-03-26 20:00 | 20 | 2 | 86.4836 | 18.0656 | 0 | 2018-03-26 20:00 | 20 | 2 | 86.6896 | 18.1086 | 0 | 2018-03-26 20:00 | 20 | 2 | 65.8058 | 13.7462 | 0
2018-03-26 21:00 | 21 | 2 | 86.1494 | 17.9957 | 0 | 2018-03-26 21:00 | 21 | 2 | 86.4759 | 18.064 | 0 | 2018-03-26 21:00 | 21 | 2 | 86.63 | 18.0961 | 0 | 2018-03-26 21:00 | 21 | 2 | 65.7802 | 13.7408 | 0
2018-03-26 22:00 | 22 | 2 | 86.2593 | 18.0187 | 0 | 2018-03-26 22:00 | 22 | 2 | 86.5522 | 18.0799 | 0 | 2018-03-26 22:00 | 22 | 2 | 86.6468 | 18.0997 | 0 | 2018-03-26 22:00 | 22 | 2 | 65.8156 | 13.7482 | 0
2018-03-26 23:00 | 23 | 2 | 86.4424 | 18.057 | 0 | 2018-03-26 23:00 | 23 | 2 | 86.8055 | 18.1328 | 0 | 2018-03-26 23:00 | 23 | 2 | 86.8864 | 18.1497 | 0 | 2018-03-26 23:00 | 23 | 2 | 66.0029 | 13.7874 | 0
2018-03-27 | 0 | 3 | 86.4637 | 18.0614 | 0 | 2018-03-27 | 0 | 3 | 0 | 0 | 0 | 2018-03-27 | 0 | 3 | 0 | 0 | 0 | 2018-03-27 | 0 | 3 | 0 | 0 | 0
2018-03-27 01:00 | 1 | 3 | 86.5629 | 18.0821 | 0 | 2018-03-27 01:00 | 1 | 3 | 0 | 0 | 0 | 2018-03-27 01:00 | 1 | 3 | 0 | 0 | 0 | 2018-03-27 01:00 | 1 | 3 | 0 | 0 | 0
2018-03-27 02:00 | 2 | 3 | 86.3706 | 18.042 | 0 | 2018-03-27 02:00 | 2 | 3 | 0 | 0 | 0 | 2018-03-27 02:00 | 2 | 3 | 0 | 0 | 0 | 2018-03-27 02:00 | 2 | 3 | 0 | 0 | 0
2018-03-27 03:00 | 3 | 3 | 86.3523 | 18.0381 | 0 | 2018-03-27 03:00 | 3 | 3 | 0 | 0 | 0 | 2018-03-27 03:00 | 3 | 3 | 0 | 0 | 0 | 2018-03-27 03:00 | 3 | 3 | 0 | 0 | 0
2018-03-27 04:00 | 4 | 3 | 86.3676 | 18.0413 | 0 | 2018-03-27 04:00 | 4 | 3 | 0 | 0 | 0 | 2018-03-27 04:00 | 4 | 3 | 0 | 0 | 0 | 2018-03-27 04:00 | 4 | 3 | 0 | 0 | 0
2018-03-27 05:00 | 5 | 3 | 86.4027 | 18.0487 | 0 | 2018-03-27 05:00 | 5 | 3 | 0 | 0 | 0 | 2018-03-27 05:00 | 5 | 3 | 0 | 0 | 0 | 2018-03-27 05:00 | 5 | 3 | 0 | 0 | 0
2018-03-27 06:00 | 6 | 3 | 86.4652 | 18.0617 | 0 | 2018-03-27 06:00 | 6 | 3 | 0 | 0 | 0 | 2018-03-27 06:00 | 6 | 3 | 0 | 0 | 0 | 2018-03-27 06:00 | 6 | 3 | 0 | 0 | 0
2018-03-27 07:00 | 7 | 3 | 86.4012 | 18.0483 | 0 | 2018-03-27 07:00 | 7 | 3 | 0 | 0 | 0 | 2018-03-27 07:00 | 7 | 3 | 0 | 0 | 0 | 2018-03-27 07:00 | 7 | 3 | 0 | 0 | 0
2018-03-27 08:00 | 8 | 3 | 86.4515 | 18.0589 | 0 | 2018-03-27 08:00 | 8 | 3 | 0 | 0 | 0 | 2018-03-27 08:00 | 8 | 3 | 0 | 0 | 0 | 2018-03-27 08:00 | 8 | 3 | 0 | 0 | 0
2018-03-27 09:00 | 9 | 3 | 86.2028 | 18.0069 | 0 | 2018-03-27 09:00 | 9 | 3 | 0 | 0 | 0 | 2018-03-27 09:00 | 9 | 3 | 0 | 0 | 0 | 2018-03-27 09:00 | 9 | 3 | 0 | 0 | 0
2018-03-27 10:00 | 10 | 3 | 86.2715 | 18.0213 | 0 | 2018-03-27 10:00 | 10 | 3 | 0 | 0 | 0 | 2018-03-27 10:00 | 10 | 3 | 0 | 0 | 0 | 2018-03-27 10:00 | 10 | 3 | 0 | 0 | 0
2018-03-27 11:00 | 11 | 3 | 86.7567 | 18.1226 | 0 | 2018-03-27 11:00 | 11 | 3 | 0 | 0 | 0 | 2018-03-27 11:00 | 11 | 3 | 0 | 0 | 0 | 2018-03-27 11:00 | 11 | 3 | 0 | 0 | 0
2018-03-27 12:00 | 12 | 3 | 86.6194 | 18.0939 | 0 | 2018-03-27 12:00 | 12 | 3 | 0 | 0 | 0 | 2018-03-27 12:00 | 12 | 3 | 0 | 0 | 0 | 2018-03-27 12:00 | 12 | 3 | 0 | 0 | 0
2018-03-27 13:00 | 13 | 3 | 86.6377 | 18.0977 | 0 | 2018-03-27 13:00 | 13 | 3 | 0 | 0 | 0 | 2018-03-27 13:00 | 13 | 3 | 0 | 0 | 0 | 2018-03-27 13:00 | 13 | 3 | 0 | 0 | 0
2018-03-27 14:00 | 14 | 3 | 86.8757 | 18.1475 | 0 | 2018-03-27 14:00 | 14 | 3 | 0 | 0 | 0 | 2018-03-27 14:00 | 14 | 3 | 0 | 0 | 0 | 2018-03-27 14:00 | 14 | 3 | 0 | 0 | 0
2018-03-27 15:00 | 15 | 3 | 86.7994 | 18.1315 | 0 | 2018-03-27 15:00 | 15 | 3 | 0 | 0 | 0 | 2018-03-27 15:00 | 15 | 3 | 0 | 0 | 0 | 2018-03-27 15:00 | 15 | 3 | 0 | 0 | 0
2018-03-27 16:00 | 16 | 3 | 86.7674 | 18.1248 | 0 | 2018-03-27 16:00 | 16 | 3 | 0 | 0 | 0 | 2018-03-27 16:00 | 16 | 3 | 0 | 0 | 0 | 2018-03-27 16:00 | 16 | 3 | 0 | 0 | 0
2018-03-27 17:00 | 17 | 3 | 86.7384 | 18.1188 | 0 | 2018-03-27 17:00 | 17 | 3 | 0 | 0 | 0 | 2018-03-27 17:00 | 17 | 3 | 0 | 0 | 0 | 2018-03-27 17:00 | 17 | 3 | 0 | 0 | 0
2018-03-27 18:00 | 18 | 3 | 86.7124 | 18.1134 | 0 | 2018-03-27 18:00 | 18 | 3 | 0 | 0 | 0 | 2018-03-27 18:00 | 18 | 3 | 0 | 0 | 0 | 2018-03-27 18:00 | 18 | 3 | 0 | 0 | 0
2018-03-27 19:00 | 19 | 3 | 86.8376 | 18.1395 | 0 | 2018-03-27 19:00 | 19 | 3 | 0 | 0 | 0 | 2018-03-27 19:00 | 19 | 3 | 0 | 0 | 0 | 2018-03-27 19:00 | 19 | 3 | 0 | 0 | 0
2018-03-27 20:00 | 20 | 3 | 86.627 | 18.0955 | 0 | 2018-03-27 20:00 | 20 | 3 | 0 | 0 | 0 | 2018-03-27 20:00 | 20 | 3 | 0 | 0 | 0 | 2018-03-27 20:00 | 20 | 3 | 0 | 0 | 0
2018-03-27 21:00 | 21 | 3 | 86.6239 | 18.0949 | 0 | 2018-03-27 21:00 | 21 | 3 | 0 | 0 | 0 | 2018-03-27 21:00 | 21 | 3 | 0 | 0 | 0 | 2018-03-27 21:00 | 21 | 3 | 0 | 0 | 0
2018-03-27 22:00 | 22 | 3 | 86.714 | 18.1137 | 0 | 2018-03-27 22:00 | 22 | 3 | 0 | 0 | 0 | 2018-03-27 22:00 | 22 | 3 | 0 | 0 | 0 | 2018-03-27 22:00 | 22 | 3 | 0 | 0 | 0
2018-03-27 23:00 | 23 | 3 | 86.8971 | 18.1519 | 0 | 2018-03-27 23:00 | 23 | 3 | 0 | 0 | 0 | 2018-03-27 23:00 | 23 | 3 | 0 | 0 | 0 | 2018-03-27 23:00 | 23 | 3 | 0 | 0 | 0
2018-03-28 | 0 | 4 | 0 | 0 | 0 | 2018-03-28 | 0 | 4 | 0 | 0 | 0 | 2018-03-28 | 0 | 4 | 86.6712 | 18.1047 | 0 | 2018-03-28 | 0 | 4 | 32.9351 | 6.8798 | 0
2018-03-28 01:00 | 1 | 4 | 0 | 0 | 0 | 2018-03-28 01:00 | 1 | 4 | 0 | 0 | 0 | 2018-03-28 01:00 | 1 | 4 | 86.511 | 18.0713 | 0 | 2018-03-28 01:00 | 1 | 4 | 32.8742 | 6.8671 | 0
2018-03-28 02:00 | 2 | 4 | 0 | 0 | 0 | 2018-03-28 02:00 | 2 | 4 | 0 | 0 | 0 | 2018-03-28 02:00 | 2 | 4 | 86.7628 | 18.1239 | 0 | 2018-03-28 02:00 | 2 | 4 | 32.9699 | 6.8871 | 0
2018-03-28 03:00 | 3 | 4 | 0 | 0 | 0 | 2018-03-28 03:00 | 3 | 4 | 0 | 0 | 0 | 2018-03-28 03:00 | 3 | 4 | 86.7384 | 18.1188 | 0 | 2018-03-28 03:00 | 3 | 4 | 32.9606 | 6.8851 | 0
2018-03-28 04:00 | 4 | 4 | 0 | 0 | 0 | 2018-03-28 04:00 | 4 | 4 | 0 | 0 | 0 | 2018-03-28 04:00 | 4 | 4 | 86.8376 | 18.1395 | 0 | 2018-03-28 04:00 | 4 | 4 | 32.9983 | 6.893 | 0
2018-03-28 05:00 | 5 | 4 | 0 | 0 | 0 | 2018-03-28 05:00 | 5 | 4 | 0 | 0 | 0 | 2018-03-28 05:00 | 5 | 4 | 87.0222 | 18.1781 | 0 | 2018-03-28 05:00 | 5 | 4 | 33.0684 | 6.9077 | 0
2018-03-28 06:00 | 6 | 4 | 0 | 0 | 0 | 2018-03-28 06:00 | 6 | 4 | 0 | 0 | 0 | 2018-03-28 06:00 | 6 | 4 | 86.9627 | 18.1656 | 0 | 2018-03-28 06:00 | 6 | 4 | 33.0458 | 6.9029 | 0
2018-03-28 07:00 | 7 | 4 | 0 | 0 | 0 | 2018-03-28 07:00 | 7 | 4 | 0 | 0 | 0 | 2018-03-28 07:00 | 7 | 4 | 87.1321 | 18.201 | 0 | 2018-03-28 07:00 | 7 | 4 | 33.1102 | 6.9164 | 0
2018-03-28 08:00 | 8 | 4 | 0 | 0 | 0 | 2018-03-28 08:00 | 8 | 4 | 0 | 0 | 0 | 2018-03-28 08:00 | 8 | 4 | 87.1931 | 18.2138 | 0 | 2018-03-28 08:00 | 8 | 4 | 33.1334 | 6.9212 | 0
2018-03-28 09:00 | 9 | 4 | 0 | 0 | 0 | 2018-03-28 09:00 | 9 | 4 | 0 | 0 | 0 | 2018-03-28 09:00 | 9 | 4 | 86.7155 | 18.114 | 0 | 2018-03-28 09:00 | 9 | 4 | 32.9519 | 6.8833 | 0
2018-03-28 10:00 | 10 | 4 | 0 | 0 | 0 | 2018-03-28 10:00 | 10 | 4 | 0 | 0 | 0 | 2018-03-28 10:00 | 10 | 4 | 86.6743 | 18.1054 | 0 | 2018-03-28 10:00 | 10 | 4 | 32.9362 | 6.88 | 0
2018-03-28 11:00 | 11 | 4 | 0 | 0 | 0 | 2018-03-28 11:00 | 11 | 4 | 0 | 0 | 0 | 2018-03-28 11:00 | 11 | 4 | 86.8956 | 18.1516 | 0 | 2018-03-28 11:00 | 11 | 4 | 33.0203 | 6.8976 | 0
2018-03-28 12:00 | 12 | 4 | 0 | 0 | 0 | 2018-03-28 12:00 | 12 | 4 | 0 | 0 | 0 | 2018-03-28 12:00 | 12 | 4 | 86.9276 | 18.1583 | 0 | 2018-03-28 12:00 | 12 | 4 | 33.0325 | 6.9002 | 0
2018-03-28 13:00 | 13 | 4 | 0 | 0 | 0 | 2018-03-28 13:00 | 13 | 4 | 0 | 0 | 0 | 2018-03-28 13:00 | 13 | 4 | 87.2541 | 18.2265 | 0 | 2018-03-28 13:00 | 13 | 4 | 33.1566 | 6.9261 | 0
2018-03-28 14:00 | 14 | 4 | 0 | 0 | 0 | 2018-03-28 14:00 | 14 | 4 | 0 | 0 | 0 | 2018-03-28 14:00 | 14 | 4 | 87.4037 | 18.2578 | 0 | 2018-03-28 14:00 | 14 | 4 | 33.2134 | 6.9379 | 0
2018-03-28 15:00 | 15 | 4 | 0 | 0 | 0 | 2018-03-28 15:00 | 15 | 4 | 0 | 0 | 0 | 2018-03-28 15:00 | 15 | 4 | 87.2129 | 18.2179 | 0 | 2018-03-28 15:00 | 15 | 4 | 33.1409 | 6.9228 | 0
2018-03-28 16:00 | 16 | 4 | 0 | 0 | 0 | 2018-03-28 16:00 | 16 | 4 | 0 | 0 | 0 | 2018-03-28 16:00 | 16 | 4 | 86.9718 | 18.1675 | 0 | 2018-03-28 16:00 | 16 | 4 | 33.0493 | 6.9037 | 0
2018-03-28 17:00 | 17 | 4 | 0 | 0 | 0 | 2018-03-28 17:00 | 17 | 4 | 0 | 0 | 0 | 2018-03-28 17:00 | 17 | 4 | 87.1397 | 18.2026 | 0 | 2018-03-28 17:00 | 17 | 4 | 33.1131 | 6.917 | 0
2018-03-28 18:00 | 18 | 4 | 0 | 0 | 0 | 2018-03-28 18:00 | 18 | 4 | 0 | 0 | 0 | 2018-03-28 18:00 | 18 | 4 | 87.2435 | 18.2243 | 0 | 2018-03-28 18:00 | 18 | 4 | 33.1525 | 6.9252 | 0
2018-03-28 19:00 | 19 | 4 | 0 | 0 | 0 | 2018-03-28 19:00 | 19 | 4 | 0 | 0 | 0 | 2018-03-28 19:00 | 19 | 4 | 86.8894 | 18.1503 | 0 | 2018-03-28 19:00 | 19 | 4 | 33.018 | 6.8971 | 0
2018-03-28 20:00 | 20 | 4 | 0 | 0 | 0 | 2018-03-28 20:00 | 20 | 4 | 0 | 0 | 0 | 2018-03-28 20:00 | 20 | 4 | 87.1839 | 18.2118 | 0 | 2018-03-28 20:00 | 20 | 4 | 33.1299 | 6.9205 | 0
2018-03-28 21:00 | 21 | 4 | 0 | 0 | 0 | 2018-03-28 21:00 | 21 | 4 | 0 | 0 | 0 | 2018-03-28 21:00 | 21 | 4 | 87.2419 | 18.224 | 0 | 2018-03-28 21:00 | 21 | 4 | 33.1519 | 6.9251 | 0
2018-03-28 22:00 | 22 | 4 | 0 | 0 | 0 | 2018-03-28 22:00 | 22 | 4 | 0 | 0 | 0 | 2018-03-28 22:00 | 22 | 4 | 87.1733 | 18.2096 | 0 | 2018-03-28 22:00 | 22 | 4 | 33.1259 | 6.9197 | 0
2018-03-28 23:00 | 23 | 4 | 0 | 0 | 0 | 2018-03-28 23:00 | 23 | 4 | 0 | 0 | 0 | 2018-03-28 23:00 | 23 | 4 | 87.2557 | 18.2268 | 0 | 2018-03-28 23:00 | 23 | 4 | 33.1572 | 6.9262 | 0
2018-03-29 | 0 | 5 | 86.5492 | 18.0793 | 0 | 2018-03-29 | 0 | 5 | 0 | 0 | 0 | 2018-03-29 | 0 | 5 | 0 | 0 | 0 | 2018-03-29 | 0 | 5 | 0 | 0 | 0
2018-03-29 01:00 | 1 | 5 | 86.7201 | 18.115 | 0 | 2018-03-29 01:00 | 1 | 5 | 0 | 0 | 0 | 2018-03-29 01:00 | 1 | 5 | 0 | 0 | 0 | 2018-03-29 01:00 | 1 | 5 | 0 | 0 | 0
2018-03-29 02:00 | 2 | 5 | 86.5095 | 18.071 | 0 | 2018-03-29 02:00 | 2 | 5 | 0 | 0 | 0 | 2018-03-29 02:00 | 2 | 5 | 0 | 0 | 0 | 2018-03-29 02:00 | 2 | 5 | 0 | 0 | 0
2018-03-29 03:00 | 3 | 5 | 86.4576 | 18.0601 | 0 | 2018-03-29 03:00 | 3 | 5 | 0 | 0 | 0 | 2018-03-29 03:00 | 3 | 5 | 0 | 0 | 0 | 2018-03-29 03:00 | 3 | 5 | 0 | 0 | 0
2018-03-29 04:00 | 4 | 5 | 86.6316 | 18.0965 | 0 | 2018-03-29 04:00 | 4 | 5 | 0 | 0 | 0 | 2018-03-29 04:00 | 4 | 5 | 0 | 0 | 0 | 2018-03-29 04:00 | 4 | 5 | 0 | 0 | 0
2018-03-29 05:00 | 5 | 5 | 86.569 | 18.0834 | 0 | 2018-03-29 05:00 | 5 | 5 | 0 | 0 | 0 | 2018-03-29 05:00 | 5 | 5 | 0 | 0 | 0 | 2018-03-29 05:00 | 5 | 5 | 0 | 0 | 0
2018-03-29 06:00 | 6 | 5 | 86.6468 | 18.0997 | 0 | 2018-03-29 06:00 | 6 | 5 | 0 | 0 | 0 | 2018-03-29 06:00 | 6 | 5 | 0 | 0 | 0 | 2018-03-29 06:00 | 6 | 5 | 0 | 0 | 0
2018-03-29 07:00 | 7 | 5 | 86.6361 | 18.0974 | 0 | 2018-03-29 07:00 | 7 | 5 | 0 | 0 | 0 | 2018-03-29 07:00 | 7 | 5 | 0 | 0 | 0 | 2018-03-29 07:00 | 7 | 5 | 0 | 0 | 0
2018-03-29 08:00 | 8 | 5 | 86.6819 | 18.107 | 0 | 2018-03-29 08:00 | 8 | 5 | 0 | 0 | 0 | 2018-03-29 08:00 | 8 | 5 | 0 | 0 | 0 | 2018-03-29 08:00 | 8 | 5 | 0 | 0 | 0
2018-03-29 09:00 | 9 | 5 | 86.7094 | 18.1127 | 0 | 2018-03-29 09:00 | 9 | 5 | 0 | 0 | 0 | 2018-03-29 09:00 | 9 | 5 | 0 | 0 | 0 | 2018-03-29 09:00 | 9 | 5 | 0 | 0 | 0
2018-03-29 10:00 | 10 | 5 | 86.7933 | 18.1303 | 0 | 2018-03-29 10:00 | 10 | 5 | 0 | 0 | 0 | 2018-03-29 10:00 | 10 | 5 | 0 | 0 | 0 | 2018-03-29 10:00 | 10 | 5 | 0 | 0 | 0
2018-03-29 11:00 | 11 | 5 | 86.8009 | 18.1318 | 0 | 2018-03-29 11:00 | 11 | 5 | 0 | 0 | 0 | 2018-03-29 11:00 | 11 | 5 | 0 | 0 | 0 | 2018-03-29 11:00 | 11 | 5 | 0 | 0 | 0
2018-03-29 12:00 | 12 | 5 | 86.6728 | 18.1051 | 0 | 2018-03-29 12:00 | 12 | 5 | 0 | 0 | 0 | 2018-03-29 12:00 | 12 | 5 | 0 | 0 | 0 | 2018-03-29 12:00 | 12 | 5 | 0 | 0 | 0
2018-03-29 13:00 | 13 | 5 | 86.6316 | 18.0965 | 0 | 2018-03-29 13:00 | 13 | 5 | 0 | 0 | 0 | 2018-03-29 13:00 | 13 | 5 | 0 | 0 | 0 | 2018-03-29 13:00 | 13 | 5 | 0 | 0 | 0
2018-03-29 14:00 | 14 | 5 | 86.6316 | 18.0965 | 0 | 2018-03-29 14:00 | 14 | 5 | 0 | 0 | 0 | 2018-03-29 14:00 | 14 | 5 | 0 | 0 | 0 | 2018-03-29 14:00 | 14 | 5 | 0 | 0 | 0
2018-03-29 15:00 | 15 | 5 | 86.6636 | 18.1032 | 0 | 2018-03-29 15:00 | 15 | 5 | 0 | 0 | 0 | 2018-03-29 15:00 | 15 | 5 | 0 | 0 | 0 | 2018-03-29 15:00 | 15 | 5 | 0 | 0 | 0
2018-03-29 16:00 | 16 | 5 | 86.5568 | 18.0808 | 0 | 2018-03-29 16:00 | 16 | 5 | 0 | 0 | 0 | 2018-03-29 16:00 | 16 | 5 | 0 | 0 | 0 | 2018-03-29 16:00 | 16 | 5 | 0 | 0 | 0
2018-03-29 17:00 | 17 | 5 | 86.6865 | 18.1079 | 0 | 2018-03-29 17:00 | 17 | 5 | 0 | 0 | 0 | 2018-03-29 17:00 | 17 | 5 | 0 | 0 | 0 | 2018-03-29 17:00 | 17 | 5 | 0 | 0 | 0
2018-03-29 18:00 | 18 | 5 | 86.7262 | 18.1162 | 0 | 2018-03-29 18:00 | 18 | 5 | 0 | 0 | 0 | 2018-03-29 18:00 | 18 | 5 | 0 | 0 | 0 | 2018-03-29 18:00 | 18 | 5 | 0 | 0 | 0
2018-03-29 19:00 | 19 | 5 | 86.5187 | 18.0729 | 0 | 2018-03-29 19:00 | 19 | 5 | 0 | 0 | 0 | 2018-03-29 19:00 | 19 | 5 | 0 | 0 | 0 | 2018-03-29 19:00 | 19 | 5 | 0 | 0 | 0
2018-03-29 20:00 | 20 | 5 | 86.5766 | 18.085 | 0 | 2018-03-29 20:00 | 20 | 5 | 0 | 0 | 0 | 2018-03-29 20:00 | 20 | 5 | 0 | 0 | 0 | 2018-03-29 20:00 | 20 | 5 | 0 | 0 | 0
2018-03-29 21:00 | 21 | 5 | 86.6194 | 18.0939 | 0 | 2018-03-29 21:00 | 21 | 5 | 0 | 0 | 0 | 2018-03-29 21:00 | 21 | 5 | 0 | 0 | 0 | 2018-03-29 21:00 | 21 | 5 | 0 | 0 | 0
2018-03-29 22:00 | 22 | 5 | 86.6743 | 18.1054 | 0 | 2018-03-29 22:00 | 22 | 5 | 0 | 0 | 0 | 2018-03-29 22:00 | 22 | 5 | 0 | 0 | 0 | 2018-03-29 22:00 | 22 | 5 | 0 | 0 | 0
2018-03-29 23:00 | 23 | 5 | 86.5644 | 18.0824 | 0 | 2018-03-29 23:00 | 23 | 5 | 0 | 0 | 0 | 2018-03-29 23:00 | 23 | 5 | 0 | 0 | 0 | 2018-03-29 23:00 | 23 | 5 | 0 | 0 | 0
2018-03-30 | 0 | 6 | 86.2226 | 18.011 | 0 | 2018-03-30 | 0 | 6 | 86.688 | 18.1083 | 0 | 2018-03-30 | 0 | 6 | 0 | 0 | 0 | 2018-03-30 | 0 | 6 | 32.9414 | 6.8811 | 0
2018-03-30 01:00 | 1 | 6 | 86.1128 | 17.9881 | 0 | 2018-03-30 01:00 | 1 | 6 | 86.5232 | 18.0738 | 0 | 2018-03-30 01:00 | 1 | 6 | 0 | 0 | 0 | 2018-03-30 01:00 | 1 | 6 | 32.8788 | 6.8681 | 0
2018-03-30 02:00 | 2 | 6 | 86.2791 | 18.0228 | 0 | 2018-03-30 02:00 | 2 | 6 | 86.6896 | 18.1086 | 0 | 2018-03-30 02:00 | 2 | 6 | 0 | 0 | 0 | 2018-03-30 02:00 | 2 | 6 | 32.942 | 6.8813 | 0
2018-03-30 03:00 | 3 | 6 | 86.0014 | 17.9648 | 0 | 2018-03-30 03:00 | 3 | 6 | 86.4485 | 18.0582 | 0 | 2018-03-30 03:00 | 3 | 6 | 0 | 0 | 0 | 2018-03-30 03:00 | 3 | 6 | 32.8504 | 6.8621 | 0
2018-03-30 04:00 | 4 | 6 | 86.0533 | 17.9757 | 0 | 2018-03-30 04:00 | 4 | 6 | 86.4347 | 18.0553 | 0 | 2018-03-30 04:00 | 4 | 6 | 0 | 0 | 0 | 2018-03-30 04:00 | 4 | 6 | 32.8452 | 6.861 | 0
2018-03-30 05:00 | 5 | 6 | 86.2257 | 18.0117 | 0 | 2018-03-30 05:00 | 5 | 6 | 86.6117 | 18.0923 | 0 | 2018-03-30 05:00 | 5 | 6 | 0 | 0 | 0 | 2018-03-30 05:00 | 5 | 6 | 32.9124 | 6.8751 | 0
2018-03-30 06:00 | 6 | 6 | 86.4332 | 18.055 | 0 | 2018-03-30 06:00 | 6 | 6 | 86.9352 | 18.1599 | 0 | 2018-03-30 06:00 | 6 | 6 | 0 | 0 | 0 | 2018-03-30 06:00 | 6 | 6 | 33.0354 | 6.9008 | 0
2018-03-30 07:00 | 7 | 6 | 86.5873 | 18.0872 | 0 | 2018-03-30 07:00 | 7 | 6 | 87.0619 | 18.1864 | 0 | 2018-03-30 07:00 | 7 | 6 | 0 | 0 | 0 | 2018-03-30 07:00 | 7 | 6 | 33.0835 | 6.9108 | 0
2018-03-30 08:00 | 8 | 6 | 86.3691 | 18.0416 | 0 | 2018-03-30 08:00 | 8 | 6 | 86.7811 | 18.1277 | 0 | 2018-03-30 08:00 | 8 | 6 | 0 | 0 | 0 | 2018-03-30 08:00 | 8 | 6 | 32.9768 | 6.8885 | 0
2018-03-30 09:00 | 9 | 6 | 86.334 | 18.0343 | 0 | 2018-03-30 09:00 | 9 | 6 | 86.7399 | 18.1191 | 0 | 2018-03-30 09:00 | 9 | 6 | 0 | 0 | 0 | 2018-03-30 09:00 | 9 | 6 | 32.9612 | 6.8853 | 0
2018-03-30 10:00 | 10 | 6 | 86.5126 | 18.0716 | 0 | 2018-03-30 10:00 | 10 | 6 | 86.862 | 18.1446 | 0 | 2018-03-30 10:00 | 10 | 6 | 0 | 0 | 0 | 2018-03-30 10:00 | 10 | 6 | 33.0076 | 6.8949 | 0
2018-03-30 11:00 | 11 | 6 | 86.5003 | 18.069 | 0 | 2018-03-30 11:00 | 11 | 6 | 86.9306 | 18.1589 | 0 | 2018-03-30 11:00 | 11 | 6 | 0 | 0 | 0 | 2018-03-30 11:00 | 11 | 6 | 33.0336 | 6.9004 | 0
2018-03-30 12:00 | 12 | 6 | 86.7002 | 18.1108 | 0 | 2018-03-30 12:00 | 12 | 6 | 87.1412 | 18.2029 | 0 | 2018-03-30 12:00 | 12 | 6 | 0 | 0 | 0 | 2018-03-30 12:00 | 12 | 6 | 33.1137 | 6.9171 | 0
2018-03-30 13:00 | 13 | 6 | 86.363 | 18.0404 | 0 | 2018-03-30 13:00 | 13 | 6 | 86.8009 | 18.1318 | 0 | 2018-03-30 13:00 | 13 | 6 | 0 | 0 | 0 | 2018-03-30 13:00 | 13 | 6 | 32.9843 | 6.8901 | 0
2018-03-30 14:00 | 14 | 6 | 86.4408 | 18.0566 | 0 | 2018-03-30 14:00 | 14 | 6 | 86.8635 | 18.1449 | 0 | 2018-03-30 14:00 | 14 | 6 | 0 | 0 | 0 | 2018-03-30 14:00 | 14 | 6 | 33.0081 | 6.8951 | 0
2018-03-30 15:00 | 15 | 6 | 86.2943 | 18.026 | 0 | 2018-03-30 15:00 | 15 | 6 | 86.6743 | 18.1054 | 0 | 2018-03-30 15:00 | 15 | 6 | 0 | 0 | 0 | 2018-03-30 15:00 | 15 | 6 | 32.9362 | 6.88 | 0
2018-03-30 16:00 | 16 | 6 | 86.3706 | 18.042 | 0 | 2018-03-30 16:00 | 16 | 6 | 86.7491 | 18.121 | 0 | 2018-03-30 16:00 | 16 | 6 | 0 | 0 | 0 | 2018-03-30 16:00 | 16 | 6 | 32.9647 | 6.886 | 0
2018-03-30 17:00 | 17 | 6 | 86.2882 | 18.0247 | 0 | 2018-03-30 17:00 | 17 | 6 | 86.7445 | 18.1201 | 0 | 2018-03-30 17:00 | 17 | 6 | 0 | 0 | 0 | 2018-03-30 17:00 | 17 | 6 | 32.9629 | 6.8856 | 0
2018-03-30 18:00 | 18 | 6 | 86.1875 | 18.0037 | 0 | 2018-03-30 18:00 | 18 | 6 | 86.6667 | 18.1038 | 0 | 2018-03-30 18:00 | 18 | 6 | 0 | 0 | 0 | 2018-03-30 18:00 | 18 | 6 | 32.9333 | 6.8794 | 0
2018-03-30 19:00 | 19 | 6 | 86.099 | 17.9852 | 0 | 2018-03-30 19:00 | 19 | 6 | 86.5431 | 18.078 | 0 | 2018-03-30 19:00 | 19 | 6 | 0 | 0 | 0 | 2018-03-30 19:00 | 19 | 6 | 32.8864 | 6.8696 | 0
2018-03-30 20:00 | 20 | 6 | 86.1997 | 18.0063 | 0 | 2018-03-30 20:00 | 20 | 6 | 86.5187 | 18.0729 | 0 | 2018-03-30 20:00 | 20 | 6 | 0 | 0 | 0 | 2018-03-30 20:00 | 20 | 6 | 32.8771 | 6.8677 | 0
2018-03-30 21:00 | 21 | 6 | 86.3767 | 18.0432 | 0 | 2018-03-30 21:00 | 21 | 6 | 86.7247 | 18.1159 | 0 | 2018-03-30 21:00 | 21 | 6 | 0 | 0 | 0 | 2018-03-30 21:00 | 21 | 6 | 32.9554 | 6.8841 | 0
2018-03-30 22:00 | 22 | 6 | 86.3691 | 18.0416 | 0 | 2018-03-30 22:00 | 22 | 6 | 86.7659 | 18.1245 | 0 | 2018-03-30 22:00 | 22 | 6 | 0 | 0 | 0 | 2018-03-30 22:00 | 22 | 6 | 32.971 | 6.8873 | 0
2018-03-30 23:00 | 23 | 6 | 86.4012 | 18.0483 | 0 | 2018-03-30 23:00 | 23 | 6 | 86.7918 | 18.1299 | 0 | 2018-03-30 23:00 | 23 | 6 | 0 | 0 | 0 | 2018-03-30 23:00 | 23 | 6 | 32.9809 | 6.8894 | 0
2018-03-31 | 0 | 7 | 86.0121 | 17.9671 | 0 | 2018-03-31 | 0 | 7 | 0 | 0 | 0 | 2018-03-31 | 0 | 7 | 86.5507 | 18.0796 | 0 | 2018-03-31 | 0 | 7 | 32.8893 | 6.8702 | 0
2018-03-31 01:00 | 1 | 7 | 85.919 | 17.9476 | 0 | 2018-03-31 01:00 | 1 | 7 | 0 | 0 | 0 | 2018-03-31 01:00 | 1 | 7 | 86.5324 | 18.0758 | 0 | 2018-03-31 01:00 | 1 | 7 | 32.8823 | 6.8688 | 0
2018-03-31 02:00 | 2 | 7 | 86.0533 | 17.9757 | 0 | 2018-03-31 02:00 | 2 | 7 | 0 | 0 | 0 | 2018-03-31 02:00 | 2 | 7 | 86.6453 | 18.0993 | 0 | 2018-03-31 02:00 | 2 | 7 | 32.9252 | 6.8777 | 0
2018-03-31 03:00 | 3 | 7 | 86.1677 | 17.9996 | 0 | 2018-03-31 03:00 | 3 | 7 | 0 | 0 | 0 | 2018-03-31 03:00 | 3 | 7 | 86.7002 | 18.1108 | 0 | 2018-03-31 03:00 | 3 | 7 | 32.9461 | 6.8821 | 0
2018-03-31 04:00 | 4 | 7 | 86.3081 | 18.0289 | 0 | 2018-03-31 04:00 | 4 | 7 | 0 | 0 | 0 | 2018-03-31 04:00 | 4 | 7 | 86.8513 | 18.1424 | 0 | 2018-03-31 04:00 | 4 | 7 | 33.0035 | 6.8941 | 0
2018-03-31 05:00 | 5 | 7 | 86.2562 | 18.0181 | 0 | 2018-03-31 05:00 | 5 | 7 | 0 | 0 | 0 | 2018-03-31 05:00 | 5 | 7 | 86.8605 | 18.1443 | 0 | 2018-03-31 05:00 | 5 | 7 | 33.007 | 6.8948 | 0
2018-03-31 06:00 | 6 | 7 | 86.1234 | 17.9903 | 0 | 2018-03-31 06:00 | 6 | 7 | 0 | 0 | 0 | 2018-03-31 06:00 | 6 | 7 | 86.6682 | 18.1041 | 0 | 2018-03-31 06:00 | 6 | 7 | 32.9339 | 6.8796 | 0
2018-03-31 07:00 | 7 | 7 | 86.1906 | 18.0044 | 0 | 2018-03-31 07:00 | 7 | 7 | 0 | 0 | 0 | 2018-03-31 07:00 | 7 | 7 | 86.7247 | 18.1159 | 0 | 2018-03-31 07:00 | 7 | 7 | 32.9554 | 6.8841 | 0
2018-03-31 08:00 | 8 | 7 | 86.36 | 18.0397 | 0 | 2018-03-31 08:00 | 8 | 7 | 0 | 0 | 0 | 2018-03-31 08:00 | 8 | 7 | 86.952 | 18.1634 | 0 | 2018-03-31 08:00 | 8 | 7 | 33.0418 | 6.9021 | 0
2018-03-31 09:00 | 9 | 7 | 86.4912 | 18.0671 | 0 | 2018-03-31 09:00 | 9 | 7 | 0 | 0 | 0 | 2018-03-31 09:00 | 9 | 7 | 87.0588 | 18.1857 | 0 | 2018-03-31 09:00 | 9 | 7 | 33.0823 | 6.9106 | 0
2018-03-31 10:00 | 10 | 7 | 86.1982 | 18.0059 | 0 | 2018-03-31 10:00 | 10 | 7 | 0 | 0 | 0 | 2018-03-31 10:00 | 10 | 7 | 86.6392 | 18.0981 | 0 | 2018-03-31 10:00 | 10 | 7 | 32.9229 | 6.8773 | 0
2018-03-31 11:00 | 11 | 7 | 86.1707 | 18.0002 | 0 | 2018-03-31 11:00 | 11 | 7 | 0 | 0 | 0 | 2018-03-31 11:00 | 11 | 7 | 86.8849 | 18.1494 | 0 | 2018-03-31 11:00 | 11 | 7 | 33.0163 | 6.8968 | 0
2018-03-31 12:00 | 12 | 7 | 86.5019 | 18.0694 | 0 | 2018-03-31 12:00 | 12 | 7 | 0 | 0 | 0 | 2018-03-31 12:00 | 12 | 7 | 87.1504 | 18.2048 | 0 | 2018-03-31 12:00 | 12 | 7 | 33.1172 | 6.9178 | 0
2018-03-31 13:00 | 13 | 7 | 86.6148 | 18.093 | 0 | 2018-03-31 13:00 | 13 | 7 | 0 | 0 | 0 | 2018-03-31 13:00 | 13 | 7 | 87.3167 | 18.2396 | 0 | 2018-03-31 13:00 | 13 | 7 | 33.1803 | 6.931 | 0
2018-03-31 14:00 | 14 | 7 | 86.4439 | 18.0573 | 0 | 2018-03-31 14:00 | 14 | 7 | 0 | 0 | 0 | 2018-03-31 14:00 | 14 | 7 | 87.0832 | 18.1908 | 0 | 2018-03-31 14:00 | 14 | 7 | 33.0916 | 6.9125 | 0
2018-03-31 15:00 | 15 | 7 | 86.5522 | 18.0799 | 0 | 2018-03-31 15:00 | 15 | 7 | 0 | 0 | 0 | 2018-03-31 15:00 | 15 | 7 | 87.2938 | 18.2348 | 0 | 2018-03-31 15:00 | 15 | 7 | 33.1716 | 6.9292 | 0
2018-03-31 16:00 | 16 | 7 | 86.5644 | 18.0824 | 0 | 2018-03-31 16:00 | 16 | 7 | 0 | 0 | 0 | 2018-03-31 16:00 | 16 | 7 | 87.3579 | 18.2482 | 0 | 2018-03-31 16:00 | 16 | 7 | 33.196 | 6.9343 | 0
2018-03-31 17:00 | 17 | 7 | 86.7445 | 18.1201 | 0 | 2018-03-31 17:00 | 17 | 7 | 0 | 0 | 0 | 2018-03-31 17:00 | 17 | 7 | 87.57 | 18.2925 | 0 | 2018-03-31 17:00 | 17 | 7 | 33.2766 | 6.9511 | 0
2018-03-31 18:00 | 18 | 7 | 86.4668 | 18.062 | 0 | 2018-03-31 18:00 | 18 | 7 | 0 | 0 | 0 | 2018-03-31 18:00 | 18 | 7 | 87.3014 | 18.2364 | 0 | 2018-03-31 18:00 | 18 | 7 | 33.1745 | 6.9298 | 0
2018-03-31 19:00 | 19 | 7 | 86.3661 | 18.041 | 0 | 2018-03-31 19:00 | 19 | 7 | 0 | 0 | 0 | 2018-03-31 19:00 | 19 | 7 | 87.0954 | 18.1934 | 0 | 2018-03-31 19:00 | 19 | 7 | 33.0963 | 6.9135 | 0
2018-03-31 20:00 | 20 | 7 | 86.1173 | 17.989 | 0 | 2018-03-31 20:00 | 20 | 7 | 0 | 0 | 0 | 2018-03-31 20:00 | 20 | 7 | 86.891 | 18.1507 | 0 | 2018-03-31 20:00 | 20 | 7 | 33.0186 | 6.8973 | 0
2018-03-31 21:00 | 21 | 7 | 86.1555 | 17.997 | 0 | 2018-03-31 21:00 | 21 | 7 | 0 | 0 | 0 | 2018-03-31 21:00 | 21 | 7 | 86.9245 | 18.1577 | 0 | 2018-03-31 21:00 | 21 | 7 | 33.0313 | 6.8999 | 0
2018-03-31 22:00 | 22 | 7 | 86.2211 | 18.0107 | 0 | 2018-03-31 22:00 | 22 | 7 | 0 | 0 | 0 | 2018-03-31 22:00 | 22 | 7 | 87.0054 | 18.1746 | 0 | 2018-03-31 22:00 | 22 | 7 | 33.0621 | 6.9063 | 0
2018-03-31 23:00 | 23 | 7 | 86.2226 | 18.011 | 0 | 2018-03-31 23:00 | 23 | 7 | 0 | 0 | 0 | 2018-03-31 23:00 | 23 | 7 | 87.0787 | 18.1899 | 0 | 2018-03-31 23:00 | 23 | 7 | 33.0899 | 6.9122 | 0
2018-04-01 | 0 | 1 | 86.2364 | 18.0139 | 0 | 2018-04-01 | 0 | 1 | 86.7994 | 18.1315 | 0 | 2018-04-01 | 0 | 1 | 0 | 0 | 0 | 2018-04-01 | 0 | 1 | 32.9838 | 6.89 | 0
2018-04-01 01:00 | 1 | 1 | 86.3188 | 18.0311 | 0 | 2018-04-01 01:00 | 1 | 1 | 86.952 | 18.1634 | 0 | 2018-04-01 01:00 | 1 | 1 | 0 | 0 | 0 | 2018-04-01 01:00 | 1 | 1 | 33.0418 | 6.9021 | 0
2018-04-01 02:00 | 2 | 1 | 86.2119 | 18.0088 | 0 | 2018-04-01 02:00 | 2 | 1 | 86.8177 | 18.1353 | 0 | 2018-04-01 02:00 | 2 | 1 | 0 | 0 | 0 | 2018-04-01 02:00 | 2 | 1 | 32.9907 | 6.8914 | 0
2018-04-01 03:00 | 3 | 1 | 86.1845 | 18.0031 | 0 | 2018-04-01 03:00 | 3 | 1 | 86.7857 | 18.1287 | 0 | 2018-04-01 03:00 | 3 | 1 | 0 | 0 | 0 | 2018-04-01 03:00 | 3 | 1 | 32.9786 | 6.8889 | 0
2018-04-01 04:00 | 4 | 1 | 86.2455 | 18.0158 | 0 | 2018-04-01 04:00 | 4 | 1 | 86.833 | 18.1385 | 0 | 2018-04-01 04:00 | 4 | 1 | 0 | 0 | 0 | 2018-04-01 04:00 | 4 | 1 | 32.9965 | 6.8926 | 0
2018-04-01 05:00 | 5 | 1 | 86.2333 | 18.0133 | 0 | 2018-04-01 05:00 | 5 | 1 | 86.833 | 18.1385 | 0 | 2018-04-01 05:00 | 5 | 1 | 0 | 0 | 0 | 2018-04-01 05:00 | 5 | 1 | 32.9965 | 6.8926 | 0
2018-04-01 06:00 | 6 | 1 | 86.2776 | 18.0225 | 0 | 2018-04-01 06:00 | 6 | 1 | 86.8528 | 18.1427 | 0 | 2018-04-01 06:00 | 6 | 1 | 0 | 0 | 0 | 2018-04-01 06:00 | 6 | 1 | 33.0041 | 6.8942 | 0
2018-04-01 07:00 | 7 | 1 | 86.2867 | 18.0244 | 0 | 2018-04-01 07:00 | 7 | 1 | 86.8452 | 18.1411 | 0 | 2018-04-01 07:00 | 7 | 1 | 0 | 0 | 0 | 2018-04-01 07:00 | 7 | 1 | 33.0012 | 6.8936 | 0
2018-04-01 08:00 | 8 | 1 | 86.2989 | 18.027 | 0 | 2018-04-01 08:00 | 8 | 1 | 86.9032 | 18.1532 | 0 | 2018-04-01 08:00 | 8 | 1 | 0 | 0 | 0 | 2018-04-01 08:00 | 8 | 1 | 33.0232 | 6.8982 | 0
2018-04-01 09:00 | 9 | 1 | 86.2867 | 18.0244 | 0 | 2018-04-01 09:00 | 9 | 1 | 86.8162 | 18.135 | 0 | 2018-04-01 09:00 | 9 | 1 | 0 | 0 | 0 | 2018-04-01 09:00 | 9 | 1 | 32.9902 | 6.8913 | 0
2018-04-01 10:00 | 10 | 1 | 86.2882 | 18.0247 | 0 | 2018-04-01 10:00 | 10 | 1 | 86.8528 | 18.1427 | 0 | 2018-04-01 10:00 | 10 | 1 | 0 | 0 | 0 | 2018-04-01 10:00 | 10 | 1 | 33.0041 | 6.8942 | 0
2018-04-01 11:00 | 11 | 1 | 86.1845 | 18.0031 | 0 | 2018-04-01 11:00 | 11 | 1 | 86.743 | 18.1197 | 0 | 2018-04-01 11:00 | 11 | 1 | 0 | 0 | 0 | 2018-04-01 11:00 | 11 | 1 | 32.9623 | 6.8855 | 0
2018-04-01 12:00 | 12 | 1 | 86.1418 | 17.9942 | 0 | 2018-04-01 12:00 | 12 | 1 | 86.714 | 18.1137 | 0 | 2018-04-01 12:00 | 12 | 1 | 0 | 0 | 0 | 2018-04-01 12:00 | 12 | 1 | 32.9513 | 6.8832 | 0
2018-04-01 13:00 | 13 | 1 | 86.1479 | 17.9954 | 0 | 2018-04-01 13:00 | 13 | 1 | 86.7659 | 18.1245 | 0 | 2018-04-01 13:00 | 13 | 1 | 0 | 0 | 0 | 2018-04-01 13:00 | 13 | 1 | 32.971 | 6.8873 | 0
2018-04-01 14:00 | 14 | 1 | 86.1112 | 17.9878 | 0 | 2018-04-01 14:00 | 14 | 1 | 86.7018 | 18.1111 | 0 | 2018-04-01 14:00 | 14 | 1 | 0 | 0 | 0 | 2018-04-01 14:00 | 14 | 1 | 32.9467 | 6.8822 | 0
2018-04-01 15:00 | 15 | 1 | 86.2455 | 18.0158 | 0 | 2018-04-01 15:00 | 15 | 1 | 86.8482 | 18.1417 | 0 | 2018-04-01 15:00 | 15 | 1 | 0 | 0 | 0 | 2018-04-01 15:00 | 15 | 1 | 33.0023 | 6.8939 | 0
2018-04-01 16:00 | 16 | 1 | 86.3447 | 18.0365 | 0 | 2018-04-01 16:00 | 16 | 1 | 86.9398 | 18.1609 | 0 | 2018-04-01 16:00 | 16 | 1 | 0 | 0 | 0 | 2018-04-01 16:00 | 16 | 1 | 33.0371 | 6.9011 | 0
2018-04-01 17:00 | 17 | 1 | 86.4805 | 18.0649 | 0 | 2018-04-01 17:00 | 17 | 1 | 86.9856 | 18.1704 | 0 | 2018-04-01 17:00 | 17 | 1 | 0 | 0 | 0 | 2018-04-01 17:00 | 17 | 1 | 33.0545 | 6.9048 | 0
2018-04-01 18:00 | 18 | 1 | 86.4332 | 18.055 | 0 | 2018-04-01 18:00 | 18 | 1 | 86.92 | 18.1567 | 0 | 2018-04-01 18:00 | 18 | 1 | 0 | 0 | 0 | 2018-04-01 18:00 | 18 | 1 | 33.0296 | 6.8996 | 0
2018-04-01 19:00 | 19 | 1 | 85.6794 | 17.8976 | 0 | 2018-04-01 19:00 | 19 | 1 | 85.9266 | 17.9492 | 0 | 2018-04-01 19:00 | 19 | 1 | 0 | 0 | 0 | 2018-04-01 19:00 | 19 | 1 | 32.6521 | 6.8207 | 0
2018-04-01 20:00 | 20 | 1 | 86.3294 | 18.0333 | 0 | 2018-04-01 20:00 | 20 | 1 | 86.5888 | 18.0875 | 0 | 2018-04-01 20:00 | 20 | 1 | 0 | 0 | 0 | 2018-04-01 20:00 | 20 | 1 | 32.9037 | 6.8733 | 0
2018-04-01 21:00 | 21 | 1 | 86.3569 | 18.0391 | 0 | 2018-04-01 21:00 | 21 | 1 | 86.6728 | 18.1051 | 0 | 2018-04-01 21:00 | 21 | 1 | 0 | 0 | 0 | 2018-04-01 21:00 | 21 | 1 | 32.9357 | 6.8799 | 0
2018-04-01 22:00 | 22 | 1 | 86.4881 | 18.0665 | 0 | 2018-04-01 22:00 | 22 | 1 | 86.8086 | 18.1334 | 0 | 2018-04-01 22:00 | 22 | 1 | 0 | 0 | 0 | 2018-04-01 22:00 | 22 | 1 | 32.9873 | 6.8907 | 0
2018-04-01 23:00 | 23 | 1 | 86.4332 | 18.055 | 0 | 2018-04-01 23:00 | 23 | 1 | 86.7353 | 18.1181 | 0 | 2018-04-01 23:00 | 23 | 1 | 0 | 0 | 0 | 2018-04-01 23:00 | 23 | 1 | 32.9594 | 6.8849 | 0
2018-04-02 | 0 | 2 | 86.4088 | 18.0499 | 0 | 2018-04-02 | 0 | 2 | 86.7002 | 18.1108 | 0 | 2018-04-02 | 0 | 2 | 86.9352 | 18.1599 | 0 | 2018-04-02 | 0 | 2 | 65.9815 | 13.7829 | 0
2018-04-02 01:00 | 1 | 2 | 86.0426 | 17.9734 | 0 | 2018-04-02 01:00 | 1 | 2 | 86.3127 | 18.0299 | 0 | 2018-04-02 01:00 | 1 | 2 | 86.5278 | 18.0748 | 0 | 2018-04-02 01:00 | 1 | 2 | 65.6794 | 13.7198 | 0
2018-04-02 02:00 | 2 | 2 | 86.392 | 18.0464 | 0 | 2018-04-02 02:00 | 2 | 2 | 86.6392 | 18.0981 | 0 | 2018-04-02 02:00 | 2 | 2 | 86.8421 | 18.1404 | 0 | 2018-04-02 02:00 | 2 | 2 | 65.9229 | 13.7706 | 0
2018-04-02 03:00 | 3 | 2 | 86.2776 | 18.0225 | 0 | 2018-04-02 03:00 | 3 | 2 | 86.5766 | 18.085 | 0 | 2018-04-02 03:00 | 3 | 2 | 86.7536 | 18.122 | 0 | 2018-04-02 03:00 | 3 | 2 | 65.8655 | 13.7586 | 0
2018-04-02 04:00 | 4 | 2 | 86.5034 | 18.0697 | 0 | 2018-04-02 04:00 | 4 | 2 | 86.8849 | 18.1494 | 0 | 2018-04-02 04:00 | 4 | 2 | 87.0283 | 18.1793 | 0 | 2018-04-02 04:00 | 4 | 2 | 66.087 | 13.8049 | 0
2018-04-02 05:00 | 5 | 2 | 86.3661 | 18.041 | 0 | 2018-04-02 05:00 | 5 | 2 | 86.772 | 18.1258 | 0 | 2018-04-02 05:00 | 5 | 2 | 87.0054 | 18.1746 | 0 | 2018-04-02 05:00 | 5 | 2 | 66.0354 | 13.7941 | 0
2018-04-02 06:00 | 6 | 2 | 86.2898 | 18.0251 | 0 | 2018-04-02 06:00 | 6 | 2 | 86.6499 | 18.1003 | 0 | 2018-04-02 06:00 | 6 | 2 | 86.8147 | 18.1347 | 0 | 2018-04-02 06:00 | 6 | 2 | 65.9165 | 13.7693 | 0
2018-04-02 07:00 | 7 | 2 | 86.2043 | 18.0072 | 0 | 2018-04-02 07:00 | 7 | 2 | 86.5278 | 18.0748 | 0 | 2018-04-02 07:00 | 7 | 2 | 86.7079 | 18.1124 | 0 | 2018-04-02 07:00 | 7 | 2 | 65.8296 | 13.7511 | 0
2018-04-02 08:00 | 8 | 2 | 86.3355 | 18.0346 | 0 | 2018-04-02 08:00 | 8 | 2 | 86.5461 | 18.0786 | 0 | 2018-04-02 08:00 | 8 | 2 | 86.8025 | 18.1322 | 0 | 2018-04-02 08:00 | 8 | 2 | 65.8725 | 13.7601 | 0
2018-04-02 09:00 | 9 | 2 | 86.3798 | 18.0439 | 0 | 2018-04-02 09:00 | 9 | 2 | 86.7262 | 18.1162 | 0 | 2018-04-02 09:00 | 9 | 2 | 86.8711 | 18.1465 | 0 | 2018-04-02 09:00 | 9 | 2 | 65.967 | 13.7798 | 0
2018-04-02 10:00 | 10 | 2 | 86.2272 | 18.012 | 0 | 2018-04-02 10:00 | 10 | 2 | 86.5156 | 18.0722 | 0 | 2018-04-02 10:00 | 10 | 2 | 86.714 | 18.1137 | 0 | 2018-04-02 10:00 | 10 | 2 | 65.8272 | 13.7507 | 0
2018-04-02 11:00 | 11 | 2 | 86.2119 | 18.0088 | 0 | 2018-04-02 11:00 | 11 | 2 | 86.5141 | 18.0719 | 0 | 2018-04-02 11:00 | 11 | 2 | 86.7201 | 18.115 | 0 | 2018-04-02 11:00 | 11 | 2 | 65.829 | 13.751 | 0
2018-04-02 12:00 | 12 | 2 | 86.389 | 18.0458 | 0 | 2018-04-02 12:00 | 12 | 2 | 86.6835 | 18.1073 | 0 | 2018-04-02 12:00 | 12 | 2 | 86.8574 | 18.1436 | 0 | 2018-04-02 12:00 | 12 | 2 | 65.9455 | 13.7754 | 0
2018-04-02 13:00 | 13 | 2 | 86.4027 | 18.0487 | 0 | 2018-04-02 13:00 | 13 | 2 | 86.6224 | 18.0946 | 0 | 2018-04-02 13:00 | 13 | 2 | 86.7475 | 18.1207 | 0 | 2018-04-02 13:00 | 13 | 2 | 65.8806 | 13.7618 | 0
2018-04-02 14:00 | 14 | 2 | 86.3783 | 18.0436 | 0 | 2018-04-02 14:00 | 14 | 2 | 86.6606 | 18.1025 | 0 | 2018-04-02 14:00 | 14 | 2 | 86.7903 | 18.1296 | 0 | 2018-04-02 14:00 | 14 | 2 | 65.9113 | 13.7682 | 0
2018-04-02 15:00 | 15 | 2 | 86.3355 | 18.0346 | 0 | 2018-04-02 15:00 | 15 | 2 | 86.5248 | 18.0742 | 0 | 2018-04-02 15:00 | 15 | 2 | 86.7384 | 18.1188 | 0 | 2018-04-02 15:00 | 15 | 2 | 65.84 | 13.7533 | 0
2018-04-02 16:00 | 16 | 2 | 86.3493 | 18.0375 | 0 | 2018-04-02 16:00 | 16 | 2 | 86.4912 | 18.0671 | 0 | 2018-04-02 16:00 | 16 | 2 | 86.685 | 18.1076 | 0 | 2018-04-02 16:00 | 16 | 2 | 65.807 | 13.7464 | 0
2018-04-02 17:00 | 17 | 2 | 86.244 | 18.0155 | 0 | 2018-04-02 17:00 | 17 | 2 | 86.4683 | 18.0624 | 0 | 2018-04-02 17:00 | 17 | 2 | 86.6743 | 18.1054 | 0 | 2018-04-02 17:00 | 17 | 2 | 65.7942 | 13.7437 | 0
2018-04-02 18:00 | 18 | 2 | 86.3142 | 18.0302 | 0 | 2018-04-02 18:00 | 18 | 2 | 86.4378 | 18.056 | 0 | 2018-04-02 18:00 | 18 | 2 | 86.5934 | 18.0885 | 0 | 2018-04-02 18:00 | 18 | 2 | 65.7519 | 13.7349 | 0
2018-04-02 19:00 | 19 | 2 | 86.2089 | 18.0082 | 0 | 2018-04-02 19:00 | 19 | 2 | 86.3508 | 18.0378 | 0 | 2018-04-02 19:00 | 19 | 2 | 86.5583 | 18.0812 | 0 | 2018-04-02 19:00 | 19 | 2 | 65.7055 | 13.7252 | 0
2018-04-02 20:00 | 20 | 2 | 86.2181 | 18.0101 | 0 | 2018-04-02 20:00 | 20 | 2 | 86.4836 | 18.0656 | 0 | 2018-04-02 20:00 | 20 | 2 | 86.6896 | 18.1086 | 0 | 2018-04-02 20:00 | 20 | 2 | 65.8058 | 13.7462 | 0
2018-04-02 21:00 | 21 | 2 | 86.1494 | 17.9957 | 0 | 2018-04-02 21:00 | 21 | 2 | 86.4759 | 18.064 | 0 | 2018-04-02 21:00 | 21 | 2 | 86.63 | 18.0961 | 0 | 2018-04-02 21:00 | 21 | 2 | 65.7802 | 13.7408 | 0
2018-04-02 22:00 | 22 | 2 | 86.2593 | 18.0187 | 0 | 2018-04-02 22:00 | 22 | 2 | 86.5522 | 18.0799 | 0 | 2018-04-02 22:00 | 22 | 2 | 86.6468 | 18.0997 | 0 | 2018-04-02 22:00 | 22 | 2 | 65.8156 | 13.7482 | 0
2018-04-02 23:00 | 23 | 2 | 86.4424 | 18.057 | 0 | 2018-04-02 23:00 | 23 | 2 | 86.8055 | 18.1328 | 0 | 2018-04-02 23:00 | 23 | 2 | 86.8864 | 18.1497 | 0 | 2018-04-02 23:00 | 23 | 2 | 66.0029 | 13.7874 | 0
2018-04-03 | 0 | 3 | 86.4637 | 18.0614 | 0 | 2018-04-03 | 0 | 3 | 0 | 0 | 0 | 2018-04-03 | 0 | 3 | 0 | 0 | 0 | 2018-04-03 | 0 | 3 | 0 | 0 | 0
2018-04-03 01:00 | 1 | 3 | 86.5629 | 18.0821 | 0 | 2018-04-03 01:00 | 1 | 3 | 0 | 0 | 0 | 2018-04-03 01:00 | 1 | 3 | 0 | 0 | 0 | 2018-04-03 01:00 | 1 | 3 | 0 | 0 | 0
2018-04-03 02:00 | 2 | 3 | 86.3706 | 18.042 | 0 | 2018-04-03 02:00 | 2 | 3 | 0 | 0 | 0 | 2018-04-03 02:00 | 2 | 3 | 0 | 0 | 0 | 2018-04-03 02:00 | 2 | 3 | 0 | 0 | 0
2018-04-03 03:00 | 3 | 3 | 86.3523 | 18.0381 | 0 | 2018-04-03 03:00 | 3 | 3 | 0 | 0 | 0 | 2018-04-03 03:00 | 3 | 3 | 0 | 0 | 0 | 2018-04-03 03:00 | 3 | 3 | 0 | 0 | 0
2018-04-03 04:00 | 4 | 3 | 86.3676 | 18.0413 | 0 | 2018-04-03 04:00 | 4 | 3 | 0 | 0 | 0 | 2018-04-03 04:00 | 4 | 3 | 0 | 0 | 0 | 2018-04-03 04:00 | 4 | 3 | 0 | 0 | 0
2018-04-03 05:00 | 5 | 3 | 86.4027 | 18.0487 | 0 | 2018-04-03 05:00 | 5 | 3 | 0 | 0 | 0 | 2018-04-03 05:00 | 5 | 3 | 0 | 0 | 0 | 2018-04-03 05:00 | 5 | 3 | 0 | 0 | 0
2018-04-03 06:00 | 6 | 3 | 86.4652 | 18.0617 | 0 | 2018-04-03 06:00 | 6 | 3 | 0 | 0 | 0 | 2018-04-03 06:00 | 6 | 3 | 0 | 0 | 0 | 2018-04-03 06:00 | 6 | 3 | 0 | 0 | 0
2018-04-03 07:00 | 7 | 3 | 86.4012 | 18.0483 | 0 | 2018-04-03 07:00 | 7 | 3 | 0 | 0 | 0 | 2018-04-03 07:00 | 7 | 3 | 0 | 0 | 0 | 2018-04-03 07:00 | 7 | 3 | 0 | 0 | 0
2018-04-03 08:00 | 8 | 3 | 86.4515 | 18.0589 | 0 | 2018-04-03 08:00 | 8 | 3 | 0 | 0 | 0 | 2018-04-03 08:00 | 8 | 3 | 0 | 0 | 0 | 2018-04-03 08:00 | 8 | 3 | 0 | 0 | 0
2018-04-03 09:00 | 9 | 3 | 86.2028 | 18.0069 | 0 | 2018-04-03 09:00 | 9 | 3 | 0 | 0 | 0 | 2018-04-03 09:00 | 9 | 3 | 0 | 0 | 0 | 2018-04-03 09:00 | 9 | 3 | 0 | 0 | 0
2018-04-03 10:00 | 10 | 3 | 86.2715 | 18.0213 | 0 | 2018-04-03 10:00 | 10 | 3 | 0 | 0 | 0 | 2018-04-03 10:00 | 10 | 3 | 0 | 0 | 0 | 2018-04-03 10:00 | 10 | 3 | 0 | 0 | 0
2018-04-03 11:00 | 11 | 3 | 86.7567 | 18.1226 | 0 | 2018-04-03 11:00 | 11 | 3 | 0 | 0 | 0 | 2018-04-03 11:00 | 11 | 3 | 0 | 0 | 0 | 2018-04-03 11:00 | 11 | 3 | 0 | 0 | 0
2018-04-03 12:00 | 12 | 3 | 86.6194 | 18.0939 | 0 | 2018-04-03 12:00 | 12 | 3 | 0 | 0 | 0 | 2018-04-03 12:00 | 12 | 3 | 0 | 0 | 0 | 2018-04-03 12:00 | 12 | 3 | 0 | 0 | 0
2018-04-03 13:00 | 13 | 3 | 86.6377 | 18.0977 | 0 | 2018-04-03 13:00 | 13 | 3 | 0 | 0 | 0 | 2018-04-03 13:00 | 13 | 3 | 0 | 0 | 0 | 2018-04-03 13:00 | 13 | 3 | 0 | 0 | 0
2018-04-03 14:00 | 14 | 3 | 86.8757 | 18.1475 | 0 | 2018-04-03 14:00 | 14 | 3 | 0 | 0 | 0 | 2018-04-03 14:00 | 14 | 3 | 0 | 0 | 0 | 2018-04-03 14:00 | 14 | 3 | 0 | 0 | 0
2018-04-03 15:00 | 15 | 3 | 86.7994 | 18.1315 | 0 | 2018-04-03 15:00 | 15 | 3 | 0 | 0 | 0 | 2018-04-03 15:00 | 15 | 3 | 0 | 0 | 0 | 2018-04-03 15:00 | 15 | 3 | 0 | 0 | 0
2018-04-03 16:00 | 16 | 3 | 86.7674 | 18.1248 | 0 | 2018-04-03 16:00 | 16 | 3 | 0 | 0 | 0 | 2018-04-03 16:00 | 16 | 3 | 0 | 0 | 0 | 2018-04-03 16:00 | 16 | 3 | 0 | 0 | 0
2018-04-03 17:00 | 17 | 3 | 86.7384 | 18.1188 | 0 | 2018-04-03 17:00 | 17 | 3 | 0 | 0 | 0 | 2018-04-03 17:00 | 17 | 3 | 0 | 0 | 0 | 2018-04-03 17:00 | 17 | 3 | 0 | 0 | 0
2018-04-03 18:00 | 18 | 3 | 86.7124 | 18.1134 | 0 | 2018-04-03 18:00 | 18 | 3 | 0 | 0 | 0 | 2018-04-03 18:00 | 18 | 3 | 0 | 0 | 0 | 2018-04-03 18:00 | 18 | 3 | 0 | 0 | 0
2018-04-03 19:00 | 19 | 3 | 86.8376 | 18.1395 | 0 | 2018-04-03 19:00 | 19 | 3 | 0 | 0 | 0 | 2018-04-03 19:00 | 19 | 3 | 0 | 0 | 0 | 2018-04-03 19:00 | 19 | 3 | 0 | 0 | 0
2018-04-03 20:00 | 20 | 3 | 86.627 | 18.0955 | 0 | 2018-04-03 20:00 | 20 | 3 | 0 | 0 | 0 | 2018-04-03 20:00 | 20 | 3 | 0 | 0 | 0 | 2018-04-03 20:00 | 20 | 3 | 0 | 0 | 0
2018-04-03 21:00 | 21 | 3 | 86.6239 | 18.0949 | 0 | 2018-04-03 21:00 | 21 | 3 | 0 | 0 | 0 | 2018-04-03 21:00 | 21 | 3 | 0 | 0 | 0 | 2018-04-03 21:00 | 21 | 3 | 0 | 0 | 0
2018-04-03 22:00 | 22 | 3 | 86.714 | 18.1137 | 0 | 2018-04-03 22:00 | 22 | 3 | 0 | 0 | 0 | 2018-04-03 22:00 | 22 | 3 | 0 | 0 | 0 | 2018-04-03 22:00 | 22 | 3 | 0 | 0 | 0
2018-04-03 23:00 | 23 | 3 | 86.8971 | 18.1519 | 0 | 2018-04-03 23:00 | 23 | 3 | 0 | 0 | 0 | 2018-04-03 23:00 | 23 | 3 | 0 | 0 | 0 | 2018-04-03 23:00 | 23 | 3 | 0 | 0 | 0
2018-04-04 | 0 | 4 | 0 | 0 | 0 | 2018-04-04 | 0 | 4 | 0 | 0 | 0 | 2018-04-04 | 0 | 4 | 86.6712 | 18.1047 | 0 | 2018-04-04 | 0 | 4 | 32.9351 | 6.8798 | 0
2018-04-04 01:00 | 1 | 4 | 0 | 0 | 0 | 2018-04-04 01:00 | 1 | 4 | 0 | 0 | 0 | 2018-04-04 01:00 | 1 | 4 | 86.511 | 18.0713 | 0 | 2018-04-04 01:00 | 1 | 4 | 32.8742 | 6.8671 | 0
2018-04-04 02:00 | 2 | 4 | 0 | 0 | 0 | 2018-04-04 02:00 | 2 | 4 | 0 | 0 | 0 | 2018-04-04 02:00 | 2 | 4 | 86.7628 | 18.1239 | 0 | 2018-04-04 02:00 | 2 | 4 | 32.9699 | 6.8871 | 0
2018-04-04 03:00 | 3 | 4 | 0 | 0 | 0 | 2018-04-04 03:00 | 3 | 4 | 0 | 0 | 0 | 2018-04-04 03:00 | 3 | 4 | 86.7384 | 18.1188 | 0 | 2018-04-04 03:00 | 3 | 4 | 32.9606 | 6.8851 | 0
2018-04-04 04:00 | 4 | 4 | 0 | 0 | 0 | 2018-04-04 04:00 | 4 | 4 | 0 | 0 | 0 | 2018-04-04 04:00 | 4 | 4 | 86.8376 | 18.1395 | 0 | 2018-04-04 04:00 | 4 | 4 | 32.9983 | 6.893 | 0
2018-04-04 05:00 | 5 | 4 | 0 | 0 | 0 | 2018-04-04 05:00 | 5 | 4 | 0 | 0 | 0 | 2018-04-04 05:00 | 5 | 4 | 87.0222 | 18.1781 | 0 | 2018-04-04 05:00 | 5 | 4 | 33.0684 | 6.9077 | 0
2018-04-04 06:00 | 6 | 4 | 0 | 0 | 0 | 2018-04-04 06:00 | 6 | 4 | 0 | 0 | 0 | 2018-04-04 06:00 | 6 | 4 | 86.9627 | 18.1656 | 0 | 2018-04-04 06:00 | 6 | 4 | 33.0458 | 6.9029 | 0
2018-04-04 07:00 | 7 | 4 | 0 | 0 | 0 | 2018-04-04 07:00 | 7 | 4 | 0 | 0 | 0 | 2018-04-04 07:00 | 7 | 4 | 87.1321 | 18.201 | 0 | 2018-04-04 07:00 | 7 | 4 | 33.1102 | 6.9164 | 0
2018-04-04 08:00 | 8 | 4 | 0 | 0 | 0 | 2018-04-04 08:00 | 8 | 4 | 0 | 0 | 0 | 2018-04-04 08:00 | 8 | 4 | 87.1931 | 18.2138 | 0 | 2018-04-04 08:00 | 8 | 4 | 33.1334 | 6.9212 | 0
2018-04-04 09:00 | 9 | 4 | 0 | 0 | 0 | 2018-04-04 09:00 | 9 | 4 | 0 | 0 | 0 | 2018-04-04 09:00 | 9 | 4 | 86.7155 | 18.114 | 0 | 2018-04-04 09:00 | 9 | 4 | 32.9519 | 6.8833 | 0
2018-04-04 10:00 | 10 | 4 | 0 | 0 | 0 | 2018-04-04 10:00 | 10 | 4 | 0 | 0 | 0 | 2018-04-04 10:00 | 10 | 4 | 86.6743 | 18.1054 | 0 | 2018-04-04 10:00 | 10 | 4 | 32.9362 | 6.88 | 0
2018-04-04 11:00 | 11 | 4 | 0 | 0 | 0 | 2018-04-04 11:00 | 11 | 4 | 0 | 0 | 0 | 2018-04-04 11:00 | 11 | 4 | 86.8956 | 18.1516 | 0 | 2018-04-04 11:00 | 11 | 4 | 33.0203 | 6.8976 | 0
2018-04-04 12:00 | 12 | 4 | 0 | 0 | 0 | 2018-04-04 12:00 | 12 | 4 | 0 | 0 | 0 | 2018-04-04 12:00 | 12 | 4 | 86.9276 | 18.1583 | 0 | 2018-04-04 12:00 | 12 | 4 | 33.0325 | 6.9002 | 0
2018-04-04 13:00 | 13 | 4 | 0 | 0 | 0 | 2018-04-04 13:00 | 13 | 4 | 0 | 0 | 0 | 2018-04-04 13:00 | 13 | 4 | 87.2541 | 18.2265 | 0 | 2018-04-04 13:00 | 13 | 4 | 33.1566 | 6.9261 | 0
2018-04-04 14:00 | 14 | 4 | 0 | 0 | 0 | 2018-04-04 14:00 | 14 | 4 | 0 | 0 | 0 | 2018-04-04 14:00 | 14 | 4 | 87.4037 | 18.2578 | 0 | 2018-04-04 14:00 | 14 | 4 | 33.2134 | 6.9379 | 0
2018-04-04 15:00 | 15 | 4 | 0 | 0 | 0 | 2018-04-04 15:00 | 15 | 4 | 0 | 0 | 0 | 2018-04-04 15:00 | 15 | 4 | 87.2129 | 18.2179 | 0 | 2018-04-04 15:00 | 15 | 4 | 33.1409 | 6.9228 | 0
2018-04-04 16:00 | 16 | 4 | 0 | 0 | 0 | 2018-04-04 16:00 | 16 | 4 | 0 | 0 | 0 | 2018-04-04 16:00 | 16 | 4 | 86.9718 | 18.1675 | 0 | 2018-04-04 16:00 | 16 | 4 | 33.0493 | 6.9037 | 0
2018-04-04 17:00 | 17 | 4 | 0 | 0 | 0 | 2018-04-04 17:00 | 17 | 4 | 0 | 0 | 0 | 2018-04-04 17:00 | 17 | 4 | 87.1397 | 18.2026 | 0 | 2018-04-04 17:00 | 17 | 4 | 33.1131 | 6.917 | 0
2018-04-04 18:00 | 18 | 4 | 0 | 0 | 0 | 2018-04-04 18:00 | 18 | 4 | 0 | 0 | 0 | 2018-04-04 18:00 | 18 | 4 | 87.2435 | 18.2243 | 0 | 2018-04-04 18:00 | 18 | 4 | 33.1525 | 6.9252 | 0
2018-04-04 19:00 | 19 | 4 | 0 | 0 | 0 | 2018-04-04 19:00 | 19 | 4 | 0 | 0 | 0 | 2018-04-04 19:00 | 19 | 4 | 86.8894 | 18.1503 | 0 | 2018-04-04 19:00 | 19 | 4 | 33.018 | 6.8971 | 0
2018-04-04 20:00 | 20 | 4 | 0 | 0 | 0 | 2018-04-04 20:00 | 20 | 4 | 0 | 0 | 0 | 2018-04-04 20:00 | 20 | 4 | 87.1839 | 18.2118 | 0 | 2018-04-04 20:00 | 20 | 4 | 33.1299 | 6.9205 | 0
2018-04-04 21:00 | 21 | 4 | 0 | 0 | 0 | 2018-04-04 21:00 | 21 | 4 | 0 | 0 | 0 | 2018-04-04 21:00 | 21 | 4 | 87.2419 | 18.224 | 0 | 2018-04-04 21:00 | 21 | 4 | 33.1519 | 6.9251 | 0
2018-04-04 22:00 | 22 | 4 | 0 | 0 | 0 | 2018-04-04 22:00 | 22 | 4 | 0 | 0 | 0 | 2018-04-04 22:00 | 22 | 4 | 87.1733 | 18.2096 | 0 | 2018-04-04 22:00 | 22 | 4 | 33.1259 | 6.9197 | 0
2018-04-04 23:00 | 23 | 4 | 0 | 0 | 0 | 2018-04-04 23:00 | 23 | 4 | 0 | 0 | 0 | 2018-04-04 23:00 | 23 | 4 | 87.2557 | 18.2268 | 0 | 2018-04-04 23:00 | 23 | 4 | 33.1572 | 6.9262 | 0
2018-04-05 | 0 | 5 | 86.5492 | 18.0793 | 0 | 2018-04-05 | 0 | 5 | 0 | 0 | 0 | 2018-04-05 | 0 | 5 | 0 | 0 | 0 | 2018-04-05 | 0 | 5 | 0 | 0 | 0
2018-04-05 01:00 | 1 | 5 | 86.7201 | 18.115 | 0 | 2018-04-05 01:00 | 1 | 5 | 0 | 0 | 0 | 2018-04-05 01:00 | 1 | 5 | 0 | 0 | 0 | 2018-04-05 01:00 | 1 | 5 | 0 | 0 | 0
2018-04-05 02:00 | 2 | 5 | 86.5095 | 18.071 | 0 | 2018-04-05 02:00 | 2 | 5 | 0 | 0 | 0 | 2018-04-05 02:00 | 2 | 5 | 0 | 0 | 0 | 2018-04-05 02:00 | 2 | 5 | 0 | 0 | 0
2018-04-05 03:00 | 3 | 5 | 86.4576 | 18.0601 | 0 | 2018-04-05 03:00 | 3 | 5 | 0 | 0 | 0 | 2018-04-05 03:00 | 3 | 5 | 0 | 0 | 0 | 2018-04-05 03:00 | 3 | 5 | 0 | 0 | 0
2018-04-05 04:00 | 4 | 5 | 86.6316 | 18.0965 | 0 | 2018-04-05 04:00 | 4 | 5 | 0 | 0 | 0 | 2018-04-05 04:00 | 4 | 5 | 0 | 0 | 0 | 2018-04-05 04:00 | 4 | 5 | 0 | 0 | 0
2018-04-05 05:00 | 5 | 5 | 86.569 | 18.0834 | 0 | 2018-04-05 05:00 | 5 | 5 | 0 | 0 | 0 | 2018-04-05 05:00 | 5 | 5 | 0 | 0 | 0 | 2018-04-05 05:00 | 5 | 5 | 0 | 0 | 0
2018-04-05 06:00 | 6 | 5 | 86.6468 | 18.0997 | 0 | 2018-04-05 06:00 | 6 | 5 | 0 | 0 | 0 | 2018-04-05 06:00 | 6 | 5 | 0 | 0 | 0 | 2018-04-05 06:00 | 6 | 5 | 0 | 0 | 0
2018-04-05 07:00 | 7 | 5 | 86.6361 | 18.0974 | 0 | 2018-04-05 07:00 | 7 | 5 | 0 | 0 | 0 | 2018-04-05 07:00 | 7 | 5 | 0 | 0 | 0 | 2018-04-05 07:00 | 7 | 5 | 0 | 0 | 0
2018-04-05 08:00 | 8 | 5 | 86.6819 | 18.107 | 0 | 2018-04-05 08:00 | 8 | 5 | 0 | 0 | 0 | 2018-04-05 08:00 | 8 | 5 | 0 | 0 | 0 | 2018-04-05 08:00 | 8 | 5 | 0 | 0 | 0
2018-04-05 09:00 | 9 | 5 | 86.7094 | 18.1127 | 0 | 2018-04-05 09:00 | 9 | 5 | 0 | 0 | 0 | 2018-04-05 09:00 | 9 | 5 | 0 | 0 | 0 | 2018-04-05 09:00 | 9 | 5 | 0 | 0 | 0
2018-04-05 10:00 | 10 | 5 | 86.7933 | 18.1303 | 0 | 2018-04-05 10:00 | 10 | 5 | 0 | 0 | 0 | 2018-04-05 10:00 | 10 | 5 | 0 | 0 | 0 | 2018-04-05 10:00 | 10 | 5 | 0 | 0 | 0
2018-04-05 11:00 | 11 | 5 | 86.8009 | 18.1318 | 0 | 2018-04-05 11:00 | 11 | 5 | 0 | 0 | 0 | 2018-04-05 11:00 | 11 | 5 | 0 | 0 | 0 | 2018-04-05 11:00 | 11 | 5 | 0 | 0 | 0
2018-04-05 12:00 | 12 | 5 | 86.6728 | 18.1051 | 0 | 2018-04-05 12:00 | 12 | 5 | 0 | 0 | 0 | 2018-04-05 12:00 | 12 | 5 | 0 | 0 | 0 | 2018-04-05 12:00 | 12 | 5 | 0 | 0 | 0
2018-04-05 13:00 | 13 | 5 | 86.6316 | 18.0965 | 0 | 2018-04-05 13:00 | 13 | 5 | 0 | 0 | 0 | 2018-04-05 13:00 | 13 | 5 | 0 | 0 | 0 | 2018-04-05 13:00 | 13 | 5 | 0 | 0 | 0
2018-04-05 14:00 | 14 | 5 | 86.6316 | 18.0965 | 0 | 2018-04-05 14:00 | 14 | 5 | 0 | 0 | 0 | 2018-04-05 14:00 | 14 | 5 | 0 | 0 | 0 | 2018-04-05 14:00 | 14 | 5 | 0 | 0 | 0
2018-04-05 15:00 | 15 | 5 | 86.6636 | 18.1032 | 0 | 2018-04-05 15:00 | 15 | 5 | 0 | 0 | 0 | 2018-04-05 15:00 | 15 | 5 | 0 | 0 | 0 | 2018-04-05 15:00 | 15 | 5 | 0 | 0 | 0
2018-04-05 16:00 | 16 | 5 | 86.5568 | 18.0808 | 0 | 2018-04-05 16:00 | 16 | 5 | 0 | 0 | 0 | 2018-04-05 16:00 | 16 | 5 | 0 | 0 | 0 | 2018-04-05 16:00 | 16 | 5 | 0 | 0 | 0
2018-04-05 17:00 | 17 | 5 | 86.6865 | 18.1079 | 0 | 2018-04-05 17:00 | 17 | 5 | 0 | 0 | 0 | 2018-04-05 17:00 | 17 | 5 | 0 | 0 | 0 | 2018-04-05 17:00 | 17 | 5 | 0 | 0 | 0
2018-04-05 18:00 | 18 | 5 | 86.7262 | 18.1162 | 0 | 2018-04-05 18:00 | 18 | 5 | 0 | 0 | 0 | 2018-04-05 18:00 | 18 | 5 | 0 | 0 | 0 | 2018-04-05 18:00 | 18 | 5 | 0 | 0 | 0
2018-04-05 19:00 | 19 | 5 | 86.5187 | 18.0729 | 0 | 2018-04-05 19:00 | 19 | 5 | 0 | 0 | 0 | 2018-04-05 19:00 | 19 | 5 | 0 | 0 | 0 | 2018-04-05 19:00 | 19 | 5 | 0 | 0 | 0
2018-04-05 20:00 | 20 | 5 | 86.5766 | 18.085 | 0 | 2018-04-05 20:00 | 20 | 5 | 0 | 0 | 0 | 2018-04-05 20:00 | 20 | 5 | 0 | 0 | 0 | 2018-04-05 20:00 | 20 | 5 | 0 | 0 | 0
2018-04-05 21:00 | 21 | 5 | 86.6194 | 18.0939 | 0 | 2018-04-05 21:00 | 21 | 5 | 0 | 0 | 0 | 2018-04-05 21:00 | 21 | 5 | 0 | 0 | 0 | 2018-04-05 21:00 | 21 | 5 | 0 | 0 | 0
2018-04-05 22:00 | 22 | 5 | 86.6743 | 18.1054 | 0 | 2018-04-05 22:00 | 22 | 5 | 0 | 0 | 0 | 2018-04-05 22:00 | 22 | 5 | 0 | 0 | 0 | 2018-04-05 22:00 | 22 | 5 | 0 | 0 | 0
2018-04-05 23:00 | 23 | 5 | 86.5644 | 18.0824 | 0 | 2018-04-05 23:00 | 23 | 5 | 0 | 0 | 0 | 2018-04-05 23:00 | 23 | 5 | 0 | 0 | 0 | 2018-04-05 23:00 | 23 | 5 | 0 | 0 | 0
2018-04-06 | 0 | 6 | 86.2226 | 18.011 | 0 | 2018-04-06 | 0 | 6 | 86.688 | 18.1083 | 0 | 2018-04-06 | 0 | 6 | 0 | 0 | 0 | 2018-04-06 | 0 | 6 | 32.9414 | 6.8811 | 0
2018-04-06 01:00 | 1 | 6 | 86.1128 | 17.9881 | 0 | 2018-04-06 01:00 | 1 | 6 | 86.5232 | 18.0738 | 0 | 2018-04-06 01:00 | 1 | 6 | 0 | 0 | 0 | 2018-04-06 01:00 | 1 | 6 | 32.8788 | 6.8681 | 0
2018-04-06 02:00 | 2 | 6 | 86.2791 | 18.0228 | 0 | 2018-04-06 02:00 | 2 | 6 | 86.6896 | 18.1086 | 0 | 2018-04-06 02:00 | 2 | 6 | 0 | 0 | 0 | 2018-04-06 02:00 | 2 | 6 | 32.942 | 6.8813 | 0
2018-04-06 03:00 | 3 | 6 | 86.0014 | 17.9648 | 0 | 2018-04-06 03:00 | 3 | 6 | 86.4485 | 18.0582 | 0 | 2018-04-06 03:00 | 3 | 6 | 0 | 0 | 0 | 2018-04-06 03:00 | 3 | 6 | 32.8504 | 6.8621 | 0
2018-04-06 04:00 | 4 | 6 | 86.0533 | 17.9757 | 0 | 2018-04-06 04:00 | 4 | 6 | 86.4347 | 18.0553 | 0 | 2018-04-06 04:00 | 4 | 6 | 0 | 0 | 0 | 2018-04-06 04:00 | 4 | 6 | 32.8452 | 6.861 | 0
2018-04-06 05:00 | 5 | 6 | 86.2257 | 18.0117 | 0 | 2018-04-06 05:00 | 5 | 6 | 86.6117 | 18.0923 | 0 | 2018-04-06 05:00 | 5 | 6 | 0 | 0 | 0 | 2018-04-06 05:00 | 5 | 6 | 32.9124 | 6.8751 | 0
2018-04-06 06:00 | 6 | 6 | 86.4332 | 18.055 | 0 | 2018-04-06 06:00 | 6 | 6 | 86.9352 | 18.1599 | 0 | 2018-04-06 06:00 | 6 | 6 | 0 | 0 | 0 | 2018-04-06 06:00 | 6 | 6 | 33.0354 | 6.9008 | 0
2018-04-06 07:00 | 7 | 6 | 86.5873 | 18.0872 | 0 | 2018-04-06 07:00 | 7 | 6 | 87.0619 | 18.1864 | 0 | 2018-04-06 07:00 | 7 | 6 | 0 | 0 | 0 | 2018-04-06 07:00 | 7 | 6 | 33.0835 | 6.9108 | 0
2018-04-06 08:00 | 8 | 6 | 86.3691 | 18.0416 | 0 | 2018-04-06 08:00 | 8 | 6 | 86.7811 | 18.1277 | 0 | 2018-04-06 08:00 | 8 | 6 | 0 | 0 | 0 | 2018-04-06 08:00 | 8 | 6 | 32.9768 | 6.8885 | 0
2018-04-06 09:00 | 9 | 6 | 86.334 | 18.0343 | 0 | 2018-04-06 09:00 | 9 | 6 | 86.7399 | 18.1191 | 0 | 2018-04-06 09:00 | 9 | 6 | 0 | 0 | 0 | 2018-04-06 09:00 | 9 | 6 | 32.9612 | 6.8853 | 0
2018-04-06 10:00 | 10 | 6 | 86.5126 | 18.0716 | 0 | 2018-04-06 10:00 | 10 | 6 | 86.862 | 18.1446 | 0 | 2018-04-06 10:00 | 10 | 6 | 0 | 0 | 0 | 2018-04-06 10:00 | 10 | 6 | 33.0076 | 6.8949 | 0
2018-04-06 11:00 | 11 | 6 | 86.5003 | 18.069 | 0 | 2018-04-06 11:00 | 11 | 6 | 86.9306 | 18.1589 | 0 | 2018-04-06 11:00 | 11 | 6 | 0 | 0 | 0 | 2018-04-06 11:00 | 11 | 6 | 33.0336 | 6.9004 | 0
2018-04-06 12:00 | 12 | 6 | 86.7002 | 18.1108 | 0 | 2018-04-06 12:00 | 12 | 6 | 87.1412 | 18.2029 | 0 | 2018-04-06 12:00 | 12 | 6 | 0 | 0 | 0 | 2018-04-06 12:00 | 12 | 6 | 33.1137 | 6.9171 | 0
2018-04-06 13:00 | 13 | 6 | 86.363 | 18.0404 | 0 | 2018-04-06 13:00 | 13 | 6 | 86.8009 | 18.1318 | 0 | 2018-04-06 13:00 | 13 | 6 | 0 | 0 | 0 | 2018-04-06 13:00 | 13 | 6 | 32.9843 | 6.8901 | 0
2018-04-06 14:00 | 14 | 6 | 86.4408 | 18.0566 | 0 | 2018-04-06 14:00 | 14 | 6 | 86.8635 | 18.1449 | 0 | 2018-04-06 14:00 | 14 | 6 | 0 | 0 | 0 | 2018-04-06 14:00 | 14 | 6 | 33.0081 | 6.8951 | 0
2018-04-06 15:00 | 15 | 6 | 86.2943 | 18.026 | 0 | 2018-04-06 15:00 | 15 | 6 | 86.6743 | 18.1054 | 0 | 2018-04-06 15:00 | 15 | 6 | 0 | 0 | 0 | 2018-04-06 15:00 | 15 | 6 | 32.9362 | 6.88 | 0
2018-04-06 16:00 | 16 | 6 | 86.3706 | 18.042 | 0 | 2018-04-06 16:00 | 16 | 6 | 86.7491 | 18.121 | 0 | 2018-04-06 16:00 | 16 | 6 | 0 | 0 | 0 | 2018-04-06 16:00 | 16 | 6 | 32.9647 | 6.886 | 0
2018-04-06 17:00 | 17 | 6 | 86.2882 | 18.0247 | 0 | 2018-04-06 17:00 | 17 | 6 | 86.7445 | 18.1201 | 0 | 2018-04-06 17:00 | 17 | 6 | 0 | 0 | 0 | 2018-04-06 17:00 | 17 | 6 | 32.9629 | 6.8856 | 0
2018-04-06 18:00 | 18 | 6 | 86.1875 | 18.0037 | 0 | 2018-04-06 18:00 | 18 | 6 | 86.6667 | 18.1038 | 0 | 2018-04-06 18:00 | 18 | 6 | 0 | 0 | 0 | 2018-04-06 18:00 | 18 | 6 | 32.9333 | 6.8794 | 0
2018-04-06 19:00 | 19 | 6 | 86.099 | 17.9852 | 0 | 2018-04-06 19:00 | 19 | 6 | 86.5431 | 18.078 | 0 | 2018-04-06 19:00 | 19 | 6 | 0 | 0 | 0 | 2018-04-06 19:00 | 19 | 6 | 32.8864 | 6.8696 | 0
2018-04-06 20:00 | 20 | 6 | 86.1997 | 18.0063 | 0 | 2018-04-06 20:00 | 20 | 6 | 86.5187 | 18.0729 | 0 | 2018-04-06 20:00 | 20 | 6 | 0 | 0 | 0 | 2018-04-06 20:00 | 20 | 6 | 32.8771 | 6.8677 | 0
2018-04-06 21:00 | 21 | 6 | 86.3767 | 18.0432 | 0 | 2018-04-06 21:00 | 21 | 6 | 86.7247 | 18.1159 | 0 | 2018-04-06 21:00 | 21 | 6 | 0 | 0 | 0 | 2018-04-06 21:00 | 21 | 6 | 32.9554 | 6.8841 | 0
2018-04-06 22:00 | 22 | 6 | 86.3691 | 18.0416 | 0 | 2018-04-06 22:00 | 22 | 6 | 86.7659 | 18.1245 | 0 | 2018-04-06 22:00 | 22 | 6 | 0 | 0 | 0 | 2018-04-06 22:00 | 22 | 6 | 32.971 | 6.8873 | 0
2018-04-06 23:00 | 23 | 6 | 86.4012 | 18.0483 | 0 | 2018-04-06 23:00 | 23 | 6 | 86.7918 | 18.1299 | 0 | 2018-04-06 23:00 | 23 | 6 | 0 | 0 | 0 | 2018-04-06 23:00 | 23 | 6 | 32.9809 | 6.8894 | 0
2018-04-07 | 0 | 7 | 86.0121 | 17.9671 | 0 | 2018-04-07 | 0 | 7 | 0 | 0 | 0 | 2018-04-07 | 0 | 7 | 86.5507 | 18.0796 | 0 | 2018-04-07 | 0 | 7 | 32.8893 | 6.8702 | 0
2018-04-07 01:00 | 1 | 7 | 85.919 | 17.9476 | 0 | 2018-04-07 01:00 | 1 | 7 | 0 | 0 | 0 | 2018-04-07 01:00 | 1 | 7 | 86.5324 | 18.0758 | 0 | 2018-04-07 01:00 | 1 | 7 | 32.8823 | 6.8688 | 0
2018-04-07 02:00 | 2 | 7 | 86.0533 | 17.9757 | 0 | 2018-04-07 02:00 | 2 | 7 | 0 | 0 | 0 | 2018-04-07 02:00 | 2 | 7 | 86.6453 | 18.0993 | 0 | 2018-04-07 02:00 | 2 | 7 | 32.9252 | 6.8777 | 0
2018-04-07 03:00 | 3 | 7 | 86.1677 | 17.9996 | 0 | 2018-04-07 03:00 | 3 | 7 | 0 | 0 | 0 | 2018-04-07 03:00 | 3 | 7 | 86.7002 | 18.1108 | 0 | 2018-04-07 03:00 | 3 | 7 | 32.9461 | 6.8821 | 0
2018-04-07 04:00 | 4 | 7 | 86.3081 | 18.0289 | 0 | 2018-04-07 04:00 | 4 | 7 | 0 | 0 | 0 | 2018-04-07 04:00 | 4 | 7 | 86.8513 | 18.1424 | 0 | 2018-04-07 04:00 | 4 | 7 | 33.0035 | 6.8941 | 0
2018-04-07 05:00 | 5 | 7 | 86.2562 | 18.0181 | 0 | 2018-04-07 05:00 | 5 | 7 | 0 | 0 | 0 | 2018-04-07 05:00 | 5 | 7 | 86.8605 | 18.1443 | 0 | 2018-04-07 05:00 | 5 | 7 | 33.007 | 6.8948 | 0
2018-04-07 06:00 | 6 | 7 | 86.1234 | 17.9903 | 0 | 2018-04-07 06:00 | 6 | 7 | 0 | 0 | 0 | 2018-04-07 06:00 | 6 | 7 | 86.6682 | 18.1041 | 0 | 2018-04-07 06:00 | 6 | 7 | 32.9339 | 6.8796 | 0
2018-04-07 07:00 | 7 | 7 | 86.1906 | 18.0044 | 0 | 2018-04-07 07:00 | 7 | 7 | 0 | 0 | 0 | 2018-04-07 07:00 | 7 | 7 | 86.7247 | 18.1159 | 0 | 2018-04-07 07:00 | 7 | 7 | 32.9554 | 6.8841 | 0
2018-04-07 08:00 | 8 | 7 | 86.36 | 18.0397 | 0 | 2018-04-07 08:00 | 8 | 7 | 0 | 0 | 0 | 2018-04-07 08:00 | 8 | 7 | 86.952 | 18.1634 | 0 | 2018-04-07 08:00 | 8 | 7 | 33.0418 | 6.9021 | 0
2018-04-07 09:00 | 9 | 7 | 86.4912 | 18.0671 | 0 | 2018-04-07 09:00 | 9 | 7 | 0 | 0 | 0 | 2018-04-07 09:00 | 9 | 7 | 87.0588 | 18.1857 | 0 | 2018-04-07 09:00 | 9 | 7 | 33.0823 | 6.9106 | 0
2018-04-07 10:00 | 10 | 7 | 86.1982 | 18.0059 | 0 | 2018-04-07 10:00 | 10 | 7 | 0 | 0 | 0 | 2018-04-07 10:00 | 10 | 7 | 86.6392 | 18.0981 | 0 | 2018-04-07 10:00 | 10 | 7 | 32.9229 | 6.8773 | 0
2018-04-07 11:00 | 11 | 7 | 86.1707 | 18.0002 | 0 | 2018-04-07 11:00 | 11 | 7 | 0 | 0 | 0 | 2018-04-07 11:00 | 11 | 7 | 86.8849 | 18.1494 | 0 | 2018-04-07 11:00 | 11 | 7 | 33.0163 | 6.8968 | 0
2018-04-07 12:00 | 12 | 7 | 86.5019 | 18.0694 | 0 | 2018-04-07 12:00 | 12 | 7 | 0 | 0 | 0 | 2018-04-07 12:00 | 12 | 7 | 87.1504 | 18.2048 | 0 | 2018-04-07 12:00 | 12 | 7 | 33.1172 | 6.9178 | 0
2018-04-07 13:00 | 13 | 7 | 86.6148 | 18.093 | 0 | 2018-04-07 13:00 | 13 | 7 | 0 | 0 | 0 | 2018-04-07 13:00 | 13 | 7 | 87.3167 | 18.2396 | 0 | 2018-04-07 13:00 | 13 | 7 | 33.1803 | 6.931 | 0
2018-04-07 14:00 | 14 | 7 | 86.4439 | 18.0573 | 0 | 2018-04-07 14:00 | 14 | 7 | 0 | 0 | 0 | 2018-04-07 14:00 | 14 | 7 | 87.0832 | 18.1908 | 0 | 2018-04-07 14:00 | 14 | 7 | 33.0916 | 6.9125 | 0
2018-04-07 15:00 | 15 | 7 | 86.5522 | 18.0799 | 0 | 2018-04-07 15:00 | 15 | 7 | 0 | 0 | 0 | 2018-04-07 15:00 | 15 | 7 | 87.2938 | 18.2348 | 0 | 2018-04-07 15:00 | 15 | 7 | 33.1716 | 6.9292 | 0
2018-04-07 16:00 | 16 | 7 | 86.5644 | 18.0824 | 0 | 2018-04-07 16:00 | 16 | 7 | 0 | 0 | 0 | 2018-04-07 16:00 | 16 | 7 | 87.3579 | 18.2482 | 0 | 2018-04-07 16:00 | 16 | 7 | 33.196 | 6.9343 | 0
2018-04-07 17:00 | 17 | 7 | 86.7445 | 18.1201 | 0 | 2018-04-07 17:00 | 17 | 7 | 0 | 0 | 0 | 2018-04-07 17:00 | 17 | 7 | 87.57 | 18.2925 | 0 | 2018-04-07 17:00 | 17 | 7 | 33.2766 | 6.9511 | 0
2018-04-07 18:00 | 18 | 7 | 86.4668 | 18.062 | 0 | 2018-04-07 18:00 | 18 | 7 | 0 | 0 | 0 | 2018-04-07 18:00 | 18 | 7 | 87.3014 | 18.2364 | 0 | 2018-04-07 18:00 | 18 | 7 | 33.1745 | 6.9298 | 0
2018-04-07 19:00 | 19 | 7 | 86.3661 | 18.041 | 0 | 2018-04-07 19:00 | 19 | 7 | 0 | 0 | 0 | 2018-04-07 19:00 | 19 | 7 | 87.0954 | 18.1934 | 0 | 2018-04-07 19:00 | 19 | 7 | 33.0963 | 6.9135 | 0
2018-04-07 20:00 | 20 | 7 | 86.1173 | 17.989 | 0 | 2018-04-07 20:00 | 20 | 7 | 0 | 0 | 0 | 2018-04-07 20:00 | 20 | 7 | 86.891 | 18.1507 | 0 | 2018-04-07 20:00 | 20 | 7 | 33.0186 | 6.8973 | 0
2018-04-07 21:00 | 21 | 7 | 86.1555 | 17.997 | 0 | 2018-04-07 21:00 | 21 | 7 | 0 | 0 | 0 | 2018-04-07 21:00 | 21 | 7 | 86.9245 | 18.1577 | 0 | 2018-04-07 21:00 | 21 | 7 | 33.0313 | 6.8999 | 0
2018-04-07 22:00 | 22 | 7 | 86.2211 | 18.0107 | 0 | 2018-04-07 22:00 | 22 | 7 | 0 | 0 | 0 | 2018-04-07 22:00 | 22 | 7 | 87.0054 | 18.1746 | 0 | 2018-04-07 22:00 | 22 | 7 | 33.0621 | 6.9063 | 0
2018-04-07 23:00 | 23 | 7 | 86.2226 | 18.011 | 0 | 2018-04-07 23:00 | 23 | 7 | 0 | 0 | 0 | 2018-04-07 23:00 | 23 | 7 | 87.0787 | 18.1899 | 0 | 2018-04-07 23:00 | 23 | 7 | 33.0899 | 6.9122 | 0
2018-04-08 | 0 | 1 | 86.2364 | 18.0139 | 0 | 2018-04-08 | 0 | 1 | 86.7994 | 18.1315 | 0 | 2018-04-08 | 0 | 1 | 0 | 0 | 0 | 2018-04-08 | 0 | 1 | 32.9838 | 6.89 | 0
2018-04-08 01:00 | 1 | 1 | 86.3188 | 18.0311 | 0 | 2018-04-08 01:00 | 1 | 1 | 86.952 | 18.1634 | 0 | 2018-04-08 01:00 | 1 | 1 | 0 | 0 | 0 | 2018-04-08 01:00 | 1 | 1 | 33.0418 | 6.9021 | 0
2018-04-08 02:00 | 2 | 1 | 86.2119 | 18.0088 | 0 | 2018-04-08 02:00 | 2 | 1 | 86.8177 | 18.1353 | 0 | 2018-04-08 02:00 | 2 | 1 | 0 | 0 | 0 | 2018-04-08 02:00 | 2 | 1 | 32.9907 | 6.8914 | 0
2018-04-08 03:00 | 3 | 1 | 86.1845 | 18.0031 | 0 | 2018-04-08 03:00 | 3 | 1 | 86.7857 | 18.1287 | 0 | 2018-04-08 03:00 | 3 | 1 | 0 | 0 | 0 | 2018-04-08 03:00 | 3 | 1 | 32.9786 | 6.8889 | 0
2018-04-08 04:00 | 4 | 1 | 86.2455 | 18.0158 | 0 | 2018-04-08 04:00 | 4 | 1 | 86.833 | 18.1385 | 0 | 2018-04-08 04:00 | 4 | 1 | 0 | 0 | 0 | 2018-04-08 04:00 | 4 | 1 | 32.9965 | 6.8926 | 0
2018-04-08 05:00 | 5 | 1 | 86.2333 | 18.0133 | 0 | 2018-04-08 05:00 | 5 | 1 | 86.833 | 18.1385 | 0 | 2018-04-08 05:00 | 5 | 1 | 0 | 0 | 0 | 2018-04-08 05:00 | 5 | 1 | 32.9965 | 6.8926 | 0
2018-04-08 06:00 | 6 | 1 | 86.2776 | 18.0225 | 0 | 2018-04-08 06:00 | 6 | 1 | 86.8528 | 18.1427 | 0 | 2018-04-08 06:00 | 6 | 1 | 0 | 0 | 0 | 2018-04-08 06:00 | 6 | 1 | 33.0041 | 6.8942 | 0
2018-04-08 07:00 | 7 | 1 | 86.2867 | 18.0244 | 0 | 2018-04-08 07:00 | 7 | 1 | 86.8452 | 18.1411 | 0 | 2018-04-08 07:00 | 7 | 1 | 0 | 0 | 0 | 2018-04-08 07:00 | 7 | 1 | 33.0012 | 6.8936 | 0
2018-04-08 08:00 | 8 | 1 | 86.2989 | 18.027 | 0 | 2018-04-08 08:00 | 8 | 1 | 86.9032 | 18.1532 | 0 | 2018-04-08 08:00 | 8 | 1 | 0 | 0 | 0 | 2018-04-08 08:00 | 8 | 1 | 33.0232 | 6.8982 | 0
2018-04-08 09:00 | 9 | 1 | 86.2867 | 18.0244 | 0 | 2018-04-08 09:00 | 9 | 1 | 86.8162 | 18.135 | 0 | 2018-04-08 09:00 | 9 | 1 | 0 | 0 | 0 | 2018-04-08 09:00 | 9 | 1 | 32.9902 | 6.8913 | 0
2018-04-08 10:00 | 10 | 1 | 86.2882 | 18.0247 | 0 | 2018-04-08 10:00 | 10 | 1 | 86.8528 | 18.1427 | 0 | 2018-04-08 10:00 | 10 | 1 | 0 | 0 | 0 | 2018-04-08 10:00 | 10 | 1 | 33.0041 | 6.8942 | 0
2018-04-08 11:00 | 11 | 1 | 86.1845 | 18.0031 | 0 | 2018-04-08 11:00 | 11 | 1 | 86.743 | 18.1197 | 0 | 2018-04-08 11:00 | 11 | 1 | 0 | 0 | 0 | 2018-04-08 11:00 | 11 | 1 | 32.9623 | 6.8855 | 0
2018-04-08 12:00 | 12 | 1 | 86.1418 | 17.9942 | 0 | 2018-04-08 12:00 | 12 | 1 | 86.714 | 18.1137 | 0 | 2018-04-08 12:00 | 12 | 1 | 0 | 0 | 0 | 2018-04-08 12:00 | 12 | 1 | 32.9513 | 6.8832 | 0
2018-04-08 13:00 | 13 | 1 | 86.1479 | 17.9954 | 0 | 2018-04-08 13:00 | 13 | 1 | 86.7659 | 18.1245 | 0 | 2018-04-08 13:00 | 13 | 1 | 0 | 0 | 0 | 2018-04-08 13:00 | 13 | 1 | 32.971 | 6.8873 | 0
2018-04-08 14:00 | 14 | 1 | 86.1112 | 17.9878 | 0 | 2018-04-08 14:00 | 14 | 1 | 86.7018 | 18.1111 | 0 | 2018-04-08 14:00 | 14 | 1 | 0 | 0 | 0 | 2018-04-08 14:00 | 14 | 1 | 32.9467 | 6.8822 | 0
2018-04-08 15:00 | 15 | 1 | 86.2455 | 18.0158 | 0 | 2018-04-08 15:00 | 15 | 1 | 86.8482 | 18.1417 | 0 | 2018-04-08 15:00 | 15 | 1 | 0 | 0 | 0 | 2018-04-08 15:00 | 15 | 1 | 33.0023 | 6.8939 | 0
2018-04-08 16:00 | 16 | 1 | 86.3447 | 18.0365 | 0 | 2018-04-08 16:00 | 16 | 1 | 86.9398 | 18.1609 | 0 | 2018-04-08 16:00 | 16 | 1 | 0 | 0 | 0 | 2018-04-08 16:00 | 16 | 1 | 33.0371 | 6.9011 | 0
2018-04-08 17:00 | 17 | 1 | 86.4805 | 18.0649 | 0 | 2018-04-08 17:00 | 17 | 1 | 86.9856 | 18.1704 | 0 | 2018-04-08 17:00 | 17 | 1 | 0 | 0 | 0 | 2018-04-08 17:00 | 17 | 1 | 33.0545 | 6.9048 | 0
2018-04-08 18:00 | 18 | 1 | 86.4332 | 18.055 | 0 | 2018-04-08 18:00 | 18 | 1 | 86.92 | 18.1567 | 0 | 2018-04-08 18:00 | 18 | 1 | 0 | 0 | 0 | 2018-04-08 18:00 | 18 | 1 | 33.0296 | 6.8996 | 0
2018-04-08 19:00 | 19 | 1 | 85.6794 | 17.8976 | 0 | 2018-04-08 19:00 | 19 | 1 | 85.9266 | 17.9492 | 0 | 2018-04-08 19:00 | 19 | 1 | 0 | 0 | 0 | 2018-04-08 19:00 | 19 | 1 | 32.6521 | 6.8207 | 0
2018-04-08 20:00 | 20 | 1 | 86.3294 | 18.0333 | 0 | 2018-04-08 20:00 | 20 | 1 | 86.5888 | 18.0875 | 0 | 2018-04-08 20:00 | 20 | 1 | 0 | 0 | 0 | 2018-04-08 20:00 | 20 | 1 | 32.9037 | 6.8733 | 0
2018-04-08 21:00 | 21 | 1 | 86.3569 | 18.0391 | 0 | 2018-04-08 21:00 | 21 | 1 | 86.6728 | 18.1051 | 0 | 2018-04-08 21:00 | 21 | 1 | 0 | 0 | 0 | 2018-04-08 21:00 | 21 | 1 | 32.9357 | 6.8799 | 0
2018-04-08 22:00 | 22 | 1 | 86.4881 | 18.0665 | 0 | 2018-04-08 22:00 | 22 | 1 | 86.8086 | 18.1334 | 0 | 2018-04-08 22:00 | 22 | 1 | 0 | 0 | 0 | 2018-04-08 22:00 | 22 | 1 | 32.9873 | 6.8907 | 0
2018-04-08 23:00 | 23 | 1 | 86.4332 | 18.055 | 0 | 2018-04-08 23:00 | 23 | 1 | 86.7353 | 18.1181 | 0 | 2018-04-08 23:00 | 23 | 1 | 0 | 0 | 0 | 2018-04-08 23:00 | 23 | 1 | 32.9594 | 6.8849 | 0
2018-04-09 | 0 | 2 | 86.4088 | 18.0499 | 0 | 2018-04-09 | 0 | 2 | 86.7002 | 18.1108 | 0 | 2018-04-09 | 0 | 2 | 86.9352 | 18.1599 | 0 | 2018-04-09 | 0 | 2 | 65.9815 | 13.7829 | 0
2018-04-09 01:00 | 1 | 2 | 86.0426 | 17.9734 | 0 | 2018-04-09 01:00 | 1 | 2 | 86.3127 | 18.0299 | 0 | 2018-04-09 01:00 | 1 | 2 | 86.5278 | 18.0748 | 0 | 2018-04-09 01:00 | 1 | 2 | 65.6794 | 13.7198 | 0
2018-04-09 02:00 | 2 | 2 | 86.392 | 18.0464 | 0 | 2018-04-09 02:00 | 2 | 2 | 86.6392 | 18.0981 | 0 | 2018-04-09 02:00 | 2 | 2 | 86.8421 | 18.1404 | 0 | 2018-04-09 02:00 | 2 | 2 | 65.9229 | 13.7706 | 0
2018-04-09 03:00 | 3 | 2 | 86.2776 | 18.0225 | 0 | 2018-04-09 03:00 | 3 | 2 | 86.5766 | 18.085 | 0 | 2018-04-09 03:00 | 3 | 2 | 86.7536 | 18.122 | 0 | 2018-04-09 03:00 | 3 | 2 | 65.8655 | 13.7586 | 0
2018-04-09 04:00 | 4 | 2 | 86.5034 | 18.0697 | 0 | 2018-04-09 04:00 | 4 | 2 | 86.8849 | 18.1494 | 0 | 2018-04-09 04:00 | 4 | 2 | 87.0283 | 18.1793 | 0 | 2018-04-09 04:00 | 4 | 2 | 66.087 | 13.8049 | 0
2018-04-09 05:00 | 5 | 2 | 86.3661 | 18.041 | 0 | 2018-04-09 05:00 | 5 | 2 | 86.772 | 18.1258 | 0 | 2018-04-09 05:00 | 5 | 2 | 87.0054 | 18.1746 | 0 | 2018-04-09 05:00 | 5 | 2 | 66.0354 | 13.7941 | 0
2018-04-09 06:00 | 6 | 2 | 86.2898 | 18.0251 | 0 | 2018-04-09 06:00 | 6 | 2 | 86.6499 | 18.1003 | 0 | 2018-04-09 06:00 | 6 | 2 | 86.8147 | 18.1347 | 0 | 2018-04-09 06:00 | 6 | 2 | 65.9165 | 13.7693 | 0
2018-04-09 07:00 | 7 | 2 | 86.2043 | 18.0072 | 0 | 2018-04-09 07:00 | 7 | 2 | 86.5278 | 18.0748 | 0 | 2018-04-09 07:00 | 7 | 2 | 86.7079 | 18.1124 | 0 | 2018-04-09 07:00 | 7 | 2 | 65.8296 | 13.7511 | 0
2018-04-09 08:00 | 8 | 2 | 86.3355 | 18.0346 | 0 | 2018-04-09 08:00 | 8 | 2 | 86.5461 | 18.0786 | 0 | 2018-04-09 08:00 | 8 | 2 | 86.8025 | 18.1322 | 0 | 2018-04-09 08:00 | 8 | 2 | 65.8725 | 13.7601 | 0
2018-04-09 09:00 | 9 | 2 | 86.3798 | 18.0439 | 0 | 2018-04-09 09:00 | 9 | 2 | 86.7262 | 18.1162 | 0 | 2018-04-09 09:00 | 9 | 2 | 86.8711 | 18.1465 | 0 | 2018-04-09 09:00 | 9 | 2 | 65.967 | 13.7798 | 0
2018-04-09 10:00 | 10 | 2 | 86.2272 | 18.012 | 0 | 2018-04-09 10:00 | 10 | 2 | 86.5156 | 18.0722 | 0 | 2018-04-09 10:00 | 10 | 2 | 86.714 | 18.1137 | 0 | 2018-04-09 10:00 | 10 | 2 | 65.8272 | 13.7507 | 0
2018-04-09 11:00 | 11 | 2 | 86.2119 | 18.0088 | 0 | 2018-04-09 11:00 | 11 | 2 | 86.5141 | 18.0719 | 0 | 2018-04-09 11:00 | 11 | 2 | 86.7201 | 18.115 | 0 | 2018-04-09 11:00 | 11 | 2 | 65.829 | 13.751 | 0
2018-04-09 12:00 | 12 | 2 | 86.389 | 18.0458 | 0 | 2018-04-09 12:00 | 12 | 2 | 86.6835 | 18.1073 | 0 | 2018-04-09 12:00 | 12 | 2 | 86.8574 | 18.1436 | 0 | 2018-04-09 12:00 | 12 | 2 | 65.9455 | 13.7754 | 0
2018-04-09 13:00 | 13 | 2 | 86.4027 | 18.0487 | 0 | 2018-04-09 13:00 | 13 | 2 | 86.6224 | 18.0946 | 0 | 2018-04-09 13:00 | 13 | 2 | 86.7475 | 18.1207 | 0 | 2018-04-09 13:00 | 13 | 2 | 65.8806 | 13.7618 | 0
2018-04-09 14:00 | 14 | 2 | 86.3783 | 18.0436 | 0 | 2018-04-09 14:00 | 14 | 2 | 86.6606 | 18.1025 | 0 | 2018-04-09 14:00 | 14 | 2 | 86.7903 | 18.1296 | 0 | 2018-04-09 14:00 | 14 | 2 | 65.9113 | 13.7682 | 0
2018-04-09 15:00 | 15 | 2 | 86.3355 | 18.0346 | 0 | 2018-04-09 15:00 | 15 | 2 | 86.5248 | 18.0742 | 0 | 2018-04-09 15:00 | 15 | 2 | 86.7384 | 18.1188 | 0 | 2018-04-09 15:00 | 15 | 2 | 65.84 | 13.7533 | 0
2018-04-09 16:00 | 16 | 2 | 86.3493 | 18.0375 | 0 | 2018-04-09 16:00 | 16 | 2 | 86.4912 | 18.0671 | 0 | 2018-04-09 16:00 | 16 | 2 | 86.685 | 18.1076 | 0 | 2018-04-09 16:00 | 16 | 2 | 65.807 | 13.7464 | 0
2018-04-09 17:00 | 17 | 2 | 86.244 | 18.0155 | 0 | 2018-04-09 17:00 | 17 | 2 | 86.4683 | 18.0624 | 0 | 2018-04-09 17:00 | 17 | 2 | 86.6743 | 18.1054 | 0 | 2018-04-09 17:00 | 17 | 2 | 65.7942 | 13.7437 | 0
2018-04-09 18:00 | 18 | 2 | 86.3142 | 18.0302 | 0 | 2018-04-09 18:00 | 18 | 2 | 86.4378 | 18.056 | 0 | 2018-04-09 18:00 | 18 | 2 | 86.5934 | 18.0885 | 0 | 2018-04-09 18:00 | 18 | 2 | 65.7519 | 13.7349 | 0
2018-04-09 19:00 | 19 | 2 | 86.2089 | 18.0082 | 0 | 2018-04-09 19:00 | 19 | 2 | 86.3508 | 18.0378 | 0 | 2018-04-09 19:00 | 19 | 2 | 86.5583 | 18.0812 | 0 | 2018-04-09 19:00 | 19 | 2 | 65.7055 | 13.7252 | 0
2018-04-09 20:00 | 20 | 2 | 86.2181 | 18.0101 | 0 | 2018-04-09 20:00 | 20 | 2 | 86.4836 | 18.0656 | 0 | 2018-04-09 20:00 | 20 | 2 | 86.6896 | 18.1086 | 0 | 2018-04-09 20:00 | 20 | 2 | 65.8058 | 13.7462 | 0
2018-04-09 21:00 | 21 | 2 | 86.1494 | 17.9957 | 0 | 2018-04-09 21:00 | 21 | 2 | 86.4759 | 18.064 | 0 | 2018-04-09 21:00 | 21 | 2 | 86.63 | 18.0961 | 0 | 2018-04-09 21:00 | 21 | 2 | 65.7802 | 13.7408 | 0
2018-04-09 22:00 | 22 | 2 | 86.2593 | 18.0187 | 0 | 2018-04-09 22:00 | 22 | 2 | 86.5522 | 18.0799 | 0 | 2018-04-09 22:00 | 22 | 2 | 86.6468 | 18.0997 | 0 | 2018-04-09 22:00 | 22 | 2 | 65.8156 | 13.7482 | 0
2018-04-09 23:00 | 23 | 2 | 86.4424 | 18.057 | 0 | 2018-04-09 23:00 | 23 | 2 | 86.8055 | 18.1328 | 0 | 2018-04-09 23:00 | 23 | 2 | 86.8864 | 18.1497 | 0 | 2018-04-09 23:00 | 23 | 2 | 66.0029 | 13.7874 | 0
2018-04-10 | 0 | 3 | 86.4637 | 18.0614 | 0 | 2018-04-10 | 0 | 3 | 0 | 0 | 0 | 2018-04-10 | 0 | 3 | 0 | 0 | 0 | 2018-04-10 | 0 | 3 | 0 | 0 | 0
2018-04-10 01:00 | 1 | 3 | 86.5629 | 18.0821 | 0 | 2018-04-10 01:00 | 1 | 3 | 0 | 0 | 0 | 2018-04-10 01:00 | 1 | 3 | 0 | 0 | 0 | 2018-04-10 01:00 | 1 | 3 | 0 | 0 | 0
2018-04-10 02:00 | 2 | 3 | 86.3706 | 18.042 | 0 | 2018-04-10 02:00 | 2 | 3 | 0 | 0 | 0 | 2018-04-10 02:00 | 2 | 3 | 0 | 0 | 0 | 2018-04-10 02:00 | 2 | 3 | 0 | 0 | 0
2018-04-10 03:00 | 3 | 3 | 86.3523 | 18.0381 | 0 | 2018-04-10 03:00 | 3 | 3 | 0 | 0 | 0 | 2018-04-10 03:00 | 3 | 3 | 0 | 0 | 0 | 2018-04-10 03:00 | 3 | 3 | 0 | 0 | 0
2018-04-10 04:00 | 4 | 3 | 86.3676 | 18.0413 | 0 | 2018-04-10 04:00 | 4 | 3 | 0 | 0 | 0 | 2018-04-10 04:00 | 4 | 3 | 0 | 0 | 0 | 2018-04-10 04:00 | 4 | 3 | 0 | 0 | 0
2018-04-10 05:00 | 5 | 3 | 86.4027 | 18.0487 | 0 | 2018-04-10 05:00 | 5 | 3 | 0 | 0 | 0 | 2018-04-10 05:00 | 5 | 3 | 0 | 0 | 0 | 2018-04-10 05:00 | 5 | 3 | 0 | 0 | 0
2018-04-10 06:00 | 6 | 3 | 86.4652 | 18.0617 | 0 | 2018-04-10 06:00 | 6 | 3 | 0 | 0 | 0 | 2018-04-10 06:00 | 6 | 3 | 0 | 0 | 0 | 2018-04-10 06:00 | 6 | 3 | 0 | 0 | 0
2018-04-10 07:00 | 7 | 3 | 86.4012 | 18.0483 | 0 | 2018-04-10 07:00 | 7 | 3 | 0 | 0 | 0 | 2018-04-10 07:00 | 7 | 3 | 0 | 0 | 0 | 2018-04-10 07:00 | 7 | 3 | 0 | 0 | 0
2018-04-10 08:00 | 8 | 3 | 86.4515 | 18.0589 | 0 | 2018-04-10 08:00 | 8 | 3 | 0 | 0 | 0 | 2018-04-10 08:00 | 8 | 3 | 0 | 0 | 0 | 2018-04-10 08:00 | 8 | 3 | 0 | 0 | 0
2018-04-10 09:00 | 9 | 3 | 86.2028 | 18.0069 | 0 | 2018-04-10 09:00 | 9 | 3 | 0 | 0 | 0 | 2018-04-10 09:00 | 9 | 3 | 0 | 0 | 0 | 2018-04-10 09:00 | 9 | 3 | 0 | 0 | 0
2018-04-10 10:00 | 10 | 3 | 86.2715 | 18.0213 | 0 | 2018-04-10 10:00 | 10 | 3 | 0 | 0 | 0 | 2018-04-10 10:00 | 10 | 3 | 0 | 0 | 0 | 2018-04-10 10:00 | 10 | 3 | 0 | 0 | 0
2018-04-10 11:00 | 11 | 3 | 86.7567 | 18.1226 | 0 | 2018-04-10 11:00 | 11 | 3 | 0 | 0 | 0 | 2018-04-10 11:00 | 11 | 3 | 0 | 0 | 0 | 2018-04-10 11:00 | 11 | 3 | 0 | 0 | 0
2018-04-10 12:00 | 12 | 3 | 86.6194 | 18.0939 | 0 | 2018-04-10 12:00 | 12 | 3 | 0 | 0 | 0 | 2018-04-10 12:00 | 12 | 3 | 0 | 0 | 0 | 2018-04-10 12:00 | 12 | 3 | 0 | 0 | 0
2018-04-10 13:00 | 13 | 3 | 86.6377 | 18.0977 | 0 | 2018-04-10 13:00 | 13 | 3 | 0 | 0 | 0 | 2018-04-10 13:00 | 13 | 3 | 0 | 0 | 0 | 2018-04-10 13:00 | 13 | 3 | 0 | 0 | 0
2018-04-10 14:00 | 14 | 3 | 86.8757 | 18.1475 | 0 | 2018-04-10 14:00 | 14 | 3 | 0 | 0 | 0 | 2018-04-10 14:00 | 14 | 3 | 0 | 0 | 0 | 2018-04-10 14:00 | 14 | 3 | 0 | 0 | 0
2018-04-10 15:00 | 15 | 3 | 86.7994 | 18.1315 | 0 | 2018-04-10 15:00 | 15 | 3 | 0 | 0 | 0 | 2018-04-10 15:00 | 15 | 3 | 0 | 0 | 0 | 2018-04-10 15:00 | 15 | 3 | 0 | 0 | 0
2018-04-10 16:00 | 16 | 3 | 86.7674 | 18.1248 | 0 | 2018-04-10 16:00 | 16 | 3 | 0 | 0 | 0 | 2018-04-10 16:00 | 16 | 3 | 0 | 0 | 0 | 2018-04-10 16:00 | 16 | 3 | 0 | 0 | 0
2018-04-10 17:00 | 17 | 3 | 86.7384 | 18.1188 | 0 | 2018-04-10 17:00 | 17 | 3 | 0 | 0 | 0 | 2018-04-10 17:00 | 17 | 3 | 0 | 0 | 0 | 2018-04-10 17:00 | 17 | 3 | 0 | 0 | 0
2018-04-10 18:00 | 18 | 3 | 86.7124 | 18.1134 | 0 | 2018-04-10 18:00 | 18 | 3 | 0 | 0 | 0 | 2018-04-10 18:00 | 18 | 3 | 0 | 0 | 0 | 2018-04-10 18:00 | 18 | 3 | 0 | 0 | 0
2018-04-10 19:00 | 19 | 3 | 86.8376 | 18.1395 | 0 | 2018-04-10 19:00 | 19 | 3 | 0 | 0 | 0 | 2018-04-10 19:00 | 19 | 3 | 0 | 0 | 0 | 2018-04-10 19:00 | 19 | 3 | 0 | 0 | 0
2018-04-10 20:00 | 20 | 3 | 86.627 | 18.0955 | 0 | 2018-04-10 20:00 | 20 | 3 | 0 | 0 | 0 | 2018-04-10 20:00 | 20 | 3 | 0 | 0 | 0 | 2018-04-10 20:00 | 20 | 3 | 0 | 0 | 0
2018-04-10 21:00 | 21 | 3 | 86.6239 | 18.0949 | 0 | 2018-04-10 21:00 | 21 | 3 | 0 | 0 | 0 | 2018-04-10 21:00 | 21 | 3 | 0 | 0 | 0 | 2018-04-10 21:00 | 21 | 3 | 0 | 0 | 0
2018-04-10 22:00 | 22 | 3 | 86.714 | 18.1137 | 0 | 2018-04-10 22:00 | 22 | 3 | 0 | 0 | 0 | 2018-04-10 22:00 | 22 | 3 | 0 | 0 | 0 | 2018-04-10 22:00 | 22 | 3 | 0 | 0 | 0
2018-04-10 23:00 | 23 | 3 | 86.8971 | 18.1519 | 0 | 2018-04-10 23:00 | 23 | 3 | 0 | 0 | 0 | 2018-04-10 23:00 | 23 | 3 | 0 | 0 | 0 | 2018-04-10 23:00 | 23 | 3 | 0 | 0 | 0
2018-04-11 | 0 | 4 | 0 | 0 | 0 | 2018-04-11 | 0 | 4 | 0 | 0 | 0 | 2018-04-11 | 0 | 4 | 86.6712 | 18.1047 | 0 | 2018-04-11 | 0 | 4 | 32.9351 | 6.8798 | 0
2018-04-11 01:00 | 1 | 4 | 0 | 0 | 0 | 2018-04-11 01:00 | 1 | 4 | 0 | 0 | 0 | 2018-04-11 01:00 | 1 | 4 | 86.511 | 18.0713 | 0 | 2018-04-11 01:00 | 1 | 4 | 32.8742 | 6.8671 | 0
2018-04-11 02:00 | 2 | 4 | 0 | 0 | 0 | 2018-04-11 02:00 | 2 | 4 | 0 | 0 | 0 | 2018-04-11 02:00 | 2 | 4 | 86.7628 | 18.1239 | 0 | 2018-04-11 02:00 | 2 | 4 | 32.9699 | 6.8871 | 0
2018-04-11 03:00 | 3 | 4 | 0 | 0 | 0 | 2018-04-11 03:00 | 3 | 4 | 0 | 0 | 0 | 2018-04-11 03:00 | 3 | 4 | 86.7384 | 18.1188 | 0 | 2018-04-11 03:00 | 3 | 4 | 32.9606 | 6.8851 | 0
2018-04-11 04:00 | 4 | 4 | 0 | 0 | 0 | 2018-04-11 04:00 | 4 | 4 | 0 | 0 | 0 | 2018-04-11 04:00 | 4 | 4 | 86.8376 | 18.1395 | 0 | 2018-04-11 04:00 | 4 | 4 | 32.9983 | 6.893 | 0
2018-04-11 05:00 | 5 | 4 | 0 | 0 | 0 | 2018-04-11 05:00 | 5 | 4 | 0 | 0 | 0 | 2018-04-11 05:00 | 5 | 4 | 87.0222 | 18.1781 | 0 | 2018-04-11 05:00 | 5 | 4 | 33.0684 | 6.9077 | 0
2018-04-11 06:00 | 6 | 4 | 0 | 0 | 0 | 2018-04-11 06:00 | 6 | 4 | 0 | 0 | 0 | 2018-04-11 06:00 | 6 | 4 | 86.9627 | 18.1656 | 0 | 2018-04-11 06:00 | 6 | 4 | 33.0458 | 6.9029 | 0
2018-04-11 07:00 | 7 | 4 | 0 | 0 | 0 | 2018-04-11 07:00 | 7 | 4 | 0 | 0 | 0 | 2018-04-11 07:00 | 7 | 4 | 87.1321 | 18.201 | 0 | 2018-04-11 07:00 | 7 | 4 | 33.1102 | 6.9164 | 0
2018-04-11 08:00 | 8 | 4 | 0 | 0 | 0 | 2018-04-11 08:00 | 8 | 4 | 0 | 0 | 0 | 2018-04-11 08:00 | 8 | 4 | 87.1931 | 18.2138 | 0 | 2018-04-11 08:00 | 8 | 4 | 33.1334 | 6.9212 | 0
2018-04-11 09:00 | 9 | 4 | 0 | 0 | 0 | 2018-04-11 09:00 | 9 | 4 | 0 | 0 | 0 | 2018-04-11 09:00 | 9 | 4 | 86.7155 | 18.114 | 0 | 2018-04-11 09:00 | 9 | 4 | 32.9519 | 6.8833 | 0
2018-04-11 10:00 | 10 | 4 | 0 | 0 | 0 | 2018-04-11 10:00 | 10 | 4 | 0 | 0 | 0 | 2018-04-11 10:00 | 10 | 4 | 86.6743 | 18.1054 | 0 | 2018-04-11 10:00 | 10 | 4 | 32.9362 | 6.88 | 0
2018-04-11 11:00 | 11 | 4 | 0 | 0 | 0 | 2018-04-11 11:00 | 11 | 4 | 0 | 0 | 0 | 2018-04-11 11:00 | 11 | 4 | 86.8956 | 18.1516 | 0 | 2018-04-11 11:00 | 11 | 4 | 33.0203 | 6.8976 | 0
2018-04-11 12:00 | 12 | 4 | 0 | 0 | 0 | 2018-04-11 12:00 | 12 | 4 | 0 | 0 | 0 | 2018-04-11 12:00 | 12 | 4 | 86.9276 | 18.1583 | 0 | 2018-04-11 12:00 | 12 | 4 | 33.0325 | 6.9002 | 0
2018-04-11 13:00 | 13 | 4 | 0 | 0 | 0 | 2018-04-11 13:00 | 13 | 4 | 0 | 0 | 0 | 2018-04-11 13:00 | 13 | 4 | 87.2541 | 18.2265 | 0 | 2018-04-11 13:00 | 13 | 4 | 33.1566 | 6.9261 | 0
2018-04-11 14:00 | 14 | 4 | 0 | 0 | 0 | 2018-04-11 14:00 | 14 | 4 | 0 | 0 | 0 | 2018-04-11 14:00 | 14 | 4 | 87.4037 | 18.2578 | 0 | 2018-04-11 14:00 | 14 | 4 | 33.2134 | 6.9379 | 0
2018-04-11 15:00 | 15 | 4 | 0 | 0 | 0 | 2018-04-11 15:00 | 15 | 4 | 0 | 0 | 0 | 2018-04-11 15:00 | 15 | 4 | 87.2129 | 18.2179 | 0 | 2018-04-11 15:00 | 15 | 4 | 33.1409 | 6.9228 | 0
2018-04-11 16:00 | 16 | 4 | 0 | 0 | 0 | 2018-04-11 16:00 | 16 | 4 | 0 | 0 | 0 | 2018-04-11 16:00 | 16 | 4 | 86.9718 | 18.1675 | 0 | 2018-04-11 16:00 | 16 | 4 | 33.0493 | 6.9037 | 0
2018-04-11 17:00 | 17 | 4 | 0 | 0 | 0 | 2018-04-11 17:00 | 17 | 4 | 0 | 0 | 0 | 2018-04-11 17:00 | 17 | 4 | 87.1397 | 18.2026 | 0 | 2018-04-11 17:00 | 17 | 4 | 33.1131 | 6.917 | 0
2018-04-11 18:00 | 18 | 4 | 0 | 0 | 0 | 2018-04-11 18:00 | 18 | 4 | 0 | 0 | 0 | 2018-04-11 18:00 | 18 | 4 | 87.2435 | 18.2243 | 0 | 2018-04-11 18:00 | 18 | 4 | 33.1525 | 6.9252 | 0
2018-04-11 19:00 | 19 | 4 | 0 | 0 | 0 | 2018-04-11 19:00 | 19 | 4 | 0 | 0 | 0 | 2018-04-11 19:00 | 19 | 4 | 86.8894 | 18.1503 | 0 | 2018-04-11 19:00 | 19 | 4 | 33.018 | 6.8971 | 0
2018-04-11 20:00 | 20 | 4 | 0 | 0 | 0 | 2018-04-11 20:00 | 20 | 4 | 0 | 0 | 0 | 2018-04-11 20:00 | 20 | 4 | 87.1839 | 18.2118 | 0 | 2018-04-11 20:00 | 20 | 4 | 33.1299 | 6.9205 | 0
2018-04-11 21:00 | 21 | 4 | 0 | 0 | 0 | 2018-04-11 21:00 | 21 | 4 | 0 | 0 | 0 | 2018-04-11 21:00 | 21 | 4 | 87.2419 | 18.224 | 0 | 2018-04-11 21:00 | 21 | 4 | 33.1519 | 6.9251 | 0
2018-04-11 22:00 | 22 | 4 | 0 | 0 | 0 | 2018-04-11 22:00 | 22 | 4 | 0 | 0 | 0 | 2018-04-11 22:00 | 22 | 4 | 87.1733 | 18.2096 | 0 | 2018-04-11 22:00 | 22 | 4 | 33.1259 | 6.9197 | 0
2018-04-11 23:00 | 23 | 4 | 0 | 0 | 0 | 2018-04-11 23:00 | 23 | 4 | 0 | 0 | 0 | 2018-04-11 23:00 | 23 | 4 | 87.2557 | 18.2268 | 0 | 2018-04-11 23:00 | 23 | 4 | 33.1572 | 6.9262 | 0
2018-04-12 | 0 | 5 | 86.5492 | 18.0793 | 0 | 2018-04-12 | 0 | 5 | 0 | 0 | 0 | 2018-04-12 | 0 | 5 | 0 | 0 | 0 | 2018-04-12 | 0 | 5 | 0 | 0 | 0
2018-04-12 01:00 | 1 | 5 | 86.7201 | 18.115 | 0 | 2018-04-12 01:00 | 1 | 5 | 0 | 0 | 0 | 2018-04-12 01:00 | 1 | 5 | 0 | 0 | 0 | 2018-04-12 01:00 | 1 | 5 | 0 | 0 | 0
2018-04-12 02:00 | 2 | 5 | 86.5095 | 18.071 | 0 | 2018-04-12 02:00 | 2 | 5 | 0 | 0 | 0 | 2018-04-12 02:00 | 2 | 5 | 0 | 0 | 0 | 2018-04-12 02:00 | 2 | 5 | 0 | 0 | 0
2018-04-12 03:00 | 3 | 5 | 86.4576 | 18.0601 | 0 | 2018-04-12 03:00 | 3 | 5 | 0 | 0 | 0 | 2018-04-12 03:00 | 3 | 5 | 0 | 0 | 0 | 2018-04-12 03:00 | 3 | 5 | 0 | 0 | 0
2018-04-12 04:00 | 4 | 5 | 86.6316 | 18.0965 | 0 | 2018-04-12 04:00 | 4 | 5 | 0 | 0 | 0 | 2018-04-12 04:00 | 4 | 5 | 0 | 0 | 0 | 2018-04-12 04:00 | 4 | 5 | 0 | 0 | 0
2018-04-12 05:00 | 5 | 5 | 86.569 | 18.0834 | 0 | 2018-04-12 05:00 | 5 | 5 | 0 | 0 | 0 | 2018-04-12 05:00 | 5 | 5 | 0 | 0 | 0 | 2018-04-12 05:00 | 5 | 5 | 0 | 0 | 0
2018-04-12 06:00 | 6 | 5 | 86.6468 | 18.0997 | 0 | 2018-04-12 06:00 | 6 | 5 | 0 | 0 | 0 | 2018-04-12 06:00 | 6 | 5 | 0 | 0 | 0 | 2018-04-12 06:00 | 6 | 5 | 0 | 0 | 0
2018-04-12 07:00 | 7 | 5 | 86.6361 | 18.0974 | 0 | 2018-04-12 07:00 | 7 | 5 | 0 | 0 | 0 | 2018-04-12 07:00 | 7 | 5 | 0 | 0 | 0 | 2018-04-12 07:00 | 7 | 5 | 0 | 0 | 0
2018-04-12 08:00 | 8 | 5 | 86.6819 | 18.107 | 0 | 2018-04-12 08:00 | 8 | 5 | 0 | 0 | 0 | 2018-04-12 08:00 | 8 | 5 | 0 | 0 | 0 | 2018-04-12 08:00 | 8 | 5 | 0 | 0 | 0
2018-04-12 09:00 | 9 | 5 | 86.7094 | 18.1127 | 0 | 2018-04-12 09:00 | 9 | 5 | 0 | 0 | 0 | 2018-04-12 09:00 | 9 | 5 | 0 | 0 | 0 | 2018-04-12 09:00 | 9 | 5 | 0 | 0 | 0
2018-04-12 10:00 | 10 | 5 | 86.7933 | 18.1303 | 0 | 2018-04-12 10:00 | 10 | 5 | 0 | 0 | 0 | 2018-04-12 10:00 | 10 | 5 | 0 | 0 | 0 | 2018-04-12 10:00 | 10 | 5 | 0 | 0 | 0
2018-04-12 11:00 | 11 | 5 | 86.8009 | 18.1318 | 0 | 2018-04-12 11:00 | 11 | 5 | 0 | 0 | 0 | 2018-04-12 11:00 | 11 | 5 | 0 | 0 | 0 | 2018-04-12 11:00 | 11 | 5 | 0 | 0 | 0
2018-04-12 12:00 | 12 | 5 | 86.6728 | 18.1051 | 0 | 2018-04-12 12:00 | 12 | 5 | 0 | 0 | 0 | 2018-04-12 12:00 | 12 | 5 | 0 | 0 | 0 | 2018-04-12 12:00 | 12 | 5 | 0 | 0 | 0
2018-04-12 13:00 | 13 | 5 | 86.6316 | 18.0965 | 0 | 2018-04-12 13:00 | 13 | 5 | 0 | 0 | 0 | 2018-04-12 13:00 | 13 | 5 | 0 | 0 | 0 | 2018-04-12 13:00 | 13 | 5 | 0 | 0 | 0
2018-04-12 14:00 | 14 | 5 | 86.6316 | 18.0965 | 0 | 2018-04-12 14:00 | 14 | 5 | 0 | 0 | 0 | 2018-04-12 14:00 | 14 | 5 | 0 | 0 | 0 | 2018-04-12 14:00 | 14 | 5 | 0 | 0 | 0
2018-04-12 15:00 | 15 | 5 | 86.6636 | 18.1032 | 0 | 2018-04-12 15:00 | 15 | 5 | 0 | 0 | 0 | 2018-04-12 15:00 | 15 | 5 | 0 | 0 | 0 | 2018-04-12 15:00 | 15 | 5 | 0 | 0 | 0
2018-04-12 16:00 | 16 | 5 | 86.5568 | 18.0808 | 0 | 2018-04-12 16:00 | 16 | 5 | 0 | 0 | 0 | 2018-04-12 16:00 | 16 | 5 | 0 | 0 | 0 | 2018-04-12 16:00 | 16 | 5 | 0 | 0 | 0
2018-04-12 17:00 | 17 | 5 | 86.6865 | 18.1079 | 0 | 2018-04-12 17:00 | 17 | 5 | 0 | 0 | 0 | 2018-04-12 17:00 | 17 | 5 | 0 | 0 | 0 | 2018-04-12 17:00 | 17 | 5 | 0 | 0 | 0
2018-04-12 18:00 | 18 | 5 | 86.7262 | 18.1162 | 0 | 2018-04-12 18:00 | 18 | 5 | 0 | 0 | 0 | 2018-04-12 18:00 | 18 | 5 | 0 | 0 | 0 | 2018-04-12 18:00 | 18 | 5 | 0 | 0 | 0
2018-04-12 19:00 | 19 | 5 | 86.5187 | 18.0729 | 0 | 2018-04-12 19:00 | 19 | 5 | 0 | 0 | 0 | 2018-04-12 19:00 | 19 | 5 | 0 | 0 | 0 | 2018-04-12 19:00 | 19 | 5 | 0 | 0 | 0
2018-04-12 20:00 | 20 | 5 | 86.5766 | 18.085 | 0 | 2018-04-12 20:00 | 20 | 5 | 0 | 0 | 0 | 2018-04-12 20:00 | 20 | 5 | 0 | 0 | 0 | 2018-04-12 20:00 | 20 | 5 | 0 | 0 | 0
2018-04-12 21:00 | 21 | 5 | 86.6194 | 18.0939 | 0 | 2018-04-12 21:00 | 21 | 5 | 0 | 0 | 0 | 2018-04-12 21:00 | 21 | 5 | 0 | 0 | 0 | 2018-04-12 21:00 | 21 | 5 | 0 | 0 | 0
2018-04-12 22:00 | 22 | 5 | 86.6743 | 18.1054 | 0 | 2018-04-12 22:00 | 22 | 5 | 0 | 0 | 0 | 2018-04-12 22:00 | 22 | 5 | 0 | 0 | 0 | 2018-04-12 22:00 | 22 | 5 | 0 | 0 | 0
2018-04-12 23:00 | 23 | 5 | 86.5644 | 18.0824 | 0 | 2018-04-12 23:00 | 23 | 5 | 0 | 0 | 0 | 2018-04-12 23:00 | 23 | 5 | 0 | 0 | 0 | 2018-04-12 23:00 | 23 | 5 | 0 | 0 | 0
2018-04-13 | 0 | 6 | 86.2226 | 18.011 | 0 | 2018-04-13 | 0 | 6 | 86.688 | 18.1083 | 0 | 2018-04-13 | 0 | 6 | 0 | 0 | 0 | 2018-04-13 | 0 | 6 | 32.9414 | 6.8811 | 0
2018-04-13 01:00 | 1 | 6 | 86.1128 | 17.9881 | 0 | 2018-04-13 01:00 | 1 | 6 | 86.5232 | 18.0738 | 0 | 2018-04-13 01:00 | 1 | 6 | 0 | 0 | 0 | 2018-04-13 01:00 | 1 | 6 | 32.8788 | 6.8681 | 0
2018-04-13 02:00 | 2 | 6 | 86.2791 | 18.0228 | 0 | 2018-04-13 02:00 | 2 | 6 | 86.6896 | 18.1086 | 0 | 2018-04-13 02:00 | 2 | 6 | 0 | 0 | 0 | 2018-04-13 02:00 | 2 | 6 | 32.942 | 6.8813 | 0
2018-04-13 03:00 | 3 | 6 | 86.0014 | 17.9648 | 0 | 2018-04-13 03:00 | 3 | 6 | 86.4485 | 18.0582 | 0 | 2018-04-13 03:00 | 3 | 6 | 0 | 0 | 0 | 2018-04-13 03:00 | 3 | 6 | 32.8504 | 6.8621 | 0
2018-04-13 04:00 | 4 | 6 | 86.0533 | 17.9757 | 0 | 2018-04-13 04:00 | 4 | 6 | 86.4347 | 18.0553 | 0 | 2018-04-13 04:00 | 4 | 6 | 0 | 0 | 0 | 2018-04-13 04:00 | 4 | 6 | 32.8452 | 6.861 | 0
2018-04-13 05:00 | 5 | 6 | 86.2257 | 18.0117 | 0 | 2018-04-13 05:00 | 5 | 6 | 86.6117 | 18.0923 | 0 | 2018-04-13 05:00 | 5 | 6 | 0 | 0 | 0 | 2018-04-13 05:00 | 5 | 6 | 32.9124 | 6.8751 | 0
2018-04-13 06:00 | 6 | 6 | 86.4332 | 18.055 | 0 | 2018-04-13 06:00 | 6 | 6 | 86.9352 | 18.1599 | 0 | 2018-04-13 06:00 | 6 | 6 | 0 | 0 | 0 | 2018-04-13 06:00 | 6 | 6 | 33.0354 | 6.9008 | 0
2018-04-13 07:00 | 7 | 6 | 86.5873 | 18.0872 | 0 | 2018-04-13 07:00 | 7 | 6 | 87.0619 | 18.1864 | 0 | 2018-04-13 07:00 | 7 | 6 | 0 | 0 | 0 | 2018-04-13 07:00 | 7 | 6 | 33.0835 | 6.9108 | 0
2018-04-13 08:00 | 8 | 6 | 86.3691 | 18.0416 | 0 | 2018-04-13 08:00 | 8 | 6 | 86.7811 | 18.1277 | 0 | 2018-04-13 08:00 | 8 | 6 | 0 | 0 | 0 | 2018-04-13 08:00 | 8 | 6 | 32.9768 | 6.8885 | 0
2018-04-13 09:00 | 9 | 6 | 86.334 | 18.0343 | 0 | 2018-04-13 09:00 | 9 | 6 | 86.7399 | 18.1191 | 0 | 2018-04-13 09:00 | 9 | 6 | 0 | 0 | 0 | 2018-04-13 09:00 | 9 | 6 | 32.9612 | 6.8853 | 0
2018-04-13 10:00 | 10 | 6 | 86.5126 | 18.0716 | 0 | 2018-04-13 10:00 | 10 | 6 | 86.862 | 18.1446 | 0 | 2018-04-13 10:00 | 10 | 6 | 0 | 0 | 0 | 2018-04-13 10:00 | 10 | 6 | 33.0076 | 6.8949 | 0
2018-04-13 11:00 | 11 | 6 | 86.5003 | 18.069 | 0 | 2018-04-13 11:00 | 11 | 6 | 86.9306 | 18.1589 | 0 | 2018-04-13 11:00 | 11 | 6 | 0 | 0 | 0 | 2018-04-13 11:00 | 11 | 6 | 33.0336 | 6.9004 | 0
2018-04-13 12:00 | 12 | 6 | 86.7002 | 18.1108 | 0 | 2018-04-13 12:00 | 12 | 6 | 87.1412 | 18.2029 | 0 | 2018-04-13 12:00 | 12 | 6 | 0 | 0 | 0 | 2018-04-13 12:00 | 12 | 6 | 33.1137 | 6.9171 | 0
2018-04-13 13:00 | 13 | 6 | 86.363 | 18.0404 | 0 | 2018-04-13 13:00 | 13 | 6 | 86.8009 | 18.1318 | 0 | 2018-04-13 13:00 | 13 | 6 | 0 | 0 | 0 | 2018-04-13 13:00 | 13 | 6 | 32.9843 | 6.8901 | 0
2018-04-13 14:00 | 14 | 6 | 86.4408 | 18.0566 | 0 | 2018-04-13 14:00 | 14 | 6 | 86.8635 | 18.1449 | 0 | 2018-04-13 14:00 | 14 | 6 | 0 | 0 | 0 | 2018-04-13 14:00 | 14 | 6 | 33.0081 | 6.8951 | 0
2018-04-13 15:00 | 15 | 6 | 86.2943 | 18.026 | 0 | 2018-04-13 15:00 | 15 | 6 | 86.6743 | 18.1054 | 0 | 2018-04-13 15:00 | 15 | 6 | 0 | 0 | 0 | 2018-04-13 15:00 | 15 | 6 | 32.9362 | 6.88 | 0
2018-04-13 16:00 | 16 | 6 | 86.3706 | 18.042 | 0 | 2018-04-13 16:00 | 16 | 6 | 86.7491 | 18.121 | 0 | 2018-04-13 16:00 | 16 | 6 | 0 | 0 | 0 | 2018-04-13 16:00 | 16 | 6 | 32.9647 | 6.886 | 0
2018-04-13 17:00 | 17 | 6 | 86.2882 | 18.0247 | 0 | 2018-04-13 17:00 | 17 | 6 | 86.7445 | 18.1201 | 0 | 2018-04-13 17:00 | 17 | 6 | 0 | 0 | 0 | 2018-04-13 17:00 | 17 | 6 | 32.9629 | 6.8856 | 0
2018-04-13 18:00 | 18 | 6 | 86.1875 | 18.0037 | 0 | 2018-04-13 18:00 | 18 | 6 | 86.6667 | 18.1038 | 0 | 2018-04-13 18:00 | 18 | 6 | 0 | 0 | 0 | 2018-04-13 18:00 | 18 | 6 | 32.9333 | 6.8794 | 0
2018-04-13 19:00 | 19 | 6 | 86.099 | 17.9852 | 0 | 2018-04-13 19:00 | 19 | 6 | 86.5431 | 18.078 | 0 | 2018-04-13 19:00 | 19 | 6 | 0 | 0 | 0 | 2018-04-13 19:00 | 19 | 6 | 32.8864 | 6.8696 | 0
2018-04-13 20:00 | 20 | 6 | 86.1997 | 18.0063 | 0 | 2018-04-13 20:00 | 20 | 6 | 86.5187 | 18.0729 | 0 | 2018-04-13 20:00 | 20 | 6 | 0 | 0 | 0 | 2018-04-13 20:00 | 20 | 6 | 32.8771 | 6.8677 | 0
2018-04-13 21:00 | 21 | 6 | 86.3767 | 18.0432 | 0 | 2018-04-13 21:00 | 21 | 6 | 86.7247 | 18.1159 | 0 | 2018-04-13 21:00 | 21 | 6 | 0 | 0 | 0 | 2018-04-13 21:00 | 21 | 6 | 32.9554 | 6.8841 | 0
2018-04-13 22:00 | 22 | 6 | 86.3691 | 18.0416 | 0 | 2018-04-13 22:00 | 22 | 6 | 86.7659 | 18.1245 | 0 | 2018-04-13 22:00 | 22 | 6 | 0 | 0 | 0 | 2018-04-13 22:00 | 22 | 6 | 32.971 | 6.8873 | 0
2018-04-13 23:00 | 23 | 6 | 86.4012 | 18.0483 | 0 | 2018-04-13 23:00 | 23 | 6 | 86.7918 | 18.1299 | 0 | 2018-04-13 23:00 | 23 | 6 | 0 | 0 | 0 | 2018-04-13 23:00 | 23 | 6 | 32.9809 | 6.8894 | 0
2018-04-14 | 0 | 7 | 86.0121 | 17.9671 | 0 | 2018-04-14 | 0 | 7 | 0 | 0 | 0 | 2018-04-14 | 0 | 7 | 86.5507 | 18.0796 | 0 | 2018-04-14 | 0 | 7 | 32.8893 | 6.8702 | 0
2018-04-14 01:00 | 1 | 7 | 85.919 | 17.9476 | 0 | 2018-04-14 01:00 | 1 | 7 | 0 | 0 | 0 | 2018-04-14 01:00 | 1 | 7 | 86.5324 | 18.0758 | 0 | 2018-04-14 01:00 | 1 | 7 | 32.8823 | 6.8688 | 0
2018-04-14 02:00 | 2 | 7 | 86.0533 | 17.9757 | 0 | 2018-04-14 02:00 | 2 | 7 | 0 | 0 | 0 | 2018-04-14 02:00 | 2 | 7 | 86.6453 | 18.0993 | 0 | 2018-04-14 02:00 | 2 | 7 | 32.9252 | 6.8777 | 0
2018-04-14 03:00 | 3 | 7 | 86.1677 | 17.9996 | 0 | 2018-04-14 03:00 | 3 | 7 | 0 | 0 | 0 | 2018-04-14 03:00 | 3 | 7 | 86.7002 | 18.1108 | 0 | 2018-04-14 03:00 | 3 | 7 | 32.9461 | 6.8821 | 0
2018-04-14 04:00 | 4 | 7 | 86.3081 | 18.0289 | 0 | 2018-04-14 04:00 | 4 | 7 | 0 | 0 | 0 | 2018-04-14 04:00 | 4 | 7 | 86.8513 | 18.1424 | 0 | 2018-04-14 04:00 | 4 | 7 | 33.0035 | 6.8941 | 0
2018-04-14 05:00 | 5 | 7 | 86.2562 | 18.0181 | 0 | 2018-04-14 05:00 | 5 | 7 | 0 | 0 | 0 | 2018-04-14 05:00 | 5 | 7 | 86.8605 | 18.1443 | 0 | 2018-04-14 05:00 | 5 | 7 | 33.007 | 6.8948 | 0
2018-04-14 06:00 | 6 | 7 | 86.1234 | 17.9903 | 0 | 2018-04-14 06:00 | 6 | 7 | 0 | 0 | 0 | 2018-04-14 06:00 | 6 | 7 | 86.6682 | 18.1041 | 0 | 2018-04-14 06:00 | 6 | 7 | 32.9339 | 6.8796 | 0
2018-04-14 07:00 | 7 | 7 | 86.1906 | 18.0044 | 0 | 2018-04-14 07:00 | 7 | 7 | 0 | 0 | 0 | 2018-04-14 07:00 | 7 | 7 | 86.7247 | 18.1159 | 0 | 2018-04-14 07:00 | 7 | 7 | 32.9554 | 6.8841 | 0
2018-04-14 08:00 | 8 | 7 | 86.36 | 18.0397 | 0 | 2018-04-14 08:00 | 8 | 7 | 0 | 0 | 0 | 2018-04-14 08:00 | 8 | 7 | 86.952 | 18.1634 | 0 | 2018-04-14 08:00 | 8 | 7 | 33.0418 | 6.9021 | 0
2018-04-14 09:00 | 9 | 7 | 86.4912 | 18.0671 | 0 | 2018-04-14 09:00 | 9 | 7 | 0 | 0 | 0 | 2018-04-14 09:00 | 9 | 7 | 87.0588 | 18.1857 | 0 | 2018-04-14 09:00 | 9 | 7 | 33.0823 | 6.9106 | 0
2018-04-14 10:00 | 10 | 7 | 86.1982 | 18.0059 | 0 | 2018-04-14 10:00 | 10 | 7 | 0 | 0 | 0 | 2018-04-14 10:00 | 10 | 7 | 86.6392 | 18.0981 | 0 | 2018-04-14 10:00 | 10 | 7 | 32.9229 | 6.8773 | 0
2018-04-14 11:00 | 11 | 7 | 86.1707 | 18.0002 | 0 | 2018-04-14 11:00 | 11 | 7 | 0 | 0 | 0 | 2018-04-14 11:00 | 11 | 7 | 86.8849 | 18.1494 | 0 | 2018-04-14 11:00 | 11 | 7 | 33.0163 | 6.8968 | 0
2018-04-14 12:00 | 12 | 7 | 86.5019 | 18.0694 | 0 | 2018-04-14 12:00 | 12 | 7 | 0 | 0 | 0 | 2018-04-14 12:00 | 12 | 7 | 87.1504 | 18.2048 | 0 | 2018-04-14 12:00 | 12 | 7 | 33.1172 | 6.9178 | 0
2018-04-14 13:00 | 13 | 7 | 86.6148 | 18.093 | 0 | 2018-04-14 13:00 | 13 | 7 | 0 | 0 | 0 | 2018-04-14 13:00 | 13 | 7 | 87.3167 | 18.2396 | 0 | 2018-04-14 13:00 | 13 | 7 | 33.1803 | 6.931 | 0
2018-04-14 14:00 | 14 | 7 | 86.4439 | 18.0573 | 0 | 2018-04-14 14:00 | 14 | 7 | 0 | 0 | 0 | 2018-04-14 14:00 | 14 | 7 | 87.0832 | 18.1908 | 0 | 2018-04-14 14:00 | 14 | 7 | 33.0916 | 6.9125 | 0
2018-04-14 15:00 | 15 | 7 | 86.5522 | 18.0799 | 0 | 2018-04-14 15:00 | 15 | 7 | 0 | 0 | 0 | 2018-04-14 15:00 | 15 | 7 | 87.2938 | 18.2348 | 0 | 2018-04-14 15:00 | 15 | 7 | 33.1716 | 6.9292 | 0
2018-04-14 16:00 | 16 | 7 | 86.5644 | 18.0824 | 0 | 2018-04-14 16:00 | 16 | 7 | 0 | 0 | 0 | 2018-04-14 16:00 | 16 | 7 | 87.3579 | 18.2482 | 0 | 2018-04-14 16:00 | 16 | 7 | 33.196 | 6.9343 | 0
2018-04-14 17:00 | 17 | 7 | 86.7445 | 18.1201 | 0 | 2018-04-14 17:00 | 17 | 7 | 0 | 0 | 0 | 2018-04-14 17:00 | 17 | 7 | 87.57 | 18.2925 | 0 | 2018-04-14 17:00 | 17 | 7 | 33.2766 | 6.9511 | 0
2018-04-14 18:00 | 18 | 7 | 86.4668 | 18.062 | 0 | 2018-04-14 18:00 | 18 | 7 | 0 | 0 | 0 | 2018-04-14 18:00 | 18 | 7 | 87.3014 | 18.2364 | 0 | 2018-04-14 18:00 | 18 | 7 | 33.1745 | 6.9298 | 0
2018-04-14 19:00 | 19 | 7 | 86.3661 | 18.041 | 0 | 2018-04-14 19:00 | 19 | 7 | 0 | 0 | 0 | 2018-04-14 19:00 | 19 | 7 | 87.0954 | 18.1934 | 0 | 2018-04-14 19:00 | 19 | 7 | 33.0963 | 6.9135 | 0
2018-04-14 20:00 | 20 | 7 | 86.1173 | 17.989 | 0 | 2018-04-14 20:00 | 20 | 7 | 0 | 0 | 0 | 2018-04-14 20:00 | 20 | 7 | 86.891 | 18.1507 | 0 | 2018-04-14 20:00 | 20 | 7 | 33.0186 | 6.8973 | 0
2018-04-14 21:00 | 21 | 7 | 86.1555 | 17.997 | 0 | 2018-04-14 21:00 | 21 | 7 | 0 | 0 | 0 | 2018-04-14 21:00 | 21 | 7 | 86.9245 | 18.1577 | 0 | 2018-04-14 21:00 | 21 | 7 | 33.0313 | 6.8999 | 0
2018-04-14 22:00 | 22 | 7 | 86.2211 | 18.0107 | 0 | 2018-04-14 22:00 | 22 | 7 | 0 | 0 | 0 | 2018-04-14 22:00 | 22 | 7 | 87.0054 | 18.1746 | 0 | 2018-04-14 22:00 | 22 | 7 | 33.0621 | 6.9063 | 0
2018-04-14 23:00 | 23 | 7 | 86.2226 | 18.011 | 0 | 2018-04-14 23:00 | 23 | 7 | 0 | 0 | 0 | 2018-04-14 23:00 | 23 | 7 | 87.0787 | 18.1899 | 0 | 2018-04-14 23:00 | 23 | 7 | 33.0899 | 6.9122 | 0
2018-04-15 | 0 | 1 | 86.2364 | 18.0139 | 0 | 2018-04-15 | 0 | 1 | 86.7994 | 18.1315 | 0 | 2018-04-15 | 0 | 1 | 0 | 0 | 0 | 2018-04-15 | 0 | 1 | 32.9838 | 6.89 | 0
2018-04-15 01:00 | 1 | 1 | 86.3188 | 18.0311 | 0 | 2018-04-15 01:00 | 1 | 1 | 86.952 | 18.1634 | 0 | 2018-04-15 01:00 | 1 | 1 | 0 | 0 | 0 | 2018-04-15 01:00 | 1 | 1 | 33.0418 | 6.9021 | 0
2018-04-15 02:00 | 2 | 1 | 86.2119 | 18.0088 | 0 | 2018-04-15 02:00 | 2 | 1 | 86.8177 | 18.1353 | 0 | 2018-04-15 02:00 | 2 | 1 | 0 | 0 | 0 | 2018-04-15 02:00 | 2 | 1 | 32.9907 | 6.8914 | 0
2018-04-15 03:00 | 3 | 1 | 86.1845 | 18.0031 | 0 | 2018-04-15 03:00 | 3 | 1 | 86.7857 | 18.1287 | 0 | 2018-04-15 03:00 | 3 | 1 | 0 | 0 | 0 | 2018-04-15 03:00 | 3 | 1 | 32.9786 | 6.8889 | 0
2018-04-15 04:00 | 4 | 1 | 86.2455 | 18.0158 | 0 | 2018-04-15 04:00 | 4 | 1 | 86.833 | 18.1385 | 0 | 2018-04-15 04:00 | 4 | 1 | 0 | 0 | 0 | 2018-04-15 04:00 | 4 | 1 | 32.9965 | 6.8926 | 0
2018-04-15 05:00 | 5 | 1 | 86.2333 | 18.0133 | 0 | 2018-04-15 05:00 | 5 | 1 | 86.833 | 18.1385 | 0 | 2018-04-15 05:00 | 5 | 1 | 0 | 0 | 0 | 2018-04-15 05:00 | 5 | 1 | 32.9965 | 6.8926 | 0
2018-04-15 06:00 | 6 | 1 | 86.2776 | 18.0225 | 0 | 2018-04-15 06:00 | 6 | 1 | 86.8528 | 18.1427 | 0 | 2018-04-15 06:00 | 6 | 1 | 0 | 0 | 0 | 2018-04-15 06:00 | 6 | 1 | 33.0041 | 6.8942 | 0
2018-04-15 07:00 | 7 | 1 | 86.2867 | 18.0244 | 0 | 2018-04-15 07:00 | 7 | 1 | 86.8452 | 18.1411 | 0 | 2018-04-15 07:00 | 7 | 1 | 0 | 0 | 0 | 2018-04-15 07:00 | 7 | 1 | 33.0012 | 6.8936 | 0
2018-04-15 08:00 | 8 | 1 | 86.2989 | 18.027 | 0 | 2018-04-15 08:00 | 8 | 1 | 86.9032 | 18.1532 | 0 | 2018-04-15 08:00 | 8 | 1 | 0 | 0 | 0 | 2018-04-15 08:00 | 8 | 1 | 33.0232 | 6.8982 | 0
2018-04-15 09:00 | 9 | 1 | 86.2867 | 18.0244 | 0 | 2018-04-15 09:00 | 9 | 1 | 86.8162 | 18.135 | 0 | 2018-04-15 09:00 | 9 | 1 | 0 | 0 | 0 | 2018-04-15 09:00 | 9 | 1 | 32.9902 | 6.8913 | 0
2018-04-15 10:00 | 10 | 1 | 86.2882 | 18.0247 | 0 | 2018-04-15 10:00 | 10 | 1 | 86.8528 | 18.1427 | 0 | 2018-04-15 10:00 | 10 | 1 | 0 | 0 | 0 | 2018-04-15 10:00 | 10 | 1 | 33.0041 | 6.8942 | 0
2018-04-15 11:00 | 11 | 1 | 86.1845 | 18.0031 | 0 | 2018-04-15 11:00 | 11 | 1 | 86.743 | 18.1197 | 0 | 2018-04-15 11:00 | 11 | 1 | 0 | 0 | 0 | 2018-04-15 11:00 | 11 | 1 | 32.9623 | 6.8855 | 0
2018-04-15 12:00 | 12 | 1 | 86.1418 | 17.9942 | 0 | 2018-04-15 12:00 | 12 | 1 | 86.714 | 18.1137 | 0 | 2018-04-15 12:00 | 12 | 1 | 0 | 0 | 0 | 2018-04-15 12:00 | 12 | 1 | 32.9513 | 6.8832 | 0
2018-04-15 13:00 | 13 | 1 | 86.1479 | 17.9954 | 0 | 2018-04-15 13:00 | 13 | 1 | 86.7659 | 18.1245 | 0 | 2018-04-15 13:00 | 13 | 1 | 0 | 0 | 0 | 2018-04-15 13:00 | 13 | 1 | 32.971 | 6.8873 | 0
2018-04-15 14:00 | 14 | 1 | 86.1112 | 17.9878 | 0 | 2018-04-15 14:00 | 14 | 1 | 86.7018 | 18.1111 | 0 | 2018-04-15 14:00 | 14 | 1 | 0 | 0 | 0 | 2018-04-15 14:00 | 14 | 1 | 32.9467 | 6.8822 | 0
2018-04-15 15:00 | 15 | 1 | 86.2455 | 18.0158 | 0 | 2018-04-15 15:00 | 15 | 1 | 86.8482 | 18.1417 | 0 | 2018-04-15 15:00 | 15 | 1 | 0 | 0 | 0 | 2018-04-15 15:00 | 15 | 1 | 33.0023 | 6.8939 | 0
2018-04-15 16:00 | 16 | 1 | 86.3447 | 18.0365 | 0 | 2018-04-15 16:00 | 16 | 1 | 86.9398 | 18.1609 | 0 | 2018-04-15 16:00 | 16 | 1 | 0 | 0 | 0 | 2018-04-15 16:00 | 16 | 1 | 33.0371 | 6.9011 | 0
2018-04-15 17:00 | 17 | 1 | 86.4805 | 18.0649 | 0 | 2018-04-15 17:00 | 17 | 1 | 86.9856 | 18.1704 | 0 | 2018-04-15 17:00 | 17 | 1 | 0 | 0 | 0 | 2018-04-15 17:00 | 17 | 1 | 33.0545 | 6.9048 | 0
2018-04-15 18:00 | 18 | 1 | 86.4332 | 18.055 | 0 | 2018-04-15 18:00 | 18 | 1 | 86.92 | 18.1567 | 0 | 2018-04-15 18:00 | 18 | 1 | 0 | 0 | 0 | 2018-04-15 18:00 | 18 | 1 | 33.0296 | 6.8996 | 0
2018-04-15 19:00 | 19 | 1 | 85.6794 | 17.8976 | 0 | 2018-04-15 19:00 | 19 | 1 | 85.9266 | 17.9492 | 0 | 2018-04-15 19:00 | 19 | 1 | 0 | 0 | 0 | 2018-04-15 19:00 | 19 | 1 | 32.6521 | 6.8207 | 0
2018-04-15 20:00 | 20 | 1 | 86.3294 | 18.0333 | 0 | 2018-04-15 20:00 | 20 | 1 | 86.5888 | 18.0875 | 0 | 2018-04-15 20:00 | 20 | 1 | 0 | 0 | 0 | 2018-04-15 20:00 | 20 | 1 | 32.9037 | 6.8733 | 0
2018-04-15 21:00 | 21 | 1 | 86.3569 | 18.0391 | 0 | 2018-04-15 21:00 | 21 | 1 | 86.6728 | 18.1051 | 0 | 2018-04-15 21:00 | 21 | 1 | 0 | 0 | 0 | 2018-04-15 21:00 | 21 | 1 | 32.9357 | 6.8799 | 0
2018-04-15 22:00 | 22 | 1 | 86.4881 | 18.0665 | 0 | 2018-04-15 22:00 | 22 | 1 | 86.8086 | 18.1334 | 0 | 2018-04-15 22:00 | 22 | 1 | 0 | 0 | 0 | 2018-04-15 22:00 | 22 | 1 | 32.9873 | 6.8907 | 0
2018-04-15 23:00 | 23 | 1 | 86.4332 | 18.055 | 0 | 2018-04-15 23:00 | 23 | 1 | 86.7353 | 18.1181 | 0 | 2018-04-15 23:00 | 23 | 1 | 0 | 0 | 0 | 2018-04-15 23:00 | 23 | 1 | 32.9594 | 6.8849 | 0
2018-04-16 | 0 | 2 | 86.4088 | 18.0499 | 0 | 2018-04-16 | 0 | 2 | 86.7002 | 18.1108 | 0 | 2018-04-16 | 0 | 2 | 86.9352 | 18.1599 | 0 | 2018-04-16 | 0 | 2 | 65.9815 | 13.7829 | 0
2018-04-16 01:00 | 1 | 2 | 86.0426 | 17.9734 | 0 | 2018-04-16 01:00 | 1 | 2 | 86.3127 | 18.0299 | 0 | 2018-04-16 01:00 | 1 | 2 | 86.5278 | 18.0748 | 0 | 2018-04-16 01:00 | 1 | 2 | 65.6794 | 13.7198 | 0
2018-04-16 02:00 | 2 | 2 | 86.392 | 18.0464 | 0 | 2018-04-16 02:00 | 2 | 2 | 86.6392 | 18.0981 | 0 | 2018-04-16 02:00 | 2 | 2 | 86.8421 | 18.1404 | 0 | 2018-04-16 02:00 | 2 | 2 | 65.9229 | 13.7706 | 0
2018-04-16 03:00 | 3 | 2 | 86.2776 | 18.0225 | 0 | 2018-04-16 03:00 | 3 | 2 | 86.5766 | 18.085 | 0 | 2018-04-16 03:00 | 3 | 2 | 86.7536 | 18.122 | 0 | 2018-04-16 03:00 | 3 | 2 | 65.8655 | 13.7586 | 0
2018-04-16 04:00 | 4 | 2 | 86.5034 | 18.0697 | 0 | 2018-04-16 04:00 | 4 | 2 | 86.8849 | 18.1494 | 0 | 2018-04-16 04:00 | 4 | 2 | 87.0283 | 18.1793 | 0 | 2018-04-16 04:00 | 4 | 2 | 66.087 | 13.8049 | 0
2018-04-16 05:00 | 5 | 2 | 86.3661 | 18.041 | 0 | 2018-04-16 05:00 | 5 | 2 | 86.772 | 18.1258 | 0 | 2018-04-16 05:00 | 5 | 2 | 87.0054 | 18.1746 | 0 | 2018-04-16 05:00 | 5 | 2 | 66.0354 | 13.7941 | 0
2018-04-16 06:00 | 6 | 2 | 86.2898 | 18.0251 | 0 | 2018-04-16 06:00 | 6 | 2 | 86.6499 | 18.1003 | 0 | 2018-04-16 06:00 | 6 | 2 | 86.8147 | 18.1347 | 0 | 2018-04-16 06:00 | 6 | 2 | 65.9165 | 13.7693 | 0
2018-04-16 07:00 | 7 | 2 | 86.2043 | 18.0072 | 0 | 2018-04-16 07:00 | 7 | 2 | 86.5278 | 18.0748 | 0 | 2018-04-16 07:00 | 7 | 2 | 86.7079 | 18.1124 | 0 | 2018-04-16 07:00 | 7 | 2 | 65.8296 | 13.7511 | 0
2018-04-16 08:00 | 8 | 2 | 86.3355 | 18.0346 | 0 | 2018-04-16 08:00 | 8 | 2 | 86.5461 | 18.0786 | 0 | 2018-04-16 08:00 | 8 | 2 | 86.8025 | 18.1322 | 0 | 2018-04-16 08:00 | 8 | 2 | 65.8725 | 13.7601 | 0
2018-04-16 09:00 | 9 | 2 | 86.3798 | 18.0439 | 0 | 2018-04-16 09:00 | 9 | 2 | 86.7262 | 18.1162 | 0 | 2018-04-16 09:00 | 9 | 2 | 86.8711 | 18.1465 | 0 | 2018-04-16 09:00 | 9 | 2 | 65.967 | 13.7798 | 0
2018-04-16 10:00 | 10 | 2 | 86.2272 | 18.012 | 0 | 2018-04-16 10:00 | 10 | 2 | 86.5156 | 18.0722 | 0 | 2018-04-16 10:00 | 10 | 2 | 86.714 | 18.1137 | 0 | 2018-04-16 10:00 | 10 | 2 | 65.8272 | 13.7507 | 0
2018-04-16 11:00 | 11 | 2 | 86.2119 | 18.0088 | 0 | 2018-04-16 11:00 | 11 | 2 | 86.5141 | 18.0719 | 0 | 2018-04-16 11:00 | 11 | 2 | 86.7201 | 18.115 | 0 | 2018-04-16 11:00 | 11 | 2 | 65.829 | 13.751 | 0
2018-04-16 12:00 | 12 | 2 | 86.389 | 18.0458 | 0 | 2018-04-16 12:00 | 12 | 2 | 86.6835 | 18.1073 | 0 | 2018-04-16 12:00 | 12 | 2 | 86.8574 | 18.1436 | 0 | 2018-04-16 12:00 | 12 | 2 | 65.9455 | 13.7754 | 0
2018-04-16 13:00 | 13 | 2 | 86.4027 | 18.0487 | 0 | 2018-04-16 13:00 | 13 | 2 | 86.6224 | 18.0946 | 0 | 2018-04-16 13:00 | 13 | 2 | 86.7475 | 18.1207 | 0 | 2018-04-16 13:00 | 13 | 2 | 65.8806 | 13.7618 | 0
2018-04-16 14:00 | 14 | 2 | 86.3783 | 18.0436 | 0 | 2018-04-16 14:00 | 14 | 2 | 86.6606 | 18.1025 | 0 | 2018-04-16 14:00 | 14 | 2 | 86.7903 | 18.1296 | 0 | 2018-04-16 14:00 | 14 | 2 | 65.9113 | 13.7682 | 0
2018-04-16 15:00 | 15 | 2 | 86.3355 | 18.0346 | 0 | 2018-04-16 15:00 | 15 | 2 | 86.5248 | 18.0742 | 0 | 2018-04-16 15:00 | 15 | 2 | 86.7384 | 18.1188 | 0 | 2018-04-16 15:00 | 15 | 2 | 65.84 | 13.7533 | 0
2018-04-16 16:00 | 16 | 2 | 86.3493 | 18.0375 | 0 | 2018-04-16 16:00 | 16 | 2 | 86.4912 | 18.0671 | 0 | 2018-04-16 16:00 | 16 | 2 | 86.685 | 18.1076 | 0 | 2018-04-16 16:00 | 16 | 2 | 65.807 | 13.7464 | 0
2018-04-16 17:00 | 17 | 2 | 86.244 | 18.0155 | 0 | 2018-04-16 17:00 | 17 | 2 | 86.4683 | 18.0624 | 0 | 2018-04-16 17:00 | 17 | 2 | 86.6743 | 18.1054 | 0 | 2018-04-16 17:00 | 17 | 2 | 65.7942 | 13.7437 | 0
2018-04-16 18:00 | 18 | 2 | 86.3142 | 18.0302 | 0 | 2018-04-16 18:00 | 18 | 2 | 86.4378 | 18.056 | 0 | 2018-04-16 18:00 | 18 | 2 | 86.5934 | 18.0885 | 0 | 2018-04-16 18:00 | 18 | 2 | 65.7519 | 13.7349 | 0
2018-04-16 19:00 | 19 | 2 | 86.2089 | 18.0082 | 0 | 2018-04-16 19:00 | 19 | 2 | 86.3508 | 18.0378 | 0 | 2018-04-16 19:00 | 19 | 2 | 86.5583 | 18.0812 | 0 | 2018-04-16 19:00 | 19 | 2 | 65.7055 | 13.7252 | 0
2018-04-16 20:00 | 20 | 2 | 86.2181 | 18.0101 | 0 | 2018-04-16 20:00 | 20 | 2 | 86.4836 | 18.0656 | 0 | 2018-04-16 20:00 | 20 | 2 | 86.6896 | 18.1086 | 0 | 2018-04-16 20:00 | 20 | 2 | 65.8058 | 13.7462 | 0
2018-04-16 21:00 | 21 | 2 | 86.1494 | 17.9957 | 0 | 2018-04-16 21:00 | 21 | 2 | 86.4759 | 18.064 | 0 | 2018-04-16 21:00 | 21 | 2 | 86.63 | 18.0961 | 0 | 2018-04-16 21:00 | 21 | 2 | 65.7802 | 13.7408 | 0
2018-04-16 22:00 | 22 | 2 | 86.2593 | 18.0187 | 0 | 2018-04-16 22:00 | 22 | 2 | 86.5522 | 18.0799 | 0 | 2018-04-16 22:00 | 22 | 2 | 86.6468 | 18.0997 | 0 | 2018-04-16 22:00 | 22 | 2 | 65.8156 | 13.7482 | 0
2018-04-16 23:00 | 23 | 2 | 86.4424 | 18.057 | 0 | 2018-04-16 23:00 | 23 | 2 | 86.8055 | 18.1328 | 0 | 2018-04-16 23:00 | 23 | 2 | 86.8864 | 18.1497 | 0 | 2018-04-16 23:00 | 23 | 2 | 66.0029 | 13.7874 | 0
2018-04-17 | 0 | 3 | 86.4637 | 18.0614 | 0 | 2018-04-17 | 0 | 3 | 0 | 0 | 0 | 2018-04-17 | 0 | 3 | 0 | 0 | 0 | 2018-04-17 | 0 | 3 | 0 | 0 | 0
2018-04-17 01:00 | 1 | 3 | 86.5629 | 18.0821 | 0 | 2018-04-17 01:00 | 1 | 3 | 0 | 0 | 0 | 2018-04-17 01:00 | 1 | 3 | 0 | 0 | 0 | 2018-04-17 01:00 | 1 | 3 | 0 | 0 | 0
2018-04-17 02:00 | 2 | 3 | 86.3706 | 18.042 | 0 | 2018-04-17 02:00 | 2 | 3 | 0 | 0 | 0 | 2018-04-17 02:00 | 2 | 3 | 0 | 0 | 0 | 2018-04-17 02:00 | 2 | 3 | 0 | 0 | 0
2018-04-17 03:00 | 3 | 3 | 86.3523 | 18.0381 | 0 | 2018-04-17 03:00 | 3 | 3 | 0 | 0 | 0 | 2018-04-17 03:00 | 3 | 3 | 0 | 0 | 0 | 2018-04-17 03:00 | 3 | 3 | 0 | 0 | 0
2018-04-17 04:00 | 4 | 3 | 86.3676 | 18.0413 | 0 | 2018-04-17 04:00 | 4 | 3 | 0 | 0 | 0 | 2018-04-17 04:00 | 4 | 3 | 0 | 0 | 0 | 2018-04-17 04:00 | 4 | 3 | 0 | 0 | 0
2018-04-17 05:00 | 5 | 3 | 86.4027 | 18.0487 | 0 | 2018-04-17 05:00 | 5 | 3 | 0 | 0 | 0 | 2018-04-17 05:00 | 5 | 3 | 0 | 0 | 0 | 2018-04-17 05:00 | 5 | 3 | 0 | 0 | 0
2018-04-17 06:00 | 6 | 3 | 86.4652 | 18.0617 | 0 | 2018-04-17 06:00 | 6 | 3 | 0 | 0 | 0 | 2018-04-17 06:00 | 6 | 3 | 0 | 0 | 0 | 2018-04-17 06:00 | 6 | 3 | 0 | 0 | 0
2018-04-17 07:00 | 7 | 3 | 86.4012 | 18.0483 | 0 | 2018-04-17 07:00 | 7 | 3 | 0 | 0 | 0 | 2018-04-17 07:00 | 7 | 3 | 0 | 0 | 0 | 2018-04-17 07:00 | 7 | 3 | 0 | 0 | 0
2018-04-17 08:00 | 8 | 3 | 86.4515 | 18.0589 | 0 | 2018-04-17 08:00 | 8 | 3 | 0 | 0 | 0 | 2018-04-17 08:00 | 8 | 3 | 0 | 0 | 0 | 2018-04-17 08:00 | 8 | 3 | 0 | 0 | 0
2018-04-17 09:00 | 9 | 3 | 86.2028 | 18.0069 | 0 | 2018-04-17 09:00 | 9 | 3 | 0 | 0 | 0 | 2018-04-17 09:00 | 9 | 3 | 0 | 0 | 0 | 2018-04-17 09:00 | 9 | 3 | 0 | 0 | 0
2018-04-17 10:00 | 10 | 3 | 86.2715 | 18.0213 | 0 | 2018-04-17 10:00 | 10 | 3 | 0 | 0 | 0 | 2018-04-17 10:00 | 10 | 3 | 0 | 0 | 0 | 2018-04-17 10:00 | 10 | 3 | 0 | 0 | 0
2018-04-17 11:00 | 11 | 3 | 86.7567 | 18.1226 | 0 | 2018-04-17 11:00 | 11 | 3 | 0 | 0 | 0 | 2018-04-17 11:00 | 11 | 3 | 0 | 0 | 0 | 2018-04-17 11:00 | 11 | 3 | 0 | 0 | 0
2018-04-17 12:00 | 12 | 3 | 86.6194 | 18.0939 | 0 | 2018-04-17 12:00 | 12 | 3 | 0 | 0 | 0 | 2018-04-17 12:00 | 12 | 3 | 0 | 0 | 0 | 2018-04-17 12:00 | 12 | 3 | 0 | 0 | 0
2018-04-17 13:00 | 13 | 3 | 86.6377 | 18.0977 | 0 | 2018-04-17 13:00 | 13 | 3 | 0 | 0 | 0 | 2018-04-17 13:00 | 13 | 3 | 0 | 0 | 0 | 2018-04-17 13:00 | 13 | 3 | 0 | 0 | 0
2018-04-17 14:00 | 14 | 3 | 86.8757 | 18.1475 | 0 | 2018-04-17 14:00 | 14 | 3 | 0 | 0 | 0 | 2018-04-17 14:00 | 14 | 3 | 0 | 0 | 0 | 2018-04-17 14:00 | 14 | 3 | 0 | 0 | 0
2018-04-17 15:00 | 15 | 3 | 86.7994 | 18.1315 | 0 | 2018-04-17 15:00 | 15 | 3 | 0 | 0 | 0 | 2018-04-17 15:00 | 15 | 3 | 0 | 0 | 0 | 2018-04-17 15:00 | 15 | 3 | 0 | 0 | 0
2018-04-17 16:00 | 16 | 3 | 86.7674 | 18.1248 | 0 | 2018-04-17 16:00 | 16 | 3 | 0 | 0 | 0 | 2018-04-17 16:00 | 16 | 3 | 0 | 0 | 0 | 2018-04-17 16:00 | 16 | 3 | 0 | 0 | 0
2018-04-17 17:00 | 17 | 3 | 86.7384 | 18.1188 | 0 | 2018-04-17 17:00 | 17 | 3 | 0 | 0 | 0 | 2018-04-17 17:00 | 17 | 3 | 0 | 0 | 0 | 2018-04-17 17:00 | 17 | 3 | 0 | 0 | 0
2018-04-17 18:00 | 18 | 3 | 86.7124 | 18.1134 | 0 | 2018-04-17 18:00 | 18 | 3 | 0 | 0 | 0 | 2018-04-17 18:00 | 18 | 3 | 0 | 0 | 0 | 2018-04-17 18:00 | 18 | 3 | 0 | 0 | 0
2018-04-17 19:00 | 19 | 3 | 86.8376 | 18.1395 | 0 | 2018-04-17 19:00 | 19 | 3 | 0 | 0 | 0 | 2018-04-17 19:00 | 19 | 3 | 0 | 0 | 0 | 2018-04-17 19:00 | 19 | 3 | 0 | 0 | 0
2018-04-17 20:00 | 20 | 3 | 86.627 | 18.0955 | 0 | 2018-04-17 20:00 | 20 | 3 | 0 | 0 | 0 | 2018-04-17 20:00 | 20 | 3 | 0 | 0 | 0 | 2018-04-17 20:00 | 20 | 3 | 0 | 0 | 0
2018-04-17 21:00 | 21 | 3 | 86.6239 | 18.0949 | 0 | 2018-04-17 21:00 | 21 | 3 | 0 | 0 | 0 | 2018-04-17 21:00 | 21 | 3 | 0 | 0 | 0 | 2018-04-17 21:00 | 21 | 3 | 0 | 0 | 0
2018-04-17 22:00 | 22 | 3 | 86.714 | 18.1137 | 0 | 2018-04-17 22:00 | 22 | 3 | 0 | 0 | 0 | 2018-04-17 22:00 | 22 | 3 | 0 | 0 | 0 | 2018-04-17 22:00 | 22 | 3 | 0 | 0 | 0
2018-04-17 23:00 | 23 | 3 | 86.8971 | 18.1519 | 0 | 2018-04-17 23:00 | 23 | 3 | 0 | 0 | 0 | 2018-04-17 23:00 | 23 | 3 | 0 | 0 | 0 | 2018-04-17 23:00 | 23 | 3 | 0 | 0 | 0
2018-04-18 | 0 | 4 | 0 | 0 | 0 | 2018-04-18 | 0 | 4 | 0 | 0 | 0 | 2018-04-18 | 0 | 4 | 86.6712 | 18.1047 | 0 | 2018-04-18 | 0 | 4 | 32.9351 | 6.8798 | 0
2018-04-18 01:00 | 1 | 4 | 0 | 0 | 0 | 2018-04-18 01:00 | 1 | 4 | 0 | 0 | 0 | 2018-04-18 01:00 | 1 | 4 | 86.511 | 18.0713 | 0 | 2018-04-18 01:00 | 1 | 4 | 32.8742 | 6.8671 | 0
2018-04-18 02:00 | 2 | 4 | 0 | 0 | 0 | 2018-04-18 02:00 | 2 | 4 | 0 | 0 | 0 | 2018-04-18 02:00 | 2 | 4 | 86.7628 | 18.1239 | 0 | 2018-04-18 02:00 | 2 | 4 | 32.9699 | 6.8871 | 0
2018-04-18 03:00 | 3 | 4 | 0 | 0 | 0 | 2018-04-18 03:00 | 3 | 4 | 0 | 0 | 0 | 2018-04-18 03:00 | 3 | 4 | 86.7384 | 18.1188 | 0 | 2018-04-18 03:00 | 3 | 4 | 32.9606 | 6.8851 | 0
2018-04-18 04:00 | 4 | 4 | 0 | 0 | 0 | 2018-04-18 04:00 | 4 | 4 | 0 | 0 | 0 | 2018-04-18 04:00 | 4 | 4 | 86.8376 | 18.1395 | 0 | 2018-04-18 04:00 | 4 | 4 | 32.9983 | 6.893 | 0
2018-04-18 05:00 | 5 | 4 | 0 | 0 | 0 | 2018-04-18 05:00 | 5 | 4 | 0 | 0 | 0 | 2018-04-18 05:00 | 5 | 4 | 87.0222 | 18.1781 | 0 | 2018-04-18 05:00 | 5 | 4 | 33.0684 | 6.9077 | 0
2018-04-18 06:00 | 6 | 4 | 0 | 0 | 0 | 2018-04-18 06:00 | 6 | 4 | 0 | 0 | 0 | 2018-04-18 06:00 | 6 | 4 | 86.9627 | 18.1656 | 0 | 2018-04-18 06:00 | 6 | 4 | 33.0458 | 6.9029 | 0
2018-04-18 07:00 | 7 | 4 | 0 | 0 | 0 | 2018-04-18 07:00 | 7 | 4 | 0 | 0 | 0 | 2018-04-18 07:00 | 7 | 4 | 87.1321 | 18.201 | 0 | 2018-04-18 07:00 | 7 | 4 | 33.1102 | 6.9164 | 0
2018-04-18 08:00 | 8 | 4 | 0 | 0 | 0 | 2018-04-18 08:00 | 8 | 4 | 0 | 0 | 0 | 2018-04-18 08:00 | 8 | 4 | 87.1931 | 18.2138 | 0 | 2018-04-18 08:00 | 8 | 4 | 33.1334 | 6.9212 | 0
2018-04-18 09:00 | 9 | 4 | 0 | 0 | 0 | 2018-04-18 09:00 | 9 | 4 | 0 | 0 | 0 | 2018-04-18 09:00 | 9 | 4 | 86.7155 | 18.114 | 0 | 2018-04-18 09:00 | 9 | 4 | 32.9519 | 6.8833 | 0
2018-04-18 10:00 | 10 | 4 | 0 | 0 | 0 | 2018-04-18 10:00 | 10 | 4 | 0 | 0 | 0 | 2018-04-18 10:00 | 10 | 4 | 86.6743 | 18.1054 | 0 | 2018-04-18 10:00 | 10 | 4 | 32.9362 | 6.88 | 0
2018-04-18 11:00 | 11 | 4 | 0 | 0 | 0 | 2018-04-18 11:00 | 11 | 4 | 0 | 0 | 0 | 2018-04-18 11:00 | 11 | 4 | 86.8956 | 18.1516 | 0 | 2018-04-18 11:00 | 11 | 4 | 33.0203 | 6.8976 | 0
2018-04-18 12:00 | 12 | 4 | 0 | 0 | 0 | 2018-04-18 12:00 | 12 | 4 | 0 | 0 | 0 | 2018-04-18 12:00 | 12 | 4 | 86.9276 | 18.1583 | 0 | 2018-04-18 12:00 | 12 | 4 | 33.0325 | 6.9002 | 0
2018-04-18 13:00 | 13 | 4 | 0 | 0 | 0 | 2018-04-18 13:00 | 13 | 4 | 0 | 0 | 0 | 2018-04-18 13:00 | 13 | 4 | 87.2541 | 18.2265 | 0 | 2018-04-18 13:00 | 13 | 4 | 33.1566 | 6.9261 | 0
2018-04-18 14:00 | 14 | 4 | 0 | 0 | 0 | 2018-04-18 14:00 | 14 | 4 | 0 | 0 | 0 | 2018-04-18 14:00 | 14 | 4 | 87.4037 | 18.2578 | 0 | 2018-04-18 14:00 | 14 | 4 | 33.2134 | 6.9379 | 0
2018-04-18 15:00 | 15 | 4 | 0 | 0 | 0 | 2018-04-18 15:00 | 15 | 4 | 0 | 0 | 0 | 2018-04-18 15:00 | 15 | 4 | 87.2129 | 18.2179 | 0 | 2018-04-18 15:00 | 15 | 4 | 33.1409 | 6.9228 | 0
2018-04-18 16:00 | 16 | 4 | 0 | 0 | 0 | 2018-04-18 16:00 | 16 | 4 | 0 | 0 | 0 | 2018-04-18 16:00 | 16 | 4 | 86.9718 | 18.1675 | 0 | 2018-04-18 16:00 | 16 | 4 | 33.0493 | 6.9037 | 0
2018-04-18 17:00 | 17 | 4 | 0 | 0 | 0 | 2018-04-18 17:00 | 17 | 4 | 0 | 0 | 0 | 2018-04-18 17:00 | 17 | 4 | 87.1397 | 18.2026 | 0 | 2018-04-18 17:00 | 17 | 4 | 33.1131 | 6.917 | 0
2018-04-18 18:00 | 18 | 4 | 0 | 0 | 0 | 2018-04-18 18:00 | 18 | 4 | 0 | 0 | 0 | 2018-04-18 18:00 | 18 | 4 | 87.2435 | 18.2243 | 0 | 2018-04-18 18:00 | 18 | 4 | 33.1525 | 6.9252 | 0
2018-04-18 19:00 | 19 | 4 | 0 | 0 | 0 | 2018-04-18 19:00 | 19 | 4 | 0 | 0 | 0 | 2018-04-18 19:00 | 19 | 4 | 86.8894 | 18.1503 | 0 | 2018-04-18 19:00 | 19 | 4 | 33.018 | 6.8971 | 0
2018-04-18 20:00 | 20 | 4 | 0 | 0 | 0 | 2018-04-18 20:00 | 20 | 4 | 0 | 0 | 0 | 2018-04-18 20:00 | 20 | 4 | 87.1839 | 18.2118 | 0 | 2018-04-18 20:00 | 20 | 4 | 33.1299 | 6.9205 | 0
2018-04-18 21:00 | 21 | 4 | 0 | 0 | 0 | 2018-04-18 21:00 | 21 | 4 | 0 | 0 | 0 | 2018-04-18 21:00 | 21 | 4 | 87.2419 | 18.224 | 0 | 2018-04-18 21:00 | 21 | 4 | 33.1519 | 6.9251 | 0
2018-04-18 22:00 | 22 | 4 | 0 | 0 | 0 | 2018-04-18 22:00 | 22 | 4 | 0 | 0 | 0 | 2018-04-18 22:00 | 22 | 4 | 87.1733 | 18.2096 | 0 | 2018-04-18 22:00 | 22 | 4 | 33.1259 | 6.9197 | 0
2018-04-18 23:00 | 23 | 4 | 0 | 0 | 0 | 2018-04-18 23:00 | 23 | 4 | 0 | 0 | 0 | 2018-04-18 23:00 | 23 | 4 | 87.2557 | 18.2268 | 0 | 2018-04-18 23:00 | 23 | 4 | 33.1572 | 6.9262 | 0
2018-04-19 | 0 | 5 | 86.5492 | 18.0793 | 0 | 2018-04-19 | 0 | 5 | 0 | 0 | 0 | 2018-04-19 | 0 | 5 | 0 | 0 | 0 | 2018-04-19 | 0 | 5 | 0 | 0 | 0
2018-04-19 01:00 | 1 | 5 | 86.7201 | 18.115 | 0 | 2018-04-19 01:00 | 1 | 5 | 0 | 0 | 0 | 2018-04-19 01:00 | 1 | 5 | 0 | 0 | 0 | 2018-04-19 01:00 | 1 | 5 | 0 | 0 | 0
2018-04-19 02:00 | 2 | 5 | 86.5095 | 18.071 | 0 | 2018-04-19 02:00 | 2 | 5 | 0 | 0 | 0 | 2018-04-19 02:00 | 2 | 5 | 0 | 0 | 0 | 2018-04-19 02:00 | 2 | 5 | 0 | 0 | 0
2018-04-19 03:00 | 3 | 5 | 86.4576 | 18.0601 | 0 | 2018-04-19 03:00 | 3 | 5 | 0 | 0 | 0 | 2018-04-19 03:00 | 3 | 5 | 0 | 0 | 0 | 2018-04-19 03:00 | 3 | 5 | 0 | 0 | 0
2018-04-19 04:00 | 4 | 5 | 86.6316 | 18.0965 | 0 | 2018-04-19 04:00 | 4 | 5 | 0 | 0 | 0 | 2018-04-19 04:00 | 4 | 5 | 0 | 0 | 0 | 2018-04-19 04:00 | 4 | 5 | 0 | 0 | 0
2018-04-19 05:00 | 5 | 5 | 86.569 | 18.0834 | 0 | 2018-04-19 05:00 | 5 | 5 | 0 | 0 | 0 | 2018-04-19 05:00 | 5 | 5 | 0 | 0 | 0 | 2018-04-19 05:00 | 5 | 5 | 0 | 0 | 0
2018-04-19 06:00 | 6 | 5 | 86.6468 | 18.0997 | 0 | 2018-04-19 06:00 | 6 | 5 | 0 | 0 | 0 | 2018-04-19 06:00 | 6 | 5 | 0 | 0 | 0 | 2018-04-19 06:00 | 6 | 5 | 0 | 0 | 0
2018-04-19 07:00 | 7 | 5 | 86.6361 | 18.0974 | 0 | 2018-04-19 07:00 | 7 | 5 | 0 | 0 | 0 | 2018-04-19 07:00 | 7 | 5 | 0 | 0 | 0 | 2018-04-19 07:00 | 7 | 5 | 0 | 0 | 0
2018-04-19 08:00 | 8 | 5 | 86.6819 | 18.107 | 0 | 2018-04-19 08:00 | 8 | 5 | 0 | 0 | 0 | 2018-04-19 08:00 | 8 | 5 | 0 | 0 | 0 | 2018-04-19 08:00 | 8 | 5 | 0 | 0 | 0
2018-04-19 09:00 | 9 | 5 | 86.7094 | 18.1127 | 0 | 2018-04-19 09:00 | 9 | 5 | 0 | 0 | 0 | 2018-04-19 09:00 | 9 | 5 | 0 | 0 | 0 | 2018-04-19 09:00 | 9 | 5 | 0 | 0 | 0
2018-04-19 10:00 | 10 | 5 | 86.7933 | 18.1303 | 0 | 2018-04-19 10:00 | 10 | 5 | 0 | 0 | 0 | 2018-04-19 10:00 | 10 | 5 | 0 | 0 | 0 | 2018-04-19 10:00 | 10 | 5 | 0 | 0 | 0
2018-04-19 11:00 | 11 | 5 | 86.8009 | 18.1318 | 0 | 2018-04-19 11:00 | 11 | 5 | 0 | 0 | 0 | 2018-04-19 11:00 | 11 | 5 | 0 | 0 | 0 | 2018-04-19 11:00 | 11 | 5 | 0 | 0 | 0
2018-04-19 12:00 | 12 | 5 | 86.6728 | 18.1051 | 0 | 2018-04-19 12:00 | 12 | 5 | 0 | 0 | 0 | 2018-04-19 12:00 | 12 | 5 | 0 | 0 | 0 | 2018-04-19 12:00 | 12 | 5 | 0 | 0 | 0
2018-04-19 13:00 | 13 | 5 | 86.6316 | 18.0965 | 0 | 2018-04-19 13:00 | 13 | 5 | 0 | 0 | 0 | 2018-04-19 13:00 | 13 | 5 | 0 | 0 | 0 | 2018-04-19 13:00 | 13 | 5 | 0 | 0 | 0
2018-04-19 14:00 | 14 | 5 | 86.6316 | 18.0965 | 0 | 2018-04-19 14:00 | 14 | 5 | 0 | 0 | 0 | 2018-04-19 14:00 | 14 | 5 | 0 | 0 | 0 | 2018-04-19 14:00 | 14 | 5 | 0 | 0 | 0
2018-04-19 15:00 | 15 | 5 | 86.6636 | 18.1032 | 0 | 2018-04-19 15:00 | 15 | 5 | 0 | 0 | 0 | 2018-04-19 15:00 | 15 | 5 | 0 | 0 | 0 | 2018-04-19 15:00 | 15 | 5 | 0 | 0 | 0
2018-04-19 16:00 | 16 | 5 | 86.5568 | 18.0808 | 0 | 2018-04-19 16:00 | 16 | 5 | 0 | 0 | 0 | 2018-04-19 16:00 | 16 | 5 | 0 | 0 | 0 | 2018-04-19 16:00 | 16 | 5 | 0 | 0 | 0
2018-04-19 17:00 | 17 | 5 | 86.6865 | 18.1079 | 0 | 2018-04-19 17:00 | 17 | 5 | 0 | 0 | 0 | 2018-04-19 17:00 | 17 | 5 | 0 | 0 | 0 | 2018-04-19 17:00 | 17 | 5 | 0 | 0 | 0
2018-04-19 18:00 | 18 | 5 | 86.7262 | 18.1162 | 0 | 2018-04-19 18:00 | 18 | 5 | 0 | 0 | 0 | 2018-04-19 18:00 | 18 | 5 | 0 | 0 | 0 | 2018-04-19 18:00 | 18 | 5 | 0 | 0 | 0
2018-04-19 19:00 | 19 | 5 | 86.5187 | 18.0729 | 0 | 2018-04-19 19:00 | 19 | 5 | 0 | 0 | 0 | 2018-04-19 19:00 | 19 | 5 | 0 | 0 | 0 | 2018-04-19 19:00 | 19 | 5 | 0 | 0 | 0
2018-04-19 20:00 | 20 | 5 | 86.5766 | 18.085 | 0 | 2018-04-19 20:00 | 20 | 5 | 0 | 0 | 0 | 2018-04-19 20:00 | 20 | 5 | 0 | 0 | 0 | 2018-04-19 20:00 | 20 | 5 | 0 | 0 | 0
2018-04-19 21:00 | 21 | 5 | 86.6194 | 18.0939 | 0 | 2018-04-19 21:00 | 21 | 5 | 0 | 0 | 0 | 2018-04-19 21:00 | 21 | 5 | 0 | 0 | 0 | 2018-04-19 21:00 | 21 | 5 | 0 | 0 | 0
2018-04-19 22:00 | 22 | 5 | 86.6743 | 18.1054 | 0 | 2018-04-19 22:00 | 22 | 5 | 0 | 0 | 0 | 2018-04-19 22:00 | 22 | 5 | 0 | 0 | 0 | 2018-04-19 22:00 | 22 | 5 | 0 | 0 | 0
2018-04-19 23:00 | 23 | 5 | 86.5644 | 18.0824 | 0 | 2018-04-19 23:00 | 23 | 5 | 0 | 0 | 0 | 2018-04-19 23:00 | 23 | 5 | 0 | 0 | 0 | 2018-04-19 23:00 | 23 | 5 | 0 | 0 | 0
2018-04-20 | 0 | 6 | 86.2226 | 18.011 | 0 | 2018-04-20 | 0 | 6 | 86.688 | 18.1083 | 0 | 2018-04-20 | 0 | 6 | 0 | 0 | 0 | 2018-04-20 | 0 | 6 | 32.9414 | 6.8811 | 0
2018-04-20 01:00 | 1 | 6 | 86.1128 | 17.9881 | 0 | 2018-04-20 01:00 | 1 | 6 | 86.5232 | 18.0738 | 0 | 2018-04-20 01:00 | 1 | 6 | 0 | 0 | 0 | 2018-04-20 01:00 | 1 | 6 | 32.8788 | 6.8681 | 0
2018-04-20 02:00 | 2 | 6 | 86.2791 | 18.0228 | 0 | 2018-04-20 02:00 | 2 | 6 | 86.6896 | 18.1086 | 0 | 2018-04-20 02:00 | 2 | 6 | 0 | 0 | 0 | 2018-04-20 02:00 | 2 | 6 | 32.942 | 6.8813 | 0
2018-04-20 03:00 | 3 | 6 | 86.0014 | 17.9648 | 0 | 2018-04-20 03:00 | 3 | 6 | 86.4485 | 18.0582 | 0 | 2018-04-20 03:00 | 3 | 6 | 0 | 0 | 0 | 2018-04-20 03:00 | 3 | 6 | 32.8504 | 6.8621 | 0
2018-04-20 04:00 | 4 | 6 | 86.0533 | 17.9757 | 0 | 2018-04-20 04:00 | 4 | 6 | 86.4347 | 18.0553 | 0 | 2018-04-20 04:00 | 4 | 6 | 0 | 0 | 0 | 2018-04-20 04:00 | 4 | 6 | 32.8452 | 6.861 | 0
2018-04-20 05:00 | 5 | 6 | 86.2257 | 18.0117 | 0 | 2018-04-20 05:00 | 5 | 6 | 86.6117 | 18.0923 | 0 | 2018-04-20 05:00 | 5 | 6 | 0 | 0 | 0 | 2018-04-20 05:00 | 5 | 6 | 32.9124 | 6.8751 | 0
2018-04-20 06:00 | 6 | 6 | 86.4332 | 18.055 | 0 | 2018-04-20 06:00 | 6 | 6 | 86.9352 | 18.1599 | 0 | 2018-04-20 06:00 | 6 | 6 | 0 | 0 | 0 | 2018-04-20 06:00 | 6 | 6 | 33.0354 | 6.9008 | 0
2018-04-20 07:00 | 7 | 6 | 86.5873 | 18.0872 | 0 | 2018-04-20 07:00 | 7 | 6 | 87.0619 | 18.1864 | 0 | 2018-04-20 07:00 | 7 | 6 | 0 | 0 | 0 | 2018-04-20 07:00 | 7 | 6 | 33.0835 | 6.9108 | 0
2018-04-20 08:00 | 8 | 6 | 86.3691 | 18.0416 | 0 | 2018-04-20 08:00 | 8 | 6 | 86.7811 | 18.1277 | 0 | 2018-04-20 08:00 | 8 | 6 | 0 | 0 | 0 | 2018-04-20 08:00 | 8 | 6 | 32.9768 | 6.8885 | 0
2018-04-20 09:00 | 9 | 6 | 86.334 | 18.0343 | 0 | 2018-04-20 09:00 | 9 | 6 | 86.7399 | 18.1191 | 0 | 2018-04-20 09:00 | 9 | 6 | 0 | 0 | 0 | 2018-04-20 09:00 | 9 | 6 | 32.9612 | 6.8853 | 0
2018-04-20 10:00 | 10 | 6 | 86.5126 | 18.0716 | 0 | 2018-04-20 10:00 | 10 | 6 | 86.862 | 18.1446 | 0 | 2018-04-20 10:00 | 10 | 6 | 0 | 0 | 0 | 2018-04-20 10:00 | 10 | 6 | 33.0076 | 6.8949 | 0
2018-04-20 11:00 | 11 | 6 | 86.5003 | 18.069 | 0 | 2018-04-20 11:00 | 11 | 6 | 86.9306 | 18.1589 | 0 | 2018-04-20 11:00 | 11 | 6 | 0 | 0 | 0 | 2018-04-20 11:00 | 11 | 6 | 33.0336 | 6.9004 | 0
2018-04-20 12:00 | 12 | 6 | 86.7002 | 18.1108 | 0 | 2018-04-20 12:00 | 12 | 6 | 87.1412 | 18.2029 | 0 | 2018-04-20 12:00 | 12 | 6 | 0 | 0 | 0 | 2018-04-20 12:00 | 12 | 6 | 33.1137 | 6.9171 | 0
2018-04-20 13:00 | 13 | 6 | 86.363 | 18.0404 | 0 | 2018-04-20 13:00 | 13 | 6 | 86.8009 | 18.1318 | 0 | 2018-04-20 13:00 | 13 | 6 | 0 | 0 | 0 | 2018-04-20 13:00 | 13 | 6 | 32.9843 | 6.8901 | 0
2018-04-20 14:00 | 14 | 6 | 86.4408 | 18.0566 | 0 | 2018-04-20 14:00 | 14 | 6 | 86.8635 | 18.1449 | 0 | 2018-04-20 14:00 | 14 | 6 | 0 | 0 | 0 | 2018-04-20 14:00 | 14 | 6 | 33.0081 | 6.8951 | 0
2018-04-20 15:00 | 15 | 6 | 86.2943 | 18.026 | 0 | 2018-04-20 15:00 | 15 | 6 | 86.6743 | 18.1054 | 0 | 2018-04-20 15:00 | 15 | 6 | 0 | 0 | 0 | 2018-04-20 15:00 | 15 | 6 | 32.9362 | 6.88 | 0
2018-04-20 16:00 | 16 | 6 | 86.3706 | 18.042 | 0 | 2018-04-20 16:00 | 16 | 6 | 86.7491 | 18.121 | 0 | 2018-04-20 16:00 | 16 | 6 | 0 | 0 | 0 | 2018-04-20 16:00 | 16 | 6 | 32.9647 | 6.886 | 0
2018-04-20 17:00 | 17 | 6 | 86.2882 | 18.0247 | 0 | 2018-04-20 17:00 | 17 | 6 | 86.7445 | 18.1201 | 0 | 2018-04-20 17:00 | 17 | 6 | 0 | 0 | 0 | 2018-04-20 17:00 | 17 | 6 | 32.9629 | 6.8856 | 0
2018-04-20 18:00 | 18 | 6 | 86.1875 | 18.0037 | 0 | 2018-04-20 18:00 | 18 | 6 | 86.6667 | 18.1038 | 0 | 2018-04-20 18:00 | 18 | 6 | 0 | 0 | 0 | 2018-04-20 18:00 | 18 | 6 | 32.9333 | 6.8794 | 0
2018-04-20 19:00 | 19 | 6 | 86.099 | 17.9852 | 0 | 2018-04-20 19:00 | 19 | 6 | 86.5431 | 18.078 | 0 | 2018-04-20 19:00 | 19 | 6 | 0 | 0 | 0 | 2018-04-20 19:00 | 19 | 6 | 32.8864 | 6.8696 | 0
2018-04-20 20:00 | 20 | 6 | 86.1997 | 18.0063 | 0 | 2018-04-20 20:00 | 20 | 6 | 86.5187 | 18.0729 | 0 | 2018-04-20 20:00 | 20 | 6 | 0 | 0 | 0 | 2018-04-20 20:00 | 20 | 6 | 32.8771 | 6.8677 | 0
2018-04-20 21:00 | 21 | 6 | 86.3767 | 18.0432 | 0 | 2018-04-20 21:00 | 21 | 6 | 86.7247 | 18.1159 | 0 | 2018-04-20 21:00 | 21 | 6 | 0 | 0 | 0 | 2018-04-20 21:00 | 21 | 6 | 32.9554 | 6.8841 | 0
2018-04-20 22:00 | 22 | 6 | 86.3691 | 18.0416 | 0 | 2018-04-20 22:00 | 22 | 6 | 86.7659 | 18.1245 | 0 | 2018-04-20 22:00 | 22 | 6 | 0 | 0 | 0 | 2018-04-20 22:00 | 22 | 6 | 32.971 | 6.8873 | 0
2018-04-20 23:00 | 23 | 6 | 86.4012 | 18.0483 | 0 | 2018-04-20 23:00 | 23 | 6 | 86.7918 | 18.1299 | 0 | 2018-04-20 23:00 | 23 | 6 | 0 | 0 | 0 | 2018-04-20 23:00 | 23 | 6 | 32.9809 | 6.8894 | 0
2018-04-21 | 0 | 7 | 86.0121 | 17.9671 | 0 | 2018-04-21 | 0 | 7 | 0 | 0 | 0 | 2018-04-21 | 0 | 7 | 86.5507 | 18.0796 | 0 | 2018-04-21 | 0 | 7 | 32.8893 | 6.8702 | 0
2018-04-21 01:00 | 1 | 7 | 85.919 | 17.9476 | 0 | 2018-04-21 01:00 | 1 | 7 | 0 | 0 | 0 | 2018-04-21 01:00 | 1 | 7 | 86.5324 | 18.0758 | 0 | 2018-04-21 01:00 | 1 | 7 | 32.8823 | 6.8688 | 0
2018-04-21 02:00 | 2 | 7 | 86.0533 | 17.9757 | 0 | 2018-04-21 02:00 | 2 | 7 | 0 | 0 | 0 | 2018-04-21 02:00 | 2 | 7 | 86.6453 | 18.0993 | 0 | 2018-04-21 02:00 | 2 | 7 | 32.9252 | 6.8777 | 0
2018-04-21 03:00 | 3 | 7 | 86.1677 | 17.9996 | 0 | 2018-04-21 03:00 | 3 | 7 | 0 | 0 | 0 | 2018-04-21 03:00 | 3 | 7 | 86.7002 | 18.1108 | 0 | 2018-04-21 03:00 | 3 | 7 | 32.9461 | 6.8821 | 0
2018-04-21 04:00 | 4 | 7 | 86.3081 | 18.0289 | 0 | 2018-04-21 04:00 | 4 | 7 | 0 | 0 | 0 | 2018-04-21 04:00 | 4 | 7 | 86.8513 | 18.1424 | 0 | 2018-04-21 04:00 | 4 | 7 | 33.0035 | 6.8941 | 0
2018-04-21 05:00 | 5 | 7 | 86.2562 | 18.0181 | 0 | 2018-04-21 05:00 | 5 | 7 | 0 | 0 | 0 | 2018-04-21 05:00 | 5 | 7 | 86.8605 | 18.1443 | 0 | 2018-04-21 05:00 | 5 | 7 | 33.007 | 6.8948 | 0
2018-04-21 06:00 | 6 | 7 | 86.1234 | 17.9903 | 0 | 2018-04-21 06:00 | 6 | 7 | 0 | 0 | 0 | 2018-04-21 06:00 | 6 | 7 | 86.6682 | 18.1041 | 0 | 2018-04-21 06:00 | 6 | 7 | 32.9339 | 6.8796 | 0
2018-04-21 07:00 | 7 | 7 | 86.1906 | 18.0044 | 0 | 2018-04-21 07:00 | 7 | 7 | 0 | 0 | 0 | 2018-04-21 07:00 | 7 | 7 | 86.7247 | 18.1159 | 0 | 2018-04-21 07:00 | 7 | 7 | 32.9554 | 6.8841 | 0
2018-04-21 08:00 | 8 | 7 | 86.36 | 18.0397 | 0 | 2018-04-21 08:00 | 8 | 7 | 0 | 0 | 0 | 2018-04-21 08:00 | 8 | 7 | 86.952 | 18.1634 | 0 | 2018-04-21 08:00 | 8 | 7 | 33.0418 | 6.9021 | 0
2018-04-21 09:00 | 9 | 7 | 86.4912 | 18.0671 | 0 | 2018-04-21 09:00 | 9 | 7 | 0 | 0 | 0 | 2018-04-21 09:00 | 9 | 7 | 87.0588 | 18.1857 | 0 | 2018-04-21 09:00 | 9 | 7 | 33.0823 | 6.9106 | 0
2018-04-21 10:00 | 10 | 7 | 86.1982 | 18.0059 | 0 | 2018-04-21 10:00 | 10 | 7 | 0 | 0 | 0 | 2018-04-21 10:00 | 10 | 7 | 86.6392 | 18.0981 | 0 | 2018-04-21 10:00 | 10 | 7 | 32.9229 | 6.8773 | 0
2018-04-21 11:00 | 11 | 7 | 86.1707 | 18.0002 | 0 | 2018-04-21 11:00 | 11 | 7 | 0 | 0 | 0 | 2018-04-21 11:00 | 11 | 7 | 86.8849 | 18.1494 | 0 | 2018-04-21 11:00 | 11 | 7 | 33.0163 | 6.8968 | 0
2018-04-21 12:00 | 12 | 7 | 86.5019 | 18.0694 | 0 | 2018-04-21 12:00 | 12 | 7 | 0 | 0 | 0 | 2018-04-21 12:00 | 12 | 7 | 87.1504 | 18.2048 | 0 | 2018-04-21 12:00 | 12 | 7 | 33.1172 | 6.9178 | 0
2018-04-21 13:00 | 13 | 7 | 86.6148 | 18.093 | 0 | 2018-04-21 13:00 | 13 | 7 | 0 | 0 | 0 | 2018-04-21 13:00 | 13 | 7 | 87.3167 | 18.2396 | 0 | 2018-04-21 13:00 | 13 | 7 | 33.1803 | 6.931 | 0
2018-04-21 14:00 | 14 | 7 | 86.4439 | 18.0573 | 0 | 2018-04-21 14:00 | 14 | 7 | 0 | 0 | 0 | 2018-04-21 14:00 | 14 | 7 | 87.0832 | 18.1908 | 0 | 2018-04-21 14:00 | 14 | 7 | 33.0916 | 6.9125 | 0
2018-04-21 15:00 | 15 | 7 | 86.5522 | 18.0799 | 0 | 2018-04-21 15:00 | 15 | 7 | 0 | 0 | 0 | 2018-04-21 15:00 | 15 | 7 | 87.2938 | 18.2348 | 0 | 2018-04-21 15:00 | 15 | 7 | 33.1716 | 6.9292 | 0
2018-04-21 16:00 | 16 | 7 | 86.5644 | 18.0824 | 0 | 2018-04-21 16:00 | 16 | 7 | 0 | 0 | 0 | 2018-04-21 16:00 | 16 | 7 | 87.3579 | 18.2482 | 0 | 2018-04-21 16:00 | 16 | 7 | 33.196 | 6.9343 | 0
2018-04-21 17:00 | 17 | 7 | 86.7445 | 18.1201 | 0 | 2018-04-21 17:00 | 17 | 7 | 0 | 0 | 0 | 2018-04-21 17:00 | 17 | 7 | 87.57 | 18.2925 | 0 | 2018-04-21 17:00 | 17 | 7 | 33.2766 | 6.9511 | 0
2018-04-21 18:00 | 18 | 7 | 86.4668 | 18.062 | 0 | 2018-04-21 18:00 | 18 | 7 | 0 | 0 | 0 | 2018-04-21 18:00 | 18 | 7 | 87.3014 | 18.2364 | 0 | 2018-04-21 18:00 | 18 | 7 | 33.1745 | 6.9298 | 0
2018-04-21 19:00 | 19 | 7 | 86.3661 | 18.041 | 0 | 2018-04-21 19:00 | 19 | 7 | 0 | 0 | 0 | 2018-04-21 19:00 | 19 | 7 | 87.0954 | 18.1934 | 0 | 2018-04-21 19:00 | 19 | 7 | 33.0963 | 6.9135 | 0
2018-04-21 20:00 | 20 | 7 | 86.1173 | 17.989 | 0 | 2018-04-21 20:00 | 20 | 7 | 0 | 0 | 0 | 2018-04-21 20:00 | 20 | 7 | 86.891 | 18.1507 | 0 | 2018-04-21 20:00 | 20 | 7 | 33.0186 | 6.8973 | 0
2018-04-21 21:00 | 21 | 7 | 86.1555 | 17.997 | 0 | 2018-04-21 21:00 | 21 | 7 | 0 | 0 | 0 | 2018-04-21 21:00 | 21 | 7 | 86.9245 | 18.1577 | 0 | 2018-04-21 21:00 | 21 | 7 | 33.0313 | 6.8999 | 0
2018-04-21 22:00 | 22 | 7 | 86.2211 | 18.0107 | 0 | 2018-04-21 22:00 | 22 | 7 | 0 | 0 | 0 | 2018-04-21 22:00 | 22 | 7 | 87.0054 | 18.1746 | 0 | 2018-04-21 22:00 | 22 | 7 | 33.0621 | 6.9063 | 0
2018-04-21 23:00 | 23 | 7 | 86.2226 | 18.011 | 0 | 2018-04-21 23:00 | 23 | 7 | 0 | 0 | 0 | 2018-04-21 23:00 | 23 | 7 | 87.0787 | 18.1899 | 0 | 2018-04-21 23:00 | 23 | 7 | 33.0899 | 6.9122 | 0
2018-04-22 | 0 | 1 | 86.2364 | 18.0139 | 0 | 2018-04-22 | 0 | 1 | 86.7994 | 18.1315 | 0 | 2018-04-22 | 0 | 1 | 0 | 0 | 0 | 2018-04-22 | 0 | 1 | 32.9838 | 6.89 | 0
2018-04-22 01:00 | 1 | 1 | 86.3188 | 18.0311 | 0 | 2018-04-22 01:00 | 1 | 1 | 86.952 | 18.1634 | 0 | 2018-04-22 01:00 | 1 | 1 | 0 | 0 | 0 | 2018-04-22 01:00 | 1 | 1 | 33.0418 | 6.9021 | 0
2018-04-22 02:00 | 2 | 1 | 86.2119 | 18.0088 | 0 | 2018-04-22 02:00 | 2 | 1 | 86.8177 | 18.1353 | 0 | 2018-04-22 02:00 | 2 | 1 | 0 | 0 | 0 | 2018-04-22 02:00 | 2 | 1 | 32.9907 | 6.8914 | 0
2018-04-22 03:00 | 3 | 1 | 86.1845 | 18.0031 | 0 | 2018-04-22 03:00 | 3 | 1 | 86.7857 | 18.1287 | 0 | 2018-04-22 03:00 | 3 | 1 | 0 | 0 | 0 | 2018-04-22 03:00 | 3 | 1 | 32.9786 | 6.8889 | 0
2018-04-22 04:00 | 4 | 1 | 86.2455 | 18.0158 | 0 | 2018-04-22 04:00 | 4 | 1 | 86.833 | 18.1385 | 0 | 2018-04-22 04:00 | 4 | 1 | 0 | 0 | 0 | 2018-04-22 04:00 | 4 | 1 | 32.9965 | 6.8926 | 0
2018-04-22 05:00 | 5 | 1 | 86.2333 | 18.0133 | 0 | 2018-04-22 05:00 | 5 | 1 | 86.833 | 18.1385 | 0 | 2018-04-22 05:00 | 5 | 1 | 0 | 0 | 0 | 2018-04-22 05:00 | 5 | 1 | 32.9965 | 6.8926 | 0
2018-04-22 06:00 | 6 | 1 | 86.2776 | 18.0225 | 0 | 2018-04-22 06:00 | 6 | 1 | 86.8528 | 18.1427 | 0 | 2018-04-22 06:00 | 6 | 1 | 0 | 0 | 0 | 2018-04-22 06:00 | 6 | 1 | 33.0041 | 6.8942 | 0
2018-04-22 07:00 | 7 | 1 | 86.2867 | 18.0244 | 0 | 2018-04-22 07:00 | 7 | 1 | 86.8452 | 18.1411 | 0 | 2018-04-22 07:00 | 7 | 1 | 0 | 0 | 0 | 2018-04-22 07:00 | 7 | 1 | 33.0012 | 6.8936 | 0
2018-04-22 08:00 | 8 | 1 | 86.2989 | 18.027 | 0 | 2018-04-22 08:00 | 8 | 1 | 86.9032 | 18.1532 | 0 | 2018-04-22 08:00 | 8 | 1 | 0 | 0 | 0 | 2018-04-22 08:00 | 8 | 1 | 33.0232 | 6.8982 | 0
2018-04-22 09:00 | 9 | 1 | 86.2867 | 18.0244 | 0 | 2018-04-22 09:00 | 9 | 1 | 86.8162 | 18.135 | 0 | 2018-04-22 09:00 | 9 | 1 | 0 | 0 | 0 | 2018-04-22 09:00 | 9 | 1 | 32.9902 | 6.8913 | 0
2018-04-22 10:00 | 10 | 1 | 86.2882 | 18.0247 | 0 | 2018-04-22 10:00 | 10 | 1 | 86.8528 | 18.1427 | 0 | 2018-04-22 10:00 | 10 | 1 | 0 | 0 | 0 | 2018-04-22 10:00 | 10 | 1 | 33.0041 | 6.8942 | 0
2018-04-22 11:00 | 11 | 1 | 86.1845 | 18.0031 | 0 | 2018-04-22 11:00 | 11 | 1 | 86.743 | 18.1197 | 0 | 2018-04-22 11:00 | 11 | 1 | 0 | 0 | 0 | 2018-04-22 11:00 | 11 | 1 | 32.9623 | 6.8855 | 0
2018-04-22 12:00 | 12 | 1 | 86.1418 | 17.9942 | 0 | 2018-04-22 12:00 | 12 | 1 | 86.714 | 18.1137 | 0 | 2018-04-22 12:00 | 12 | 1 | 0 | 0 | 0 | 2018-04-22 12:00 | 12 | 1 | 32.9513 | 6.8832 | 0
2018-04-22 13:00 | 13 | 1 | 86.1479 | 17.9954 | 0 | 2018-04-22 13:00 | 13 | 1 | 86.7659 | 18.1245 | 0 | 2018-04-22 13:00 | 13 | 1 | 0 | 0 | 0 | 2018-04-22 13:00 | 13 | 1 | 32.971 | 6.8873 | 0
2018-04-22 14:00 | 14 | 1 | 86.1112 | 17.9878 | 0 | 2018-04-22 14:00 | 14 | 1 | 86.7018 | 18.1111 | 0 | 2018-04-22 14:00 | 14 | 1 | 0 | 0 | 0 | 2018-04-22 14:00 | 14 | 1 | 32.9467 | 6.8822 | 0
2018-04-22 15:00 | 15 | 1 | 86.2455 | 18.0158 | 0 | 2018-04-22 15:00 | 15 | 1 | 86.8482 | 18.1417 | 0 | 2018-04-22 15:00 | 15 | 1 | 0 | 0 | 0 | 2018-04-22 15:00 | 15 | 1 | 33.0023 | 6.8939 | 0
2018-04-22 16:00 | 16 | 1 | 86.3447 | 18.0365 | 0 | 2018-04-22 16:00 | 16 | 1 | 86.9398 | 18.1609 | 0 | 2018-04-22 16:00 | 16 | 1 | 0 | 0 | 0 | 2018-04-22 16:00 | 16 | 1 | 33.0371 | 6.9011 | 0
2018-04-22 17:00 | 17 | 1 | 86.4805 | 18.0649 | 0 | 2018-04-22 17:00 | 17 | 1 | 86.9856 | 18.1704 | 0 | 2018-04-22 17:00 | 17 | 1 | 0 | 0 | 0 | 2018-04-22 17:00 | 17 | 1 | 33.0545 | 6.9048 | 0
2018-04-22 18:00 | 18 | 1 | 86.4332 | 18.055 | 0 | 2018-04-22 18:00 | 18 | 1 | 86.92 | 18.1567 | 0 | 2018-04-22 18:00 | 18 | 1 | 0 | 0 | 0 | 2018-04-22 18:00 | 18 | 1 | 33.0296 | 6.8996 | 0
2018-04-22 19:00 | 19 | 1 | 85.6794 | 17.8976 | 0 | 2018-04-22 19:00 | 19 | 1 | 85.9266 | 17.9492 | 0 | 2018-04-22 19:00 | 19 | 1 | 0 | 0 | 0 | 2018-04-22 19:00 | 19 | 1 | 32.6521 | 6.8207 | 0
2018-04-22 20:00 | 20 | 1 | 86.3294 | 18.0333 | 0 | 2018-04-22 20:00 | 20 | 1 | 86.5888 | 18.0875 | 0 | 2018-04-22 20:00 | 20 | 1 | 0 | 0 | 0 | 2018-04-22 20:00 | 20 | 1 | 32.9037 | 6.8733 | 0
2018-04-22 21:00 | 21 | 1 | 86.3569 | 18.0391 | 0 | 2018-04-22 21:00 | 21 | 1 | 86.6728 | 18.1051 | 0 | 2018-04-22 21:00 | 21 | 1 | 0 | 0 | 0 | 2018-04-22 21:00 | 21 | 1 | 32.9357 | 6.8799 | 0
2018-04-22 22:00 | 22 | 1 | 86.4881 | 18.0665 | 0 | 2018-04-22 22:00 | 22 | 1 | 86.8086 | 18.1334 | 0 | 2018-04-22 22:00 | 22 | 1 | 0 | 0 | 0 | 2018-04-22 22:00 | 22 | 1 | 32.9873 | 6.8907 | 0
2018-04-22 23:00 | 23 | 1 | 86.4332 | 18.055 | 0 | 2018-04-22 23:00 | 23 | 1 | 86.7353 | 18.1181 | 0 | 2018-04-22 23:00 | 23 | 1 | 0 | 0 | 0 | 2018-04-22 23:00 | 23 | 1 | 32.9594 | 6.8849 | 0
2018-04-23 | 0 | 2 | 86.4088 | 18.0499 | 0 | 2018-04-23 | 0 | 2 | 86.7002 | 18.1108 | 0 | 2018-04-23 | 0 | 2 | 86.9352 | 18.1599 | 0 | 2018-04-23 | 0 | 2 | 65.9815 | 13.7829 | 0
2018-04-23 01:00 | 1 | 2 | 86.0426 | 17.9734 | 0 | 2018-04-23 01:00 | 1 | 2 | 86.3127 | 18.0299 | 0 | 2018-04-23 01:00 | 1 | 2 | 86.5278 | 18.0748 | 0 | 2018-04-23 01:00 | 1 | 2 | 65.6794 | 13.7198 | 0
2018-04-23 02:00 | 2 | 2 | 86.392 | 18.0464 | 0 | 2018-04-23 02:00 | 2 | 2 | 86.6392 | 18.0981 | 0 | 2018-04-23 02:00 | 2 | 2 | 86.8421 | 18.1404 | 0 | 2018-04-23 02:00 | 2 | 2 | 65.9229 | 13.7706 | 0
2018-04-23 03:00 | 3 | 2 | 86.2776 | 18.0225 | 0 | 2018-04-23 03:00 | 3 | 2 | 86.5766 | 18.085 | 0 | 2018-04-23 03:00 | 3 | 2 | 86.7536 | 18.122 | 0 | 2018-04-23 03:00 | 3 | 2 | 65.8655 | 13.7586 | 0
2018-04-23 04:00 | 4 | 2 | 86.5034 | 18.0697 | 0 | 2018-04-23 04:00 | 4 | 2 | 86.8849 | 18.1494 | 0 | 2018-04-23 04:00 | 4 | 2 | 87.0283 | 18.1793 | 0 | 2018-04-23 04:00 | 4 | 2 | 66.087 | 13.8049 | 0
2018-04-23 05:00 | 5 | 2 | 86.3661 | 18.041 | 0 | 2018-04-23 05:00 | 5 | 2 | 86.772 | 18.1258 | 0 | 2018-04-23 05:00 | 5 | 2 | 87.0054 | 18.1746 | 0 | 2018-04-23 05:00 | 5 | 2 | 66.0354 | 13.7941 | 0
2018-04-23 06:00 | 6 | 2 | 86.2898 | 18.0251 | 0 | 2018-04-23 06:00 | 6 | 2 | 86.6499 | 18.1003 | 0 | 2018-04-23 06:00 | 6 | 2 | 86.8147 | 18.1347 | 0 | 2018-04-23 06:00 | 6 | 2 | 65.9165 | 13.7693 | 0
2018-04-23 07:00 | 7 | 2 | 86.2043 | 18.0072 | 0 | 2018-04-23 07:00 | 7 | 2 | 86.5278 | 18.0748 | 0 | 2018-04-23 07:00 | 7 | 2 | 86.7079 | 18.1124 | 0 | 2018-04-23 07:00 | 7 | 2 | 65.8296 | 13.7511 | 0
2018-04-23 08:00 | 8 | 2 | 86.3355 | 18.0346 | 0 | 2018-04-23 08:00 | 8 | 2 | 86.5461 | 18.0786 | 0 | 2018-04-23 08:00 | 8 | 2 | 86.8025 | 18.1322 | 0 | 2018-04-23 08:00 | 8 | 2 | 65.8725 | 13.7601 | 0
2018-04-23 09:00 | 9 | 2 | 86.3798 | 18.0439 | 0 | 2018-04-23 09:00 | 9 | 2 | 86.7262 | 18.1162 | 0 | 2018-04-23 09:00 | 9 | 2 | 86.8711 | 18.1465 | 0 | 2018-04-23 09:00 | 9 | 2 | 65.967 | 13.7798 | 0
2018-04-23 10:00 | 10 | 2 | 86.2272 | 18.012 | 0 | 2018-04-23 10:00 | 10 | 2 | 86.5156 | 18.0722 | 0 | 2018-04-23 10:00 | 10 | 2 | 86.714 | 18.1137 | 0 | 2018-04-23 10:00 | 10 | 2 | 65.8272 | 13.7507 | 0
2018-04-23 11:00 | 11 | 2 | 86.2119 | 18.0088 | 0 | 2018-04-23 11:00 | 11 | 2 | 86.5141 | 18.0719 | 0 | 2018-04-23 11:00 | 11 | 2 | 86.7201 | 18.115 | 0 | 2018-04-23 11:00 | 11 | 2 | 65.829 | 13.751 | 0
2018-04-23 12:00 | 12 | 2 | 86.389 | 18.0458 | 0 | 2018-04-23 12:00 | 12 | 2 | 86.6835 | 18.1073 | 0 | 2018-04-23 12:00 | 12 | 2 | 86.8574 | 18.1436 | 0 | 2018-04-23 12:00 | 12 | 2 | 65.9455 | 13.7754 | 0
2018-04-23 13:00 | 13 | 2 | 86.4027 | 18.0487 | 0 | 2018-04-23 13:00 | 13 | 2 | 86.6224 | 18.0946 | 0 | 2018-04-23 13:00 | 13 | 2 | 86.7475 | 18.1207 | 0 | 2018-04-23 13:00 | 13 | 2 | 65.8806 | 13.7618 | 0
2018-04-23 14:00 | 14 | 2 | 86.3783 | 18.0436 | 0 | 2018-04-23 14:00 | 14 | 2 | 86.6606 | 18.1025 | 0 | 2018-04-23 14:00 | 14 | 2 | 86.7903 | 18.1296 | 0 | 2018-04-23 14:00 | 14 | 2 | 65.9113 | 13.7682 | 0
2018-04-23 15:00 | 15 | 2 | 86.3355 | 18.0346 | 0 | 2018-04-23 15:00 | 15 | 2 | 86.5248 | 18.0742 | 0 | 2018-04-23 15:00 | 15 | 2 | 86.7384 | 18.1188 | 0 | 2018-04-23 15:00 | 15 | 2 | 65.84 | 13.7533 | 0
2018-04-23 16:00 | 16 | 2 | 86.3493 | 18.0375 | 0 | 2018-04-23 16:00 | 16 | 2 | 86.4912 | 18.0671 | 0 | 2018-04-23 16:00 | 16 | 2 | 86.685 | 18.1076 | 0 | 2018-04-23 16:00 | 16 | 2 | 65.807 | 13.7464 | 0
2018-04-23 17:00 | 17 | 2 | 86.244 | 18.0155 | 0 | 2018-04-23 17:00 | 17 | 2 | 86.4683 | 18.0624 | 0 | 2018-04-23 17:00 | 17 | 2 | 86.6743 | 18.1054 | 0 | 2018-04-23 17:00 | 17 | 2 | 65.7942 | 13.7437 | 0
2018-04-23 18:00 | 18 | 2 | 86.3142 | 18.0302 | 0 | 2018-04-23 18:00 | 18 | 2 | 86.4378 | 18.056 | 0 | 2018-04-23 18:00 | 18 | 2 | 86.5934 | 18.0885 | 0 | 2018-04-23 18:00 | 18 | 2 | 65.7519 | 13.7349 | 0
2018-04-23 19:00 | 19 | 2 | 86.2089 | 18.0082 | 0 | 2018-04-23 19:00 | 19 | 2 | 86.3508 | 18.0378 | 0 | 2018-04-23 19:00 | 19 | 2 | 86.5583 | 18.0812 | 0 | 2018-04-23 19:00 | 19 | 2 | 65.7055 | 13.7252 | 0
2018-04-23 20:00 | 20 | 2 | 86.2181 | 18.0101 | 0 | 2018-04-23 20:00 | 20 | 2 | 86.4836 | 18.0656 | 0 | 2018-04-23 20:00 | 20 | 2 | 86.6896 | 18.1086 | 0 | 2018-04-23 20:00 | 20 | 2 | 65.8058 | 13.7462 | 0
2018-04-23 21:00 | 21 | 2 | 86.1494 | 17.9957 | 0 | 2018-04-23 21:00 | 21 | 2 | 86.4759 | 18.064 | 0 | 2018-04-23 21:00 | 21 | 2 | 86.63 | 18.0961 | 0 | 2018-04-23 21:00 | 21 | 2 | 65.7802 | 13.7408 | 0
2018-04-23 22:00 | 22 | 2 | 86.2593 | 18.0187 | 0 | 2018-04-23 22:00 | 22 | 2 | 86.5522 | 18.0799 | 0 | 2018-04-23 22:00 | 22 | 2 | 86.6468 | 18.0997 | 0 | 2018-04-23 22:00 | 22 | 2 | 65.8156 | 13.7482 | 0
2018-04-23 23:00 | 23 | 2 | 86.4424 | 18.057 | 0 | 2018-04-23 23:00 | 23 | 2 | 86.8055 | 18.1328 | 0 | 2018-04-23 23:00 | 23 | 2 | 86.8864 | 18.1497 | 0 | 2018-04-23 23:00 | 23 | 2 | 66.0029 | 13.7874 | 0
2018-04-24 | 0 | 3 | 86.4637 | 18.0614 | 0 | 2018-04-24 | 0 | 3 | 0 | 0 | 0 | 2018-04-24 | 0 | 3 | 0 | 0 | 0 | 2018-04-24 | 0 | 3 | 0 | 0 | 0
2018-04-24 01:00 | 1 | 3 | 86.5629 | 18.0821 | 0 | 2018-04-24 01:00 | 1 | 3 | 0 | 0 | 0 | 2018-04-24 01:00 | 1 | 3 | 0 | 0 | 0 | 2018-04-24 01:00 | 1 | 3 | 0 | 0 | 0
2018-04-24 02:00 | 2 | 3 | 86.3706 | 18.042 | 0 | 2018-04-24 02:00 | 2 | 3 | 0 | 0 | 0 | 2018-04-24 02:00 | 2 | 3 | 0 | 0 | 0 | 2018-04-24 02:00 | 2 | 3 | 0 | 0 | 0
2018-04-24 03:00 | 3 | 3 | 86.3523 | 18.0381 | 0 | 2018-04-24 03:00 | 3 | 3 | 0 | 0 | 0 | 2018-04-24 03:00 | 3 | 3 | 0 | 0 | 0 | 2018-04-24 03:00 | 3 | 3 | 0 | 0 | 0
2018-04-24 04:00 | 4 | 3 | 86.3676 | 18.0413 | 0 | 2018-04-24 04:00 | 4 | 3 | 0 | 0 | 0 | 2018-04-24 04:00 | 4 | 3 | 0 | 0 | 0 | 2018-04-24 04:00 | 4 | 3 | 0 | 0 | 0
2018-04-24 05:00 | 5 | 3 | 86.4027 | 18.0487 | 0 | 2018-04-24 05:00 | 5 | 3 | 0 | 0 | 0 | 2018-04-24 05:00 | 5 | 3 | 0 | 0 | 0 | 2018-04-24 05:00 | 5 | 3 | 0 | 0 | 0
2018-04-24 06:00 | 6 | 3 | 86.4652 | 18.0617 | 0 | 2018-04-24 06:00 | 6 | 3 | 0 | 0 | 0 | 2018-04-24 06:00 | 6 | 3 | 0 | 0 | 0 | 2018-04-24 06:00 | 6 | 3 | 0 | 0 | 0
2018-04-24 07:00 | 7 | 3 | 86.4012 | 18.0483 | 0 | 2018-04-24 07:00 | 7 | 3 | 0 | 0 | 0 | 2018-04-24 07:00 | 7 | 3 | 0 | 0 | 0 | 2018-04-24 07:00 | 7 | 3 | 0 | 0 | 0
2018-04-24 08:00 | 8 | 3 | 86.4515 | 18.0589 | 0 | 2018-04-24 08:00 | 8 | 3 | 0 | 0 | 0 | 2018-04-24 08:00 | 8 | 3 | 0 | 0 | 0 | 2018-04-24 08:00 | 8 | 3 | 0 | 0 | 0
2018-04-24 09:00 | 9 | 3 | 86.2028 | 18.0069 | 0 | 2018-04-24 09:00 | 9 | 3 | 0 | 0 | 0 | 2018-04-24 09:00 | 9 | 3 | 0 | 0 | 0 | 2018-04-24 09:00 | 9 | 3 | 0 | 0 | 0
2018-04-24 10:00 | 10 | 3 | 86.2715 | 18.0213 | 0 | 2018-04-24 10:00 | 10 | 3 | 0 | 0 | 0 | 2018-04-24 10:00 | 10 | 3 | 0 | 0 | 0 | 2018-04-24 10:00 | 10 | 3 | 0 | 0 | 0
2018-04-24 11:00 | 11 | 3 | 86.7567 | 18.1226 | 0 | 2018-04-24 11:00 | 11 | 3 | 0 | 0 | 0 | 2018-04-24 11:00 | 11 | 3 | 0 | 0 | 0 | 2018-04-24 11:00 | 11 | 3 | 0 | 0 | 0
2018-04-24 12:00 | 12 | 3 | 86.6194 | 18.0939 | 0 | 2018-04-24 12:00 | 12 | 3 | 0 | 0 | 0 | 2018-04-24 12:00 | 12 | 3 | 0 | 0 | 0 | 2018-04-24 12:00 | 12 | 3 | 0 | 0 | 0
2018-04-24 13:00 | 13 | 3 | 86.6377 | 18.0977 | 0 | 2018-04-24 13:00 | 13 | 3 | 0 | 0 | 0 | 2018-04-24 13:00 | 13 | 3 | 0 | 0 | 0 | 2018-04-24 13:00 | 13 | 3 | 0 | 0 | 0
2018-04-24 14:00 | 14 | 3 | 86.8757 | 18.1475 | 0 | 2018-04-24 14:00 | 14 | 3 | 0 | 0 | 0 | 2018-04-24 14:00 | 14 | 3 | 0 | 0 | 0 | 2018-04-24 14:00 | 14 | 3 | 0 | 0 | 0
2018-04-24 15:00 | 15 | 3 | 86.7994 | 18.1315 | 0 | 2018-04-24 15:00 | 15 | 3 | 0 | 0 | 0 | 2018-04-24 15:00 | 15 | 3 | 0 | 0 | 0 | 2018-04-24 15:00 | 15 | 3 | 0 | 0 | 0
2018-04-24 16:00 | 16 | 3 | 86.7674 | 18.1248 | 0 | 2018-04-24 16:00 | 16 | 3 | 0 | 0 | 0 | 2018-04-24 16:00 | 16 | 3 | 0 | 0 | 0 | 2018-04-24 16:00 | 16 | 3 | 0 | 0 | 0
2018-04-24 17:00 | 17 | 3 | 86.7384 | 18.1188 | 0 | 2018-04-24 17:00 | 17 | 3 | 0 | 0 | 0 | 2018-04-24 17:00 | 17 | 3 | 0 | 0 | 0 | 2018-04-24 17:00 | 17 | 3 | 0 | 0 | 0
2018-04-24 18:00 | 18 | 3 | 86.7124 | 18.1134 | 0 | 2018-04-24 18:00 | 18 | 3 | 0 | 0 | 0 | 2018-04-24 18:00 | 18 | 3 | 0 | 0 | 0 | 2018-04-24 18:00 | 18 | 3 | 0 | 0 | 0
2018-04-24 19:00 | 19 | 3 | 86.8376 | 18.1395 | 0 | 2018-04-24 19:00 | 19 | 3 | 0 | 0 | 0 | 2018-04-24 19:00 | 19 | 3 | 0 | 0 | 0 | 2018-04-24 19:00 | 19 | 3 | 0 | 0 | 0
2018-04-24 20:00 | 20 | 3 | 86.627 | 18.0955 | 0 | 2018-04-24 20:00 | 20 | 3 | 0 | 0 | 0 | 2018-04-24 20:00 | 20 | 3 | 0 | 0 | 0 | 2018-04-24 20:00 | 20 | 3 | 0 | 0 | 0
2018-04-24 21:00 | 21 | 3 | 86.6239 | 18.0949 | 0 | 2018-04-24 21:00 | 21 | 3 | 0 | 0 | 0 | 2018-04-24 21:00 | 21 | 3 | 0 | 0 | 0 | 2018-04-24 21:00 | 21 | 3 | 0 | 0 | 0
2018-04-24 22:00 | 22 | 3 | 86.714 | 18.1137 | 0 | 2018-04-24 22:00 | 22 | 3 | 0 | 0 | 0 | 2018-04-24 22:00 | 22 | 3 | 0 | 0 | 0 | 2018-04-24 22:00 | 22 | 3 | 0 | 0 | 0
2018-04-24 23:00 | 23 | 3 | 86.8971 | 18.1519 | 0 | 2018-04-24 23:00 | 23 | 3 | 0 | 0 | 0 | 2018-04-24 23:00 | 23 | 3 | 0 | 0 | 0 | 2018-04-24 23:00 | 23 | 3 | 0 | 0 | 0
2018-04-25 | 0 | 4 | 0 | 0 | 0 | 2018-04-25 | 0 | 4 | 0 | 0 | 0 | 2018-04-25 | 0 | 4 | 86.6712 | 18.1047 | 0 | 2018-04-25 | 0 | 4 | 32.9351 | 6.8798 | 0
2018-04-25 01:00 | 1 | 4 | 0 | 0 | 0 | 2018-04-25 01:00 | 1 | 4 | 0 | 0 | 0 | 2018-04-25 01:00 | 1 | 4 | 86.511 | 18.0713 | 0 | 2018-04-25 01:00 | 1 | 4 | 32.8742 | 6.8671 | 0
2018-04-25 02:00 | 2 | 4 | 0 | 0 | 0 | 2018-04-25 02:00 | 2 | 4 | 0 | 0 | 0 | 2018-04-25 02:00 | 2 | 4 | 86.7628 | 18.1239 | 0 | 2018-04-25 02:00 | 2 | 4 | 32.9699 | 6.8871 | 0
2018-04-25 03:00 | 3 | 4 | 0 | 0 | 0 | 2018-04-25 03:00 | 3 | 4 | 0 | 0 | 0 | 2018-04-25 03:00 | 3 | 4 | 86.7384 | 18.1188 | 0 | 2018-04-25 03:00 | 3 | 4 | 32.9606 | 6.8851 | 0
2018-04-25 04:00 | 4 | 4 | 0 | 0 | 0 | 2018-04-25 04:00 | 4 | 4 | 0 | 0 | 0 | 2018-04-25 04:00 | 4 | 4 | 86.8376 | 18.1395 | 0 | 2018-04-25 04:00 | 4 | 4 | 32.9983 | 6.893 | 0
2018-04-25 05:00 | 5 | 4 | 0 | 0 | 0 | 2018-04-25 05:00 | 5 | 4 | 0 | 0 | 0 | 2018-04-25 05:00 | 5 | 4 | 87.0222 | 18.1781 | 0 | 2018-04-25 05:00 | 5 | 4 | 33.0684 | 6.9077 | 0
2018-04-25 06:00 | 6 | 4 | 0 | 0 | 0 | 2018-04-25 06:00 | 6 | 4 | 0 | 0 | 0 | 2018-04-25 06:00 | 6 | 4 | 86.9627 | 18.1656 | 0 | 2018-04-25 06:00 | 6 | 4 | 33.0458 | 6.9029 | 0
2018-04-25 07:00 | 7 | 4 | 0 | 0 | 0 | 2018-04-25 07:00 | 7 | 4 | 0 | 0 | 0 | 2018-04-25 07:00 | 7 | 4 | 87.1321 | 18.201 | 0 | 2018-04-25 07:00 | 7 | 4 | 33.1102 | 6.9164 | 0
2018-04-25 08:00 | 8 | 4 | 0 | 0 | 0 | 2018-04-25 08:00 | 8 | 4 | 0 | 0 | 0 | 2018-04-25 08:00 | 8 | 4 | 87.1931 | 18.2138 | 0 | 2018-04-25 08:00 | 8 | 4 | 33.1334 | 6.9212 | 0
2018-04-25 09:00 | 9 | 4 | 0 | 0 | 0 | 2018-04-25 09:00 | 9 | 4 | 0 | 0 | 0 | 2018-04-25 09:00 | 9 | 4 | 86.7155 | 18.114 | 0 | 2018-04-25 09:00 | 9 | 4 | 32.9519 | 6.8833 | 0
2018-04-25 10:00 | 10 | 4 | 0 | 0 | 0 | 2018-04-25 10:00 | 10 | 4 | 0 | 0 | 0 | 2018-04-25 10:00 | 10 | 4 | 86.6743 | 18.1054 | 0 | 2018-04-25 10:00 | 10 | 4 | 32.9362 | 6.88 | 0
2018-04-25 11:00 | 11 | 4 | 0 | 0 | 0 | 2018-04-25 11:00 | 11 | 4 | 0 | 0 | 0 | 2018-04-25 11:00 | 11 | 4 | 86.8956 | 18.1516 | 0 | 2018-04-25 11:00 | 11 | 4 | 33.0203 | 6.8976 | 0
2018-04-25 12:00 | 12 | 4 | 0 | 0 | 0 | 2018-04-25 12:00 | 12 | 4 | 0 | 0 | 0 | 2018-04-25 12:00 | 12 | 4 | 86.9276 | 18.1583 | 0 | 2018-04-25 12:00 | 12 | 4 | 33.0325 | 6.9002 | 0
2018-04-25 13:00 | 13 | 4 | 0 | 0 | 0 | 2018-04-25 13:00 | 13 | 4 | 0 | 0 | 0 | 2018-04-25 13:00 | 13 | 4 | 87.2541 | 18.2265 | 0 | 2018-04-25 13:00 | 13 | 4 | 33.1566 | 6.9261 | 0
2018-04-25 14:00 | 14 | 4 | 0 | 0 | 0 | 2018-04-25 14:00 | 14 | 4 | 0 | 0 | 0 | 2018-04-25 14:00 | 14 | 4 | 87.4037 | 18.2578 | 0 | 2018-04-25 14:00 | 14 | 4 | 33.2134 | 6.9379 | 0
2018-04-25 15:00 | 15 | 4 | 0 | 0 | 0 | 2018-04-25 15:00 | 15 | 4 | 0 | 0 | 0 | 2018-04-25 15:00 | 15 | 4 | 87.2129 | 18.2179 | 0 | 2018-04-25 15:00 | 15 | 4 | 33.1409 | 6.9228 | 0
2018-04-25 16:00 | 16 | 4 | 0 | 0 | 0 | 2018-04-25 16:00 | 16 | 4 | 0 | 0 | 0 | 2018-04-25 16:00 | 16 | 4 | 86.9718 | 18.1675 | 0 | 2018-04-25 16:00 | 16 | 4 | 33.0493 | 6.9037 | 0
2018-04-25 17:00 | 17 | 4 | 0 | 0 | 0 | 2018-04-25 17:00 | 17 | 4 | 0 | 0 | 0 | 2018-04-25 17:00 | 17 | 4 | 87.1397 | 18.2026 | 0 | 2018-04-25 17:00 | 17 | 4 | 33.1131 | 6.917 | 0
2018-04-25 18:00 | 18 | 4 | 0 | 0 | 0 | 2018-04-25 18:00 | 18 | 4 | 0 | 0 | 0 | 2018-04-25 18:00 | 18 | 4 | 87.2435 | 18.2243 | 0 | 2018-04-25 18:00 | 18 | 4 | 33.1525 | 6.9252 | 0
2018-04-25 19:00 | 19 | 4 | 0 | 0 | 0 | 2018-04-25 19:00 | 19 | 4 | 0 | 0 | 0 | 2018-04-25 19:00 | 19 | 4 | 86.8894 | 18.1503 | 0 | 2018-04-25 19:00 | 19 | 4 | 33.018 | 6.8971 | 0
2018-04-25 20:00 | 20 | 4 | 0 | 0 | 0 | 2018-04-25 20:00 | 20 | 4 | 0 | 0 | 0 | 2018-04-25 20:00 | 20 | 4 | 87.1839 | 18.2118 | 0 | 2018-04-25 20:00 | 20 | 4 | 33.1299 | 6.9205 | 0
2018-04-25 21:00 | 21 | 4 | 0 | 0 | 0 | 2018-04-25 21:00 | 21 | 4 | 0 | 0 | 0 | 2018-04-25 21:00 | 21 | 4 | 87.2419 | 18.224 | 0 | 2018-04-25 21:00 | 21 | 4 | 33.1519 | 6.9251 | 0
2018-04-25 22:00 | 22 | 4 | 0 | 0 | 0 | 2018-04-25 22:00 | 22 | 4 | 0 | 0 | 0 | 2018-04-25 22:00 | 22 | 4 | 87.1733 | 18.2096 | 0 | 2018-04-25 22:00 | 22 | 4 | 33.1259 | 6.9197 | 0
2018-04-25 23:00 | 23 | 4 | 0 | 0 | 0 | 2018-04-25 23:00 | 23 | 4 | 0 | 0 | 0 | 2018-04-25 23:00 | 23 | 4 | 87.2557 | 18.2268 | 0 | 2018-04-25 23:00 | 23 | 4 | 33.1572 | 6.9262 | 0
2018-04-26 | 0 | 5 | 86.5492 | 18.0793 | 0 | 2018-04-26 | 0 | 5 | 0 | 0 | 0 | 2018-04-26 | 0 | 5 | 0 | 0 | 0 | 2018-04-26 | 0 | 5 | 0 | 0 | 0
2018-04-26 01:00 | 1 | 5 | 86.7201 | 18.115 | 0 | 2018-04-26 01:00 | 1 | 5 | 0 | 0 | 0 | 2018-04-26 01:00 | 1 | 5 | 0 | 0 | 0 | 2018-04-26 01:00 | 1 | 5 | 0 | 0 | 0
2018-04-26 02:00 | 2 | 5 | 86.5095 | 18.071 | 0 | 2018-04-26 02:00 | 2 | 5 | 0 | 0 | 0 | 2018-04-26 02:00 | 2 | 5 | 0 | 0 | 0 | 2018-04-26 02:00 | 2 | 5 | 0 | 0 | 0
2018-04-26 03:00 | 3 | 5 | 86.4576 | 18.0601 | 0 | 2018-04-26 03:00 | 3 | 5 | 0 | 0 | 0 | 2018-04-26 03:00 | 3 | 5 | 0 | 0 | 0 | 2018-04-26 03:00 | 3 | 5 | 0 | 0 | 0
2018-04-26 04:00 | 4 | 5 | 86.6316 | 18.0965 | 0 | 2018-04-26 04:00 | 4 | 5 | 0 | 0 | 0 | 2018-04-26 04:00 | 4 | 5 | 0 | 0 | 0 | 2018-04-26 04:00 | 4 | 5 | 0 | 0 | 0
2018-04-26 05:00 | 5 | 5 | 86.569 | 18.0834 | 0 | 2018-04-26 05:00 | 5 | 5 | 0 | 0 | 0 | 2018-04-26 05:00 | 5 | 5 | 0 | 0 | 0 | 2018-04-26 05:00 | 5 | 5 | 0 | 0 | 0
2018-04-26 06:00 | 6 | 5 | 86.6468 | 18.0997 | 0 | 2018-04-26 06:00 | 6 | 5 | 0 | 0 | 0 | 2018-04-26 06:00 | 6 | 5 | 0 | 0 | 0 | 2018-04-26 06:00 | 6 | 5 | 0 | 0 | 0
2018-04-26 07:00 | 7 | 5 | 86.6361 | 18.0974 | 0 | 2018-04-26 07:00 | 7 | 5 | 0 | 0 | 0 | 2018-04-26 07:00 | 7 | 5 | 0 | 0 | 0 | 2018-04-26 07:00 | 7 | 5 | 0 | 0 | 0
2018-04-26 08:00 | 8 | 5 | 86.6819 | 18.107 | 0 | 2018-04-26 08:00 | 8 | 5 | 0 | 0 | 0 | 2018-04-26 08:00 | 8 | 5 | 0 | 0 | 0 | 2018-04-26 08:00 | 8 | 5 | 0 | 0 | 0
2018-04-26 09:00 | 9 | 5 | 86.7094 | 18.1127 | 0 | 2018-04-26 09:00 | 9 | 5 | 0 | 0 | 0 | 2018-04-26 09:00 | 9 | 5 | 0 | 0 | 0 | 2018-04-26 09:00 | 9 | 5 | 0 | 0 | 0
2018-04-26 10:00 | 10 | 5 | 86.7933 | 18.1303 | 0 | 2018-04-26 10:00 | 10 | 5 | 0 | 0 | 0 | 2018-04-26 10:00 | 10 | 5 | 0 | 0 | 0 | 2018-04-26 10:00 | 10 | 5 | 0 | 0 | 0
2018-04-26 11:00 | 11 | 5 | 86.8009 | 18.1318 | 0 | 2018-04-26 11:00 | 11 | 5 | 0 | 0 | 0 | 2018-04-26 11:00 | 11 | 5 | 0 | 0 | 0 | 2018-04-26 11:00 | 11 | 5 | 0 | 0 | 0
2018-04-26 12:00 | 12 | 5 | 86.6728 | 18.1051 | 0 | 2018-04-26 12:00 | 12 | 5 | 0 | 0 | 0 | 2018-04-26 12:00 | 12 | 5 | 0 | 0 | 0 | 2018-04-26 12:00 | 12 | 5 | 0 | 0 | 0
2018-04-26 13:00 | 13 | 5 | 86.6316 | 18.0965 | 0 | 2018-04-26 13:00 | 13 | 5 | 0 | 0 | 0 | 2018-04-26 13:00 | 13 | 5 | 0 | 0 | 0 | 2018-04-26 13:00 | 13 | 5 | 0 | 0 | 0
2018-04-26 14:00 | 14 | 5 | 86.6316 | 18.0965 | 0 | 2018-04-26 14:00 | 14 | 5 | 0 | 0 | 0 | 2018-04-26 14:00 | 14 | 5 | 0 | 0 | 0 | 2018-04-26 14:00 | 14 | 5 | 0 | 0 | 0
2018-04-26 15:00 | 15 | 5 | 86.6636 | 18.1032 | 0 | 2018-04-26 15:00 | 15 | 5 | 0 | 0 | 0 | 2018-04-26 15:00 | 15 | 5 | 0 | 0 | 0 | 2018-04-26 15:00 | 15 | 5 | 0 | 0 | 0
2018-04-26 16:00 | 16 | 5 | 86.5568 | 18.0808 | 0 | 2018-04-26 16:00 | 16 | 5 | 0 | 0 | 0 | 2018-04-26 16:00 | 16 | 5 | 0 | 0 | 0 | 2018-04-26 16:00 | 16 | 5 | 0 | 0 | 0
2018-04-26 17:00 | 17 | 5 | 86.6865 | 18.1079 | 0 | 2018-04-26 17:00 | 17 | 5 | 0 | 0 | 0 | 2018-04-26 17:00 | 17 | 5 | 0 | 0 | 0 | 2018-04-26 17:00 | 17 | 5 | 0 | 0 | 0
2018-04-26 18:00 | 18 | 5 | 86.7262 | 18.1162 | 0 | 2018-04-26 18:00 | 18 | 5 | 0 | 0 | 0 | 2018-04-26 18:00 | 18 | 5 | 0 | 0 | 0 | 2018-04-26 18:00 | 18 | 5 | 0 | 0 | 0
2018-04-26 19:00 | 19 | 5 | 86.5187 | 18.0729 | 0 | 2018-04-26 19:00 | 19 | 5 | 0 | 0 | 0 | 2018-04-26 19:00 | 19 | 5 | 0 | 0 | 0 | 2018-04-26 19:00 | 19 | 5 | 0 | 0 | 0
2018-04-26 20:00 | 20 | 5 | 86.5766 | 18.085 | 0 | 2018-04-26 20:00 | 20 | 5 | 0 | 0 | 0 | 2018-04-26 20:00 | 20 | 5 | 0 | 0 | 0 | 2018-04-26 20:00 | 20 | 5 | 0 | 0 | 0
2018-04-26 21:00 | 21 | 5 | 86.6194 | 18.0939 | 0 | 2018-04-26 21:00 | 21 | 5 | 0 | 0 | 0 | 2018-04-26 21:00 | 21 | 5 | 0 | 0 | 0 | 2018-04-26 21:00 | 21 | 5 | 0 | 0 | 0
2018-04-26 22:00 | 22 | 5 | 86.6743 | 18.1054 | 0 | 2018-04-26 22:00 | 22 | 5 | 0 | 0 | 0 | 2018-04-26 22:00 | 22 | 5 | 0 | 0 | 0 | 2018-04-26 22:00 | 22 | 5 | 0 | 0 | 0
2018-04-26 23:00 | 23 | 5 | 86.5644 | 18.0824 | 0 | 2018-04-26 23:00 | 23 | 5 | 0 | 0 | 0 | 2018-04-26 23:00 | 23 | 5 | 0 | 0 | 0 | 2018-04-26 23:00 | 23 | 5 | 0 | 0 | 0
2018-04-27 | 0 | 6 | 86.2226 | 18.011 | 0 | 2018-04-27 | 0 | 6 | 86.688 | 18.1083 | 0 | 2018-04-27 | 0 | 6 | 0 | 0 | 0 | 2018-04-27 | 0 | 6 | 32.9414 | 6.8811 | 0
2018-04-27 01:00 | 1 | 6 | 86.1128 | 17.9881 | 0 | 2018-04-27 01:00 | 1 | 6 | 86.5232 | 18.0738 | 0 | 2018-04-27 01:00 | 1 | 6 | 0 | 0 | 0 | 2018-04-27 01:00 | 1 | 6 | 32.8788 | 6.8681 | 0
2018-04-27 02:00 | 2 | 6 | 86.2791 | 18.0228 | 0 | 2018-04-27 02:00 | 2 | 6 | 86.6896 | 18.1086 | 0 | 2018-04-27 02:00 | 2 | 6 | 0 | 0 | 0 | 2018-04-27 02:00 | 2 | 6 | 32.942 | 6.8813 | 0
2018-04-27 03:00 | 3 | 6 | 86.0014 | 17.9648 | 0 | 2018-04-27 03:00 | 3 | 6 | 86.4485 | 18.0582 | 0 | 2018-04-27 03:00 | 3 | 6 | 0 | 0 | 0 | 2018-04-27 03:00 | 3 | 6 | 32.8504 | 6.8621 | 0
2018-04-27 04:00 | 4 | 6 | 86.0533 | 17.9757 | 0 | 2018-04-27 04:00 | 4 | 6 | 86.4347 | 18.0553 | 0 | 2018-04-27 04:00 | 4 | 6 | 0 | 0 | 0 | 2018-04-27 04:00 | 4 | 6 | 32.8452 | 6.861 | 0
2018-04-27 05:00 | 5 | 6 | 86.2257 | 18.0117 | 0 | 2018-04-27 05:00 | 5 | 6 | 86.6117 | 18.0923 | 0 | 2018-04-27 05:00 | 5 | 6 | 0 | 0 | 0 | 2018-04-27 05:00 | 5 | 6 | 32.9124 | 6.8751 | 0
2018-04-27 06:00 | 6 | 6 | 86.4332 | 18.055 | 0 | 2018-04-27 06:00 | 6 | 6 | 86.9352 | 18.1599 | 0 | 2018-04-27 06:00 | 6 | 6 | 0 | 0 | 0 | 2018-04-27 06:00 | 6 | 6 | 33.0354 | 6.9008 | 0
2018-04-27 07:00 | 7 | 6 | 86.5873 | 18.0872 | 0 | 2018-04-27 07:00 | 7 | 6 | 87.0619 | 18.1864 | 0 | 2018-04-27 07:00 | 7 | 6 | 0 | 0 | 0 | 2018-04-27 07:00 | 7 | 6 | 33.0835 | 6.9108 | 0
2018-04-27 08:00 | 8 | 6 | 86.3691 | 18.0416 | 0 | 2018-04-27 08:00 | 8 | 6 | 86.7811 | 18.1277 | 0 | 2018-04-27 08:00 | 8 | 6 | 0 | 0 | 0 | 2018-04-27 08:00 | 8 | 6 | 32.9768 | 6.8885 | 0
2018-04-27 09:00 | 9 | 6 | 86.334 | 18.0343 | 0 | 2018-04-27 09:00 | 9 | 6 | 86.7399 | 18.1191 | 0 | 2018-04-27 09:00 | 9 | 6 | 0 | 0 | 0 | 2018-04-27 09:00 | 9 | 6 | 32.9612 | 6.8853 | 0
2018-04-27 10:00 | 10 | 6 | 86.5126 | 18.0716 | 0 | 2018-04-27 10:00 | 10 | 6 | 86.862 | 18.1446 | 0 | 2018-04-27 10:00 | 10 | 6 | 0 | 0 | 0 | 2018-04-27 10:00 | 10 | 6 | 33.0076 | 6.8949 | 0
2018-04-27 11:00 | 11 | 6 | 86.5003 | 18.069 | 0 | 2018-04-27 11:00 | 11 | 6 | 86.9306 | 18.1589 | 0 | 2018-04-27 11:00 | 11 | 6 | 0 | 0 | 0 | 2018-04-27 11:00 | 11 | 6 | 33.0336 | 6.9004 | 0
2018-04-27 12:00 | 12 | 6 | 86.7002 | 18.1108 | 0 | 2018-04-27 12:00 | 12 | 6 | 87.1412 | 18.2029 | 0 | 2018-04-27 12:00 | 12 | 6 | 0 | 0 | 0 | 2018-04-27 12:00 | 12 | 6 | 33.1137 | 6.9171 | 0
2018-04-27 13:00 | 13 | 6 | 86.363 | 18.0404 | 0 | 2018-04-27 13:00 | 13 | 6 | 86.8009 | 18.1318 | 0 | 2018-04-27 13:00 | 13 | 6 | 0 | 0 | 0 | 2018-04-27 13:00 | 13 | 6 | 32.9843 | 6.8901 | 0
2018-04-27 14:00 | 14 | 6 | 86.4408 | 18.0566 | 0 | 2018-04-27 14:00 | 14 | 6 | 86.8635 | 18.1449 | 0 | 2018-04-27 14:00 | 14 | 6 | 0 | 0 | 0 | 2018-04-27 14:00 | 14 | 6 | 33.0081 | 6.8951 | 0
2018-04-27 15:00 | 15 | 6 | 86.2943 | 18.026 | 0 | 2018-04-27 15:00 | 15 | 6 | 86.6743 | 18.1054 | 0 | 2018-04-27 15:00 | 15 | 6 | 0 | 0 | 0 | 2018-04-27 15:00 | 15 | 6 | 32.9362 | 6.88 | 0
2018-04-27 16:00 | 16 | 6 | 86.3706 | 18.042 | 0 | 2018-04-27 16:00 | 16 | 6 | 86.7491 | 18.121 | 0 | 2018-04-27 16:00 | 16 | 6 | 0 | 0 | 0 | 2018-04-27 16:00 | 16 | 6 | 32.9647 | 6.886 | 0
2018-04-27 17:00 | 17 | 6 | 86.2882 | 18.0247 | 0 | 2018-04-27 17:00 | 17 | 6 | 86.7445 | 18.1201 | 0 | 2018-04-27 17:00 | 17 | 6 | 0 | 0 | 0 | 2018-04-27 17:00 | 17 | 6 | 32.9629 | 6.8856 | 0
2018-04-27 18:00 | 18 | 6 | 86.1875 | 18.0037 | 0 | 2018-04-27 18:00 | 18 | 6 | 86.6667 | 18.1038 | 0 | 2018-04-27 18:00 | 18 | 6 | 0 | 0 | 0 | 2018-04-27 18:00 | 18 | 6 | 32.9333 | 6.8794 | 0
2018-04-27 19:00 | 19 | 6 | 86.099 | 17.9852 | 0 | 2018-04-27 19:00 | 19 | 6 | 86.5431 | 18.078 | 0 | 2018-04-27 19:00 | 19 | 6 | 0 | 0 | 0 | 2018-04-27 19:00 | 19 | 6 | 32.8864 | 6.8696 | 0
2018-04-27 20:00 | 20 | 6 | 86.1997 | 18.0063 | 0 | 2018-04-27 20:00 | 20 | 6 | 86.5187 | 18.0729 | 0 | 2018-04-27 20:00 | 20 | 6 | 0 | 0 | 0 | 2018-04-27 20:00 | 20 | 6 | 32.8771 | 6.8677 | 0
2018-04-27 21:00 | 21 | 6 | 86.3767 | 18.0432 | 0 | 2018-04-27 21:00 | 21 | 6 | 86.7247 | 18.1159 | 0 | 2018-04-27 21:00 | 21 | 6 | 0 | 0 | 0 | 2018-04-27 21:00 | 21 | 6 | 32.9554 | 6.8841 | 0
2018-04-27 22:00 | 22 | 6 | 86.3691 | 18.0416 | 0 | 2018-04-27 22:00 | 22 | 6 | 86.7659 | 18.1245 | 0 | 2018-04-27 22:00 | 22 | 6 | 0 | 0 | 0 | 2018-04-27 22:00 | 22 | 6 | 32.971 | 6.8873 | 0
2018-04-27 23:00 | 23 | 6 | 86.4012 | 18.0483 | 0 | 2018-04-27 23:00 | 23 | 6 | 86.7918 | 18.1299 | 0 | 2018-04-27 23:00 | 23 | 6 | 0 | 0 | 0 | 2018-04-27 23:00 | 23 | 6 | 32.9809 | 6.8894 | 0
2018-04-28 | 0 | 7 | 86.0121 | 17.9671 | 0 | 2018-04-28 | 0 | 7 | 0 | 0 | 0 | 2018-04-28 | 0 | 7 | 86.5507 | 18.0796 | 0 | 2018-04-28 | 0 | 7 | 32.8893 | 6.8702 | 0
2018-04-28 01:00 | 1 | 7 | 85.919 | 17.9476 | 0 | 2018-04-28 01:00 | 1 | 7 | 0 | 0 | 0 | 2018-04-28 01:00 | 1 | 7 | 86.5324 | 18.0758 | 0 | 2018-04-28 01:00 | 1 | 7 | 32.8823 | 6.8688 | 0
2018-04-28 02:00 | 2 | 7 | 86.0533 | 17.9757 | 0 | 2018-04-28 02:00 | 2 | 7 | 0 | 0 | 0 | 2018-04-28 02:00 | 2 | 7 | 86.6453 | 18.0993 | 0 | 2018-04-28 02:00 | 2 | 7 | 32.9252 | 6.8777 | 0
2018-04-28 03:00 | 3 | 7 | 86.1677 | 17.9996 | 0 | 2018-04-28 03:00 | 3 | 7 | 0 | 0 | 0 | 2018-04-28 03:00 | 3 | 7 | 86.7002 | 18.1108 | 0 | 2018-04-28 03:00 | 3 | 7 | 32.9461 | 6.8821 | 0
2018-04-28 04:00 | 4 | 7 | 86.3081 | 18.0289 | 0 | 2018-04-28 04:00 | 4 | 7 | 0 | 0 | 0 | 2018-04-28 04:00 | 4 | 7 | 86.8513 | 18.1424 | 0 | 2018-04-28 04:00 | 4 | 7 | 33.0035 | 6.8941 | 0
2018-04-28 05:00 | 5 | 7 | 86.2562 | 18.0181 | 0 | 2018-04-28 05:00 | 5 | 7 | 0 | 0 | 0 | 2018-04-28 05:00 | 5 | 7 | 86.8605 | 18.1443 | 0 | 2018-04-28 05:00 | 5 | 7 | 33.007 | 6.8948 | 0
2018-04-28 06:00 | 6 | 7 | 86.1234 | 17.9903 | 0 | 2018-04-28 06:00 | 6 | 7 | 0 | 0 | 0 | 2018-04-28 06:00 | 6 | 7 | 86.6682 | 18.1041 | 0 | 2018-04-28 06:00 | 6 | 7 | 32.9339 | 6.8796 | 0
2018-04-28 07:00 | 7 | 7 | 86.1906 | 18.0044 | 0 | 2018-04-28 07:00 | 7 | 7 | 0 | 0 | 0 | 2018-04-28 07:00 | 7 | 7 | 86.7247 | 18.1159 | 0 | 2018-04-28 07:00 | 7 | 7 | 32.9554 | 6.8841 | 0
2018-04-28 08:00 | 8 | 7 | 86.36 | 18.0397 | 0 | 2018-04-28 08:00 | 8 | 7 | 0 | 0 | 0 | 2018-04-28 08:00 | 8 | 7 | 86.952 | 18.1634 | 0 | 2018-04-28 08:00 | 8 | 7 | 33.0418 | 6.9021 | 0
2018-04-28 09:00 | 9 | 7 | 86.4912 | 18.0671 | 0 | 2018-04-28 09:00 | 9 | 7 | 0 | 0 | 0 | 2018-04-28 09:00 | 9 | 7 | 87.0588 | 18.1857 | 0 | 2018-04-28 09:00 | 9 | 7 | 33.0823 | 6.9106 | 0
2018-04-28 10:00 | 10 | 7 | 86.1982 | 18.0059 | 0 | 2018-04-28 10:00 | 10 | 7 | 0 | 0 | 0 | 2018-04-28 10:00 | 10 | 7 | 86.6392 | 18.0981 | 0 | 2018-04-28 10:00 | 10 | 7 | 32.9229 | 6.8773 | 0
2018-04-28 11:00 | 11 | 7 | 86.1707 | 18.0002 | 0 | 2018-04-28 11:00 | 11 | 7 | 0 | 0 | 0 | 2018-04-28 11:00 | 11 | 7 | 86.8849 | 18.1494 | 0 | 2018-04-28 11:00 | 11 | 7 | 33.0163 | 6.8968 | 0
2018-04-28 12:00 | 12 | 7 | 86.5019 | 18.0694 | 0 | 2018-04-28 12:00 | 12 | 7 | 0 | 0 | 0 | 2018-04-28 12:00 | 12 | 7 | 87.1504 | 18.2048 | 0 | 2018-04-28 12:00 | 12 | 7 | 33.1172 | 6.9178 | 0
2018-04-28 13:00 | 13 | 7 | 86.6148 | 18.093 | 0 | 2018-04-28 13:00 | 13 | 7 | 0 | 0 | 0 | 2018-04-28 13:00 | 13 | 7 | 87.3167 | 18.2396 | 0 | 2018-04-28 13:00 | 13 | 7 | 33.1803 | 6.931 | 0
2018-04-28 14:00 | 14 | 7 | 86.4439 | 18.0573 | 0 | 2018-04-28 14:00 | 14 | 7 | 0 | 0 | 0 | 2018-04-28 14:00 | 14 | 7 | 87.0832 | 18.1908 | 0 | 2018-04-28 14:00 | 14 | 7 | 33.0916 | 6.9125 | 0
2018-04-28 15:00 | 15 | 7 | 86.5522 | 18.0799 | 0 | 2018-04-28 15:00 | 15 | 7 | 0 | 0 | 0 | 2018-04-28 15:00 | 15 | 7 | 87.2938 | 18.2348 | 0 | 2018-04-28 15:00 | 15 | 7 | 33.1716 | 6.9292 | 0
2018-04-28 16:00 | 16 | 7 | 86.5644 | 18.0824 | 0 | 2018-04-28 16:00 | 16 | 7 | 0 | 0 | 0 | 2018-04-28 16:00 | 16 | 7 | 87.3579 | 18.2482 | 0 | 2018-04-28 16:00 | 16 | 7 | 33.196 | 6.9343 | 0
2018-04-28 17:00 | 17 | 7 | 86.7445 | 18.1201 | 0 | 2018-04-28 17:00 | 17 | 7 | 0 | 0 | 0 | 2018-04-28 17:00 | 17 | 7 | 87.57 | 18.2925 | 0 | 2018-04-28 17:00 | 17 | 7 | 33.2766 | 6.9511 | 0
2018-04-28 18:00 | 18 | 7 | 86.4668 | 18.062 | 0 | 2018-04-28 18:00 | 18 | 7 | 0 | 0 | 0 | 2018-04-28 18:00 | 18 | 7 | 87.3014 | 18.2364 | 0 | 2018-04-28 18:00 | 18 | 7 | 33.1745 | 6.9298 | 0
2018-04-28 19:00 | 19 | 7 | 86.3661 | 18.041 | 0 | 2018-04-28 19:00 | 19 | 7 | 0 | 0 | 0 | 2018-04-28 19:00 | 19 | 7 | 87.0954 | 18.1934 | 0 | 2018-04-28 19:00 | 19 | 7 | 33.0963 | 6.9135 | 0
2018-04-28 20:00 | 20 | 7 | 86.1173 | 17.989 | 0 | 2018-04-28 20:00 | 20 | 7 | 0 | 0 | 0 | 2018-04-28 20:00 | 20 | 7 | 86.891 | 18.1507 | 0 | 2018-04-28 20:00 | 20 | 7 | 33.0186 | 6.8973 | 0
2018-04-28 21:00 | 21 | 7 | 86.1555 | 17.997 | 0 | 2018-04-28 21:00 | 21 | 7 | 0 | 0 | 0 | 2018-04-28 21:00 | 21 | 7 | 86.9245 | 18.1577 | 0 | 2018-04-28 21:00 | 21 | 7 | 33.0313 | 6.8999 | 0
2018-04-28 22:00 | 22 | 7 | 86.2211 | 18.0107 | 0 | 2018-04-28 22:00 | 22 | 7 | 0 | 0 | 0 | 2018-04-28 22:00 | 22 | 7 | 87.0054 | 18.1746 | 0 | 2018-04-28 22:00 | 22 | 7 | 33.0621 | 6.9063 | 0
2018-04-28 23:00 | 23 | 7 | 86.2226 | 18.011 | 0 | 2018-04-28 23:00 | 23 | 7 | 0 | 0 | 0 | 2018-04-28 23:00 | 23 | 7 | 87.0787 | 18.1899 | 0 | 2018-04-28 23:00 | 23 | 7 | 33.0899 | 6.9122 | 0
2018-04-29 | 0 | 1 | 86.2364 | 18.0139 | 0 | 2018-04-29 | 0 | 1 | 86.7994 | 18.1315 | 0 | 2018-04-29 | 0 | 1 | 0 | 0 | 0 | 2018-04-29 | 0 | 1 | 32.9838 | 6.89 | 0
2018-04-29 01:00 | 1 | 1 | 86.3188 | 18.0311 | 0 | 2018-04-29 01:00 | 1 | 1 | 86.952 | 18.1634 | 0 | 2018-04-29 01:00 | 1 | 1 | 0 | 0 | 0 | 2018-04-29 01:00 | 1 | 1 | 33.0418 | 6.9021 | 0
2018-04-29 02:00 | 2 | 1 | 86.2119 | 18.0088 | 0 | 2018-04-29 02:00 | 2 | 1 | 86.8177 | 18.1353 | 0 | 2018-04-29 02:00 | 2 | 1 | 0 | 0 | 0 | 2018-04-29 02:00 | 2 | 1 | 32.9907 | 6.8914 | 0
2018-04-29 03:00 | 3 | 1 | 86.1845 | 18.0031 | 0 | 2018-04-29 03:00 | 3 | 1 | 86.7857 | 18.1287 | 0 | 2018-04-29 03:00 | 3 | 1 | 0 | 0 | 0 | 2018-04-29 03:00 | 3 | 1 | 32.9786 | 6.8889 | 0
2018-04-29 04:00 | 4 | 1 | 86.2455 | 18.0158 | 0 | 2018-04-29 04:00 | 4 | 1 | 86.833 | 18.1385 | 0 | 2018-04-29 04:00 | 4 | 1 | 0 | 0 | 0 | 2018-04-29 04:00 | 4 | 1 | 32.9965 | 6.8926 | 0
2018-04-29 05:00 | 5 | 1 | 86.2333 | 18.0133 | 0 | 2018-04-29 05:00 | 5 | 1 | 86.833 | 18.1385 | 0 | 2018-04-29 05:00 | 5 | 1 | 0 | 0 | 0 | 2018-04-29 05:00 | 5 | 1 | 32.9965 | 6.8926 | 0
2018-04-29 06:00 | 6 | 1 | 86.2776 | 18.0225 | 0 | 2018-04-29 06:00 | 6 | 1 | 86.8528 | 18.1427 | 0 | 2018-04-29 06:00 | 6 | 1 | 0 | 0 | 0 | 2018-04-29 06:00 | 6 | 1 | 33.0041 | 6.8942 | 0
2018-04-29 07:00 | 7 | 1 | 86.2867 | 18.0244 | 0 | 2018-04-29 07:00 | 7 | 1 | 86.8452 | 18.1411 | 0 | 2018-04-29 07:00 | 7 | 1 | 0 | 0 | 0 | 2018-04-29 07:00 | 7 | 1 | 33.0012 | 6.8936 | 0
2018-04-29 08:00 | 8 | 1 | 86.2989 | 18.027 | 0 | 2018-04-29 08:00 | 8 | 1 | 86.9032 | 18.1532 | 0 | 2018-04-29 08:00 | 8 | 1 | 0 | 0 | 0 | 2018-04-29 08:00 | 8 | 1 | 33.0232 | 6.8982 | 0
2018-04-29 09:00 | 9 | 1 | 86.2867 | 18.0244 | 0 | 2018-04-29 09:00 | 9 | 1 | 86.8162 | 18.135 | 0 | 2018-04-29 09:00 | 9 | 1 | 0 | 0 | 0 | 2018-04-29 09:00 | 9 | 1 | 32.9902 | 6.8913 | 0
2018-04-29 10:00 | 10 | 1 | 86.2882 | 18.0247 | 0 | 2018-04-29 10:00 | 10 | 1 | 86.8528 | 18.1427 | 0 | 2018-04-29 10:00 | 10 | 1 | 0 | 0 | 0 | 2018-04-29 10:00 | 10 | 1 | 33.0041 | 6.8942 | 0
2018-04-29 11:00 | 11 | 1 | 86.1845 | 18.0031 | 0 | 2018-04-29 11:00 | 11 | 1 | 86.743 | 18.1197 | 0 | 2018-04-29 11:00 | 11 | 1 | 0 | 0 | 0 | 2018-04-29 11:00 | 11 | 1 | 32.9623 | 6.8855 | 0
2018-04-29 12:00 | 12 | 1 | 86.1418 | 17.9942 | 0 | 2018-04-29 12:00 | 12 | 1 | 86.714 | 18.1137 | 0 | 2018-04-29 12:00 | 12 | 1 | 0 | 0 | 0 | 2018-04-29 12:00 | 12 | 1 | 32.9513 | 6.8832 | 0
2018-04-29 13:00 | 13 | 1 | 86.1479 | 17.9954 | 0 | 2018-04-29 13:00 | 13 | 1 | 86.7659 | 18.1245 | 0 | 2018-04-29 13:00 | 13 | 1 | 0 | 0 | 0 | 2018-04-29 13:00 | 13 | 1 | 32.971 | 6.8873 | 0
2018-04-29 14:00 | 14 | 1 | 86.1112 | 17.9878 | 0 | 2018-04-29 14:00 | 14 | 1 | 86.7018 | 18.1111 | 0 | 2018-04-29 14:00 | 14 | 1 | 0 | 0 | 0 | 2018-04-29 14:00 | 14 | 1 | 32.9467 | 6.8822 | 0
2018-04-29 15:00 | 15 | 1 | 86.2455 | 18.0158 | 0 | 2018-04-29 15:00 | 15 | 1 | 86.8482 | 18.1417 | 0 | 2018-04-29 15:00 | 15 | 1 | 0 | 0 | 0 | 2018-04-29 15:00 | 15 | 1 | 33.0023 | 6.8939 | 0
2018-04-29 16:00 | 16 | 1 | 86.3447 | 18.0365 | 0 | 2018-04-29 16:00 | 16 | 1 | 86.9398 | 18.1609 | 0 | 2018-04-29 16:00 | 16 | 1 | 0 | 0 | 0 | 2018-04-29 16:00 | 16 | 1 | 33.0371 | 6.9011 | 0
2018-04-29 17:00 | 17 | 1 | 86.4805 | 18.0649 | 0 | 2018-04-29 17:00 | 17 | 1 | 86.9856 | 18.1704 | 0 | 2018-04-29 17:00 | 17 | 1 | 0 | 0 | 0 | 2018-04-29 17:00 | 17 | 1 | 33.0545 | 6.9048 | 0
2018-04-29 18:00 | 18 | 1 | 86.4332 | 18.055 | 0 | 2018-04-29 18:00 | 18 | 1 | 86.92 | 18.1567 | 0 | 2018-04-29 18:00 | 18 | 1 | 0 | 0 | 0 | 2018-04-29 18:00 | 18 | 1 | 33.0296 | 6.8996 | 0
2018-04-29 19:00 | 19 | 1 | 85.6794 | 17.8976 | 0 | 2018-04-29 19:00 | 19 | 1 | 85.9266 | 17.9492 | 0 | 2018-04-29 19:00 | 19 | 1 | 0 | 0 | 0 | 2018-04-29 19:00 | 19 | 1 | 32.6521 | 6.8207 | 0
2018-04-29 20:00 | 20 | 1 | 86.3294 | 18.0333 | 0 | 2018-04-29 20:00 | 20 | 1 | 86.5888 | 18.0875 | 0 | 2018-04-29 20:00 | 20 | 1 | 0 | 0 | 0 | 2018-04-29 20:00 | 20 | 1 | 32.9037 | 6.8733 | 0
2018-04-29 21:00 | 21 | 1 | 86.3569 | 18.0391 | 0 | 2018-04-29 21:00 | 21 | 1 | 86.6728 | 18.1051 | 0 | 2018-04-29 21:00 | 21 | 1 | 0 | 0 | 0 | 2018-04-29 21:00 | 21 | 1 | 32.9357 | 6.8799 | 0
2018-04-29 22:00 | 22 | 1 | 86.4881 | 18.0665 | 0 | 2018-04-29 22:00 | 22 | 1 | 86.8086 | 18.1334 | 0 | 2018-04-29 22:00 | 22 | 1 | 0 | 0 | 0 | 2018-04-29 22:00 | 22 | 1 | 32.9873 | 6.8907 | 0
2018-04-29 23:00 | 23 | 1 | 86.4332 | 18.055 | 0 | 2018-04-29 23:00 | 23 | 1 | 86.7353 | 18.1181 | 0 | 2018-04-29 23:00 | 23 | 1 | 0 | 0 | 0 | 2018-04-29 23:00 | 23 | 1 | 32.9594 | 6.8849 | 0
2018-04-30 | 0 | 2 | 86.4088 | 18.0499 | 0 | 2018-04-30 | 0 | 2 | 86.7002 | 18.1108 | 0 | 2018-04-30 | 0 | 2 | 86.9352 | 18.1599 | 0 | 2018-04-30 | 0 | 2 | 65.9815 | 13.7829 | 0
2018-04-30 01:00 | 1 | 2 | 86.0426 | 17.9734 | 0 | 2018-04-30 01:00 | 1 | 2 | 86.3127 | 18.0299 | 0 | 2018-04-30 01:00 | 1 | 2 | 86.5278 | 18.0748 | 0 | 2018-04-30 01:00 | 1 | 2 | 65.6794 | 13.7198 | 0
2018-04-30 02:00 | 2 | 2 | 86.392 | 18.0464 | 0 | 2018-04-30 02:00 | 2 | 2 | 86.6392 | 18.0981 | 0 | 2018-04-30 02:00 | 2 | 2 | 86.8421 | 18.1404 | 0 | 2018-04-30 02:00 | 2 | 2 | 65.9229 | 13.7706 | 0
2018-04-30 03:00 | 3 | 2 | 86.2776 | 18.0225 | 0 | 2018-04-30 03:00 | 3 | 2 | 86.5766 | 18.085 | 0 | 2018-04-30 03:00 | 3 | 2 | 86.7536 | 18.122 | 0 | 2018-04-30 03:00 | 3 | 2 | 65.8655 | 13.7586 | 0
2018-04-30 04:00 | 4 | 2 | 86.5034 | 18.0697 | 0 | 2018-04-30 04:00 | 4 | 2 | 86.8849 | 18.1494 | 0 | 2018-04-30 04:00 | 4 | 2 | 87.0283 | 18.1793 | 0 | 2018-04-30 04:00 | 4 | 2 | 66.087 | 13.8049 | 0
2018-04-30 05:00 | 5 | 2 | 86.3661 | 18.041 | 0 | 2018-04-30 05:00 | 5 | 2 | 86.772 | 18.1258 | 0 | 2018-04-30 05:00 | 5 | 2 | 87.0054 | 18.1746 | 0 | 2018-04-30 05:00 | 5 | 2 | 66.0354 | 13.7941 | 0
2018-04-30 06:00 | 6 | 2 | 86.2898 | 18.0251 | 0 | 2018-04-30 06:00 | 6 | 2 | 86.6499 | 18.1003 | 0 | 2018-04-30 06:00 | 6 | 2 | 86.8147 | 18.1347 | 0 | 2018-04-30 06:00 | 6 | 2 | 65.9165 | 13.7693 | 0
2018-04-30 07:00 | 7 | 2 | 86.2043 | 18.0072 | 0 | 2018-04-30 07:00 | 7 | 2 | 86.5278 | 18.0748 | 0 | 2018-04-30 07:00 | 7 | 2 | 86.7079 | 18.1124 | 0 | 2018-04-30 07:00 | 7 | 2 | 65.8296 | 13.7511 | 0
2018-04-30 08:00 | 8 | 2 | 86.3355 | 18.0346 | 0 | 2018-04-30 08:00 | 8 | 2 | 86.5461 | 18.0786 | 0 | 2018-04-30 08:00 | 8 | 2 | 86.8025 | 18.1322 | 0 | 2018-04-30 08:00 | 8 | 2 | 65.8725 | 13.7601 | 0
2018-04-30 09:00 | 9 | 2 | 86.3798 | 18.0439 | 0 | 2018-04-30 09:00 | 9 | 2 | 86.7262 | 18.1162 | 0 | 2018-04-30 09:00 | 9 | 2 | 86.8711 | 18.1465 | 0 | 2018-04-30 09:00 | 9 | 2 | 65.967 | 13.7798 | 0
2018-04-30 10:00 | 10 | 2 | 86.2272 | 18.012 | 0 | 2018-04-30 10:00 | 10 | 2 | 86.5156 | 18.0722 | 0 | 2018-04-30 10:00 | 10 | 2 | 86.714 | 18.1137 | 0 | 2018-04-30 10:00 | 10 | 2 | 65.8272 | 13.7507 | 0
2018-04-30 11:00 | 11 | 2 | 86.2119 | 18.0088 | 0 | 2018-04-30 11:00 | 11 | 2 | 86.5141 | 18.0719 | 0 | 2018-04-30 11:00 | 11 | 2 | 86.7201 | 18.115 | 0 | 2018-04-30 11:00 | 11 | 2 | 65.829 | 13.751 | 0
2018-04-30 12:00 | 12 | 2 | 86.389 | 18.0458 | 0 | 2018-04-30 12:00 | 12 | 2 | 86.6835 | 18.1073 | 0 | 2018-04-30 12:00 | 12 | 2 | 86.8574 | 18.1436 | 0 | 2018-04-30 12:00 | 12 | 2 | 65.9455 | 13.7754 | 0
2018-04-30 13:00 | 13 | 2 | 86.4027 | 18.0487 | 0 | 2018-04-30 13:00 | 13 | 2 | 86.6224 | 18.0946 | 0 | 2018-04-30 13:00 | 13 | 2 | 86.7475 | 18.1207 | 0 | 2018-04-30 13:00 | 13 | 2 | 65.8806 | 13.7618 | 0
2018-04-30 14:00 | 14 | 2 | 86.3783 | 18.0436 | 0 | 2018-04-30 14:00 | 14 | 2 | 86.6606 | 18.1025 | 0 | 2018-04-30 14:00 | 14 | 2 | 86.7903 | 18.1296 | 0 | 2018-04-30 14:00 | 14 | 2 | 65.9113 | 13.7682 | 0
2018-04-30 15:00 | 15 | 2 | 86.3355 | 18.0346 | 0 | 2018-04-30 15:00 | 15 | 2 | 86.5248 | 18.0742 | 0 | 2018-04-30 15:00 | 15 | 2 | 86.7384 | 18.1188 | 0 | 2018-04-30 15:00 | 15 | 2 | 65.84 | 13.7533 | 0
2018-04-30 16:00 | 16 | 2 | 86.3493 | 18.0375 | 0 | 2018-04-30 16:00 | 16 | 2 | 86.4912 | 18.0671 | 0 | 2018-04-30 16:00 | 16 | 2 | 86.685 | 18.1076 | 0 | 2018-04-30 16:00 | 16 | 2 | 65.807 | 13.7464 | 0
2018-04-30 17:00 | 17 | 2 | 86.244 | 18.0155 | 0 | 2018-04-30 17:00 | 17 | 2 | 86.4683 | 18.0624 | 0 | 2018-04-30 17:00 | 17 | 2 | 86.6743 | 18.1054 | 0 | 2018-04-30 17:00 | 17 | 2 | 65.7942 | 13.7437 | 0
2018-04-30 18:00 | 18 | 2 | 86.3142 | 18.0302 | 0 | 2018-04-30 18:00 | 18 | 2 | 86.4378 | 18.056 | 0 | 2018-04-30 18:00 | 18 | 2 | 86.5934 | 18.0885 | 0 | 2018-04-30 18:00 | 18 | 2 | 65.7519 | 13.7349 | 0
2018-04-30 19:00 | 19 | 2 | 86.2089 | 18.0082 | 0 | 2018-04-30 19:00 | 19 | 2 | 86.3508 | 18.0378 | 0 | 2018-04-30 19:00 | 19 | 2 | 86.5583 | 18.0812 | 0 | 2018-04-30 19:00 | 19 | 2 | 65.7055 | 13.7252 | 0
2018-04-30 20:00 | 20 | 2 | 86.2181 | 18.0101 | 0 | 2018-04-30 20:00 | 20 | 2 | 86.4836 | 18.0656 | 0 | 2018-04-30 20:00 | 20 | 2 | 86.6896 | 18.1086 | 0 | 2018-04-30 20:00 | 20 | 2 | 65.8058 | 13.7462 | 0
2018-04-30 21:00 | 21 | 2 | 86.1494 | 17.9957 | 0 | 2018-04-30 21:00 | 21 | 2 | 86.4759 | 18.064 | 0 | 2018-04-30 21:00 | 21 | 2 | 86.63 | 18.0961 | 0 | 2018-04-30 21:00 | 21 | 2 | 65.7802 | 13.7408 | 0
2018-04-30 22:00 | 22 | 2 | 86.2593 | 18.0187 | 0 | 2018-04-30 22:00 | 22 | 2 | 86.5522 | 18.0799 | 0 | 2018-04-30 22:00 | 22 | 2 | 86.6468 | 18.0997 | 0 | 2018-04-30 22:00 | 22 | 2 | 65.8156 | 13.7482 | 0
2018-04-30 23:00 | 23 | 2 | 86.4424 | 18.057 | 0 | 2018-04-30 23:00 | 23 | 2 | 86.8055 | 18.1328 | 0 | 2018-04-30 23:00 | 23 | 2 | 86.8864 | 18.1497 | 0 | 2018-04-30 23:00 | 23 | 2 | 66.0029 | 13.7874 | 0
2018-05-01 | 0 | 3 | 86.4637 | 18.0614 | 0 | 2018-05-01 | 0 | 3 | 0 | 0 | 0 | 2018-05-01 | 0 | 3 | 0 | 0 | 0 | 2018-05-01 | 0 | 3 | 0 | 0 | 0
2018-05-01 01:00 | 1 | 3 | 86.5629 | 18.0821 | 0 | 2018-05-01 01:00 | 1 | 3 | 0 | 0 | 0 | 2018-05-01 01:00 | 1 | 3 | 0 | 0 | 0 | 2018-05-01 01:00 | 1 | 3 | 0 | 0 | 0
2018-05-01 02:00 | 2 | 3 | 86.3706 | 18.042 | 0 | 2018-05-01 02:00 | 2 | 3 | 0 | 0 | 0 | 2018-05-01 02:00 | 2 | 3 | 0 | 0 | 0 | 2018-05-01 02:00 | 2 | 3 | 0 | 0 | 0
2018-05-01 03:00 | 3 | 3 | 86.3523 | 18.0381 | 0 | 2018-05-01 03:00 | 3 | 3 | 0 | 0 | 0 | 2018-05-01 03:00 | 3 | 3 | 0 | 0 | 0 | 2018-05-01 03:00 | 3 | 3 | 0 | 0 | 0
2018-05-01 04:00 | 4 | 3 | 86.3676 | 18.0413 | 0 | 2018-05-01 04:00 | 4 | 3 | 0 | 0 | 0 | 2018-05-01 04:00 | 4 | 3 | 0 | 0 | 0 | 2018-05-01 04:00 | 4 | 3 | 0 | 0 | 0
2018-05-01 05:00 | 5 | 3 | 86.4027 | 18.0487 | 0 | 2018-05-01 05:00 | 5 | 3 | 0 | 0 | 0 | 2018-05-01 05:00 | 5 | 3 | 0 | 0 | 0 | 2018-05-01 05:00 | 5 | 3 | 0 | 0 | 0
2018-05-01 06:00 | 6 | 3 | 86.4652 | 18.0617 | 0 | 2018-05-01 06:00 | 6 | 3 | 0 | 0 | 0 | 2018-05-01 06:00 | 6 | 3 | 0 | 0 | 0 | 2018-05-01 06:00 | 6 | 3 | 0 | 0 | 0
2018-05-01 07:00 | 7 | 3 | 86.4012 | 18.0483 | 0 | 2018-05-01 07:00 | 7 | 3 | 0 | 0 | 0 | 2018-05-01 07:00 | 7 | 3 | 0 | 0 | 0 | 2018-05-01 07:00 | 7 | 3 | 0 | 0 | 0
2018-05-01 08:00 | 8 | 3 | 86.4515 | 18.0589 | 0 | 2018-05-01 08:00 | 8 | 3 | 0 | 0 | 0 | 2018-05-01 08:00 | 8 | 3 | 0 | 0 | 0 | 2018-05-01 08:00 | 8 | 3 | 0 | 0 | 0
2018-05-01 09:00 | 9 | 3 | 86.2028 | 18.0069 | 0 | 2018-05-01 09:00 | 9 | 3 | 0 | 0 | 0 | 2018-05-01 09:00 | 9 | 3 | 0 | 0 | 0 | 2018-05-01 09:00 | 9 | 3 | 0 | 0 | 0
2018-05-01 10:00 | 10 | 3 | 86.2715 | 18.0213 | 0 | 2018-05-01 10:00 | 10 | 3 | 0 | 0 | 0 | 2018-05-01 10:00 | 10 | 3 | 0 | 0 | 0 | 2018-05-01 10:00 | 10 | 3 | 0 | 0 | 0
2018-05-01 11:00 | 11 | 3 | 86.7567 | 18.1226 | 0 | 2018-05-01 11:00 | 11 | 3 | 0 | 0 | 0 | 2018-05-01 11:00 | 11 | 3 | 0 | 0 | 0 | 2018-05-01 11:00 | 11 | 3 | 0 | 0 | 0
2018-05-01 12:00 | 12 | 3 | 86.6194 | 18.0939 | 0 | 2018-05-01 12:00 | 12 | 3 | 0 | 0 | 0 | 2018-05-01 12:00 | 12 | 3 | 0 | 0 | 0 | 2018-05-01 12:00 | 12 | 3 | 0 | 0 | 0
2018-05-01 13:00 | 13 | 3 | 86.6377 | 18.0977 | 0 | 2018-05-01 13:00 | 13 | 3 | 0 | 0 | 0 | 2018-05-01 13:00 | 13 | 3 | 0 | 0 | 0 | 2018-05-01 13:00 | 13 | 3 | 0 | 0 | 0
2018-05-01 14:00 | 14 | 3 | 86.8757 | 18.1475 | 0 | 2018-05-01 14:00 | 14 | 3 | 0 | 0 | 0 | 2018-05-01 14:00 | 14 | 3 | 0 | 0 | 0 | 2018-05-01 14:00 | 14 | 3 | 0 | 0 | 0
2018-05-01 15:00 | 15 | 3 | 86.7994 | 18.1315 | 0 | 2018-05-01 15:00 | 15 | 3 | 0 | 0 | 0 | 2018-05-01 15:00 | 15 | 3 | 0 | 0 | 0 | 2018-05-01 15:00 | 15 | 3 | 0 | 0 | 0
2018-05-01 16:00 | 16 | 3 | 86.7674 | 18.1248 | 0 | 2018-05-01 16:00 | 16 | 3 | 0 | 0 | 0 | 2018-05-01 16:00 | 16 | 3 | 0 | 0 | 0 | 2018-05-01 16:00 | 16 | 3 | 0 | 0 | 0
2018-05-01 17:00 | 17 | 3 | 86.7384 | 18.1188 | 0 | 2018-05-01 17:00 | 17 | 3 | 0 | 0 | 0 | 2018-05-01 17:00 | 17 | 3 | 0 | 0 | 0 | 2018-05-01 17:00 | 17 | 3 | 0 | 0 | 0
2018-05-01 18:00 | 18 | 3 | 86.7124 | 18.1134 | 0 | 2018-05-01 18:00 | 18 | 3 | 0 | 0 | 0 | 2018-05-01 18:00 | 18 | 3 | 0 | 0 | 0 | 2018-05-01 18:00 | 18 | 3 | 0 | 0 | 0
2018-05-01 19:00 | 19 | 3 | 86.8376 | 18.1395 | 0 | 2018-05-01 19:00 | 19 | 3 | 0 | 0 | 0 | 2018-05-01 19:00 | 19 | 3 | 0 | 0 | 0 | 2018-05-01 19:00 | 19 | 3 | 0 | 0 | 0
2018-05-01 20:00 | 20 | 3 | 86.627 | 18.0955 | 0 | 2018-05-01 20:00 | 20 | 3 | 0 | 0 | 0 | 2018-05-01 20:00 | 20 | 3 | 0 | 0 | 0 | 2018-05-01 20:00 | 20 | 3 | 0 | 0 | 0
2018-05-01 21:00 | 21 | 3 | 86.6239 | 18.0949 | 0 | 2018-05-01 21:00 | 21 | 3 | 0 | 0 | 0 | 2018-05-01 21:00 | 21 | 3 | 0 | 0 | 0 | 2018-05-01 21:00 | 21 | 3 | 0 | 0 | 0
2018-05-01 22:00 | 22 | 3 | 86.714 | 18.1137 | 0 | 2018-05-01 22:00 | 22 | 3 | 0 | 0 | 0 | 2018-05-01 22:00 | 22 | 3 | 0 | 0 | 0 | 2018-05-01 22:00 | 22 | 3 | 0 | 0 | 0
2018-05-01 23:00 | 23 | 3 | 86.8971 | 18.1519 | 0 | 2018-05-01 23:00 | 23 | 3 | 0 | 0 | 0 | 2018-05-01 23:00 | 23 | 3 | 0 | 0 | 0 | 2018-05-01 23:00 | 23 | 3 | 0 | 0 | 0
2018-05-02 | 0 | 4 | 0 | 0 | 0 | 2018-05-02 | 0 | 4 | 0 | 0 | 0 | 2018-05-02 | 0 | 4 | 86.6712 | 18.1047 | 0 | 2018-05-02 | 0 | 4 | 32.9351 | 6.8798 | 0
2018-05-02 01:00 | 1 | 4 | 0 | 0 | 0 | 2018-05-02 01:00 | 1 | 4 | 0 | 0 | 0 | 2018-05-02 01:00 | 1 | 4 | 86.511 | 18.0713 | 0 | 2018-05-02 01:00 | 1 | 4 | 32.8742 | 6.8671 | 0
2018-05-02 02:00 | 2 | 4 | 0 | 0 | 0 | 2018-05-02 02:00 | 2 | 4 | 0 | 0 | 0 | 2018-05-02 02:00 | 2 | 4 | 86.7628 | 18.1239 | 0 | 2018-05-02 02:00 | 2 | 4 | 32.9699 | 6.8871 | 0
2018-05-02 03:00 | 3 | 4 | 0 | 0 | 0 | 2018-05-02 03:00 | 3 | 4 | 0 | 0 | 0 | 2018-05-02 03:00 | 3 | 4 | 86.7384 | 18.1188 | 0 | 2018-05-02 03:00 | 3 | 4 | 32.9606 | 6.8851 | 0
2018-05-02 04:00 | 4 | 4 | 0 | 0 | 0 | 2018-05-02 04:00 | 4 | 4 | 0 | 0 | 0 | 2018-05-02 04:00 | 4 | 4 | 86.8376 | 18.1395 | 0 | 2018-05-02 04:00 | 4 | 4 | 32.9983 | 6.893 | 0
2018-05-02 05:00 | 5 | 4 | 0 | 0 | 0 | 2018-05-02 05:00 | 5 | 4 | 0 | 0 | 0 | 2018-05-02 05:00 | 5 | 4 | 87.0222 | 18.1781 | 0 | 2018-05-02 05:00 | 5 | 4 | 33.0684 | 6.9077 | 0
2018-05-02 06:00 | 6 | 4 | 0 | 0 | 0 | 2018-05-02 06:00 | 6 | 4 | 0 | 0 | 0 | 2018-05-02 06:00 | 6 | 4 | 86.9627 | 18.1656 | 0 | 2018-05-02 06:00 | 6 | 4 | 33.0458 | 6.9029 | 0
2018-05-02 07:00 | 7 | 4 | 0 | 0 | 0 | 2018-05-02 07:00 | 7 | 4 | 0 | 0 | 0 | 2018-05-02 07:00 | 7 | 4 | 87.1321 | 18.201 | 0 | 2018-05-02 07:00 | 7 | 4 | 33.1102 | 6.9164 | 0
2018-05-02 08:00 | 8 | 4 | 0 | 0 | 0 | 2018-05-02 08:00 | 8 | 4 | 0 | 0 | 0 | 2018-05-02 08:00 | 8 | 4 | 87.1931 | 18.2138 | 0 | 2018-05-02 08:00 | 8 | 4 | 33.1334 | 6.9212 | 0
2018-05-02 09:00 | 9 | 4 | 0 | 0 | 0 | 2018-05-02 09:00 | 9 | 4 | 0 | 0 | 0 | 2018-05-02 09:00 | 9 | 4 | 86.7155 | 18.114 | 0 | 2018-05-02 09:00 | 9 | 4 | 32.9519 | 6.8833 | 0
2018-05-02 10:00 | 10 | 4 | 0 | 0 | 0 | 2018-05-02 10:00 | 10 | 4 | 0 | 0 | 0 | 2018-05-02 10:00 | 10 | 4 | 86.6743 | 18.1054 | 0 | 2018-05-02 10:00 | 10 | 4 | 32.9362 | 6.88 | 0
2018-05-02 11:00 | 11 | 4 | 0 | 0 | 0 | 2018-05-02 11:00 | 11 | 4 | 0 | 0 | 0 | 2018-05-02 11:00 | 11 | 4 | 86.8956 | 18.1516 | 0 | 2018-05-02 11:00 | 11 | 4 | 33.0203 | 6.8976 | 0
2018-05-02 12:00 | 12 | 4 | 0 | 0 | 0 | 2018-05-02 12:00 | 12 | 4 | 0 | 0 | 0 | 2018-05-02 12:00 | 12 | 4 | 86.9276 | 18.1583 | 0 | 2018-05-02 12:00 | 12 | 4 | 33.0325 | 6.9002 | 0
2018-05-02 13:00 | 13 | 4 | 0 | 0 | 0 | 2018-05-02 13:00 | 13 | 4 | 0 | 0 | 0 | 2018-05-02 13:00 | 13 | 4 | 87.2541 | 18.2265 | 0 | 2018-05-02 13:00 | 13 | 4 | 33.1566 | 6.9261 | 0
2018-05-02 14:00 | 14 | 4 | 0 | 0 | 0 | 2018-05-02 14:00 | 14 | 4 | 0 | 0 | 0 | 2018-05-02 14:00 | 14 | 4 | 87.4037 | 18.2578 | 0 | 2018-05-02 14:00 | 14 | 4 | 33.2134 | 6.9379 | 0
2018-05-02 15:00 | 15 | 4 | 0 | 0 | 0 | 2018-05-02 15:00 | 15 | 4 | 0 | 0 | 0 | 2018-05-02 15:00 | 15 | 4 | 87.2129 | 18.2179 | 0 | 2018-05-02 15:00 | 15 | 4 | 33.1409 | 6.9228 | 0
2018-05-02 16:00 | 16 | 4 | 0 | 0 | 0 | 2018-05-02 16:00 | 16 | 4 | 0 | 0 | 0 | 2018-05-02 16:00 | 16 | 4 | 86.9718 | 18.1675 | 0 | 2018-05-02 16:00 | 16 | 4 | 33.0493 | 6.9037 | 0
2018-05-02 17:00 | 17 | 4 | 0 | 0 | 0 | 2018-05-02 17:00 | 17 | 4 | 0 | 0 | 0 | 2018-05-02 17:00 | 17 | 4 | 87.1397 | 18.2026 | 0 | 2018-05-02 17:00 | 17 | 4 | 33.1131 | 6.917 | 0
2018-05-02 18:00 | 18 | 4 | 0 | 0 | 0 | 2018-05-02 18:00 | 18 | 4 | 0 | 0 | 0 | 2018-05-02 18:00 | 18 | 4 | 87.2435 | 18.2243 | 0 | 2018-05-02 18:00 | 18 | 4 | 33.1525 | 6.9252 | 0
2018-05-02 19:00 | 19 | 4 | 0 | 0 | 0 | 2018-05-02 19:00 | 19 | 4 | 0 | 0 | 0 | 2018-05-02 19:00 | 19 | 4 | 86.8894 | 18.1503 | 0 | 2018-05-02 19:00 | 19 | 4 | 33.018 | 6.8971 | 0
2018-05-02 20:00 | 20 | 4 | 0 | 0 | 0 | 2018-05-02 20:00 | 20 | 4 | 0 | 0 | 0 | 2018-05-02 20:00 | 20 | 4 | 87.1839 | 18.2118 | 0 | 2018-05-02 20:00 | 20 | 4 | 33.1299 | 6.9205 | 0
2018-05-02 21:00 | 21 | 4 | 0 | 0 | 0 | 2018-05-02 21:00 | 21 | 4 | 0 | 0 | 0 | 2018-05-02 21:00 | 21 | 4 | 87.2419 | 18.224 | 0 | 2018-05-02 21:00 | 21 | 4 | 33.1519 | 6.9251 | 0
2018-05-02 22:00 | 22 | 4 | 0 | 0 | 0 | 2018-05-02 22:00 | 22 | 4 | 0 | 0 | 0 | 2018-05-02 22:00 | 22 | 4 | 87.1733 | 18.2096 | 0 | 2018-05-02 22:00 | 22 | 4 | 33.1259 | 6.9197 | 0
2018-05-02 23:00 | 23 | 4 | 0 | 0 | 0 | 2018-05-02 23:00 | 23 | 4 | 0 | 0 | 0 | 2018-05-02 23:00 | 23 | 4 | 87.2557 | 18.2268 | 0 | 2018-05-02 23:00 | 23 | 4 | 33.1572 | 6.9262 | 0
2018-05-03 | 0 | 5 | 86.5492 | 18.0793 | 0 | 2018-05-03 | 0 | 5 | 0 | 0 | 0 | 2018-05-03 | 0 | 5 | 0 | 0 | 0 | 2018-05-03 | 0 | 5 | 0 | 0 | 0
2018-05-03 01:00 | 1 | 5 | 86.7201 | 18.115 | 0 | 2018-05-03 01:00 | 1 | 5 | 0 | 0 | 0 | 2018-05-03 01:00 | 1 | 5 | 0 | 0 | 0 | 2018-05-03 01:00 | 1 | 5 | 0 | 0 | 0
2018-05-03 02:00 | 2 | 5 | 86.5095 | 18.071 | 0 | 2018-05-03 02:00 | 2 | 5 | 0 | 0 | 0 | 2018-05-03 02:00 | 2 | 5 | 0 | 0 | 0 | 2018-05-03 02:00 | 2 | 5 | 0 | 0 | 0
2018-05-03 03:00 | 3 | 5 | 86.4576 | 18.0601 | 0 | 2018-05-03 03:00 | 3 | 5 | 0 | 0 | 0 | 2018-05-03 03:00 | 3 | 5 | 0 | 0 | 0 | 2018-05-03 03:00 | 3 | 5 | 0 | 0 | 0
2018-05-03 04:00 | 4 | 5 | 86.6316 | 18.0965 | 0 | 2018-05-03 04:00 | 4 | 5 | 0 | 0 | 0 | 2018-05-03 04:00 | 4 | 5 | 0 | 0 | 0 | 2018-05-03 04:00 | 4 | 5 | 0 | 0 | 0
2018-05-03 05:00 | 5 | 5 | 86.569 | 18.0834 | 0 | 2018-05-03 05:00 | 5 | 5 | 0 | 0 | 0 | 2018-05-03 05:00 | 5 | 5 | 0 | 0 | 0 | 2018-05-03 05:00 | 5 | 5 | 0 | 0 | 0
2018-05-03 06:00 | 6 | 5 | 86.6468 | 18.0997 | 0 | 2018-05-03 06:00 | 6 | 5 | 0 | 0 | 0 | 2018-05-03 06:00 | 6 | 5 | 0 | 0 | 0 | 2018-05-03 06:00 | 6 | 5 | 0 | 0 | 0
2018-05-03 07:00 | 7 | 5 | 86.6361 | 18.0974 | 0 | 2018-05-03 07:00 | 7 | 5 | 0 | 0 | 0 | 2018-05-03 07:00 | 7 | 5 | 0 | 0 | 0 | 2018-05-03 07:00 | 7 | 5 | 0 | 0 | 0
2018-05-03 08:00 | 8 | 5 | 86.6819 | 18.107 | 0 | 2018-05-03 08:00 | 8 | 5 | 0 | 0 | 0 | 2018-05-03 08:00 | 8 | 5 | 0 | 0 | 0 | 2018-05-03 08:00 | 8 | 5 | 0 | 0 | 0
2018-05-03 09:00 | 9 | 5 | 86.7094 | 18.1127 | 0 | 2018-05-03 09:00 | 9 | 5 | 0 | 0 | 0 | 2018-05-03 09:00 | 9 | 5 | 0 | 0 | 0 | 2018-05-03 09:00 | 9 | 5 | 0 | 0 | 0
2018-05-03 10:00 | 10 | 5 | 86.7933 | 18.1303 | 0 | 2018-05-03 10:00 | 10 | 5 | 0 | 0 | 0 | 2018-05-03 10:00 | 10 | 5 | 0 | 0 | 0 | 2018-05-03 10:00 | 10 | 5 | 0 | 0 | 0
2018-05-03 11:00 | 11 | 5 | 86.8009 | 18.1318 | 0 | 2018-05-03 11:00 | 11 | 5 | 0 | 0 | 0 | 2018-05-03 11:00 | 11 | 5 | 0 | 0 | 0 | 2018-05-03 11:00 | 11 | 5 | 0 | 0 | 0
2018-05-03 12:00 | 12 | 5 | 86.6728 | 18.1051 | 0 | 2018-05-03 12:00 | 12 | 5 | 0 | 0 | 0 | 2018-05-03 12:00 | 12 | 5 | 0 | 0 | 0 | 2018-05-03 12:00 | 12 | 5 | 0 | 0 | 0
2018-05-03 13:00 | 13 | 5 | 86.6316 | 18.0965 | 0 | 2018-05-03 13:00 | 13 | 5 | 0 | 0 | 0 | 2018-05-03 13:00 | 13 | 5 | 0 | 0 | 0 | 2018-05-03 13:00 | 13 | 5 | 0 | 0 | 0
2018-05-03 14:00 | 14 | 5 | 86.6316 | 18.0965 | 0 | 2018-05-03 14:00 | 14 | 5 | 0 | 0 | 0 | 2018-05-03 14:00 | 14 | 5 | 0 | 0 | 0 | 2018-05-03 14:00 | 14 | 5 | 0 | 0 | 0
2018-05-03 15:00 | 15 | 5 | 86.6636 | 18.1032 | 0 | 2018-05-03 15:00 | 15 | 5 | 0 | 0 | 0 | 2018-05-03 15:00 | 15 | 5 | 0 | 0 | 0 | 2018-05-03 15:00 | 15 | 5 | 0 | 0 | 0
2018-05-03 16:00 | 16 | 5 | 86.5568 | 18.0808 | 0 | 2018-05-03 16:00 | 16 | 5 | 0 | 0 | 0 | 2018-05-03 16:00 | 16 | 5 | 0 | 0 | 0 | 2018-05-03 16:00 | 16 | 5 | 0 | 0 | 0
2018-05-03 17:00 | 17 | 5 | 86.6865 | 18.1079 | 0 | 2018-05-03 17:00 | 17 | 5 | 0 | 0 | 0 | 2018-05-03 17:00 | 17 | 5 | 0 | 0 | 0 | 2018-05-03 17:00 | 17 | 5 | 0 | 0 | 0
2018-05-03 18:00 | 18 | 5 | 86.7262 | 18.1162 | 0 | 2018-05-03 18:00 | 18 | 5 | 0 | 0 | 0 | 2018-05-03 18:00 | 18 | 5 | 0 | 0 | 0 | 2018-05-03 18:00 | 18 | 5 | 0 | 0 | 0
2018-05-03 19:00 | 19 | 5 | 86.5187 | 18.0729 | 0 | 2018-05-03 19:00 | 19 | 5 | 0 | 0 | 0 | 2018-05-03 19:00 | 19 | 5 | 0 | 0 | 0 | 2018-05-03 19:00 | 19 | 5 | 0 | 0 | 0
2018-05-03 20:00 | 20 | 5 | 86.5766 | 18.085 | 0 | 2018-05-03 20:00 | 20 | 5 | 0 | 0 | 0 | 2018-05-03 20:00 | 20 | 5 | 0 | 0 | 0 | 2018-05-03 20:00 | 20 | 5 | 0 | 0 | 0
2018-05-03 21:00 | 21 | 5 | 86.6194 | 18.0939 | 0 | 2018-05-03 21:00 | 21 | 5 | 0 | 0 | 0 | 2018-05-03 21:00 | 21 | 5 | 0 | 0 | 0 | 2018-05-03 21:00 | 21 | 5 | 0 | 0 | 0
2018-05-03 22:00 | 22 | 5 | 86.6743 | 18.1054 | 0 | 2018-05-03 22:00 | 22 | 5 | 0 | 0 | 0 | 2018-05-03 22:00 | 22 | 5 | 0 | 0 | 0 | 2018-05-03 22:00 | 22 | 5 | 0 | 0 | 0
2018-05-03 23:00 | 23 | 5 | 86.5644 | 18.0824 | 0 | 2018-05-03 23:00 | 23 | 5 | 0 | 0 | 0 | 2018-05-03 23:00 | 23 | 5 | 0 | 0 | 0 | 2018-05-03 23:00 | 23 | 5 | 0 | 0 | 0
2018-05-04 | 0 | 6 | 86.2226 | 18.011 | 0 | 2018-05-04 | 0 | 6 | 86.688 | 18.1083 | 0 | 2018-05-04 | 0 | 6 | 0 | 0 | 0 | 2018-05-04 | 0 | 6 | 32.9414 | 6.8811 | 0
2018-05-04 01:00 | 1 | 6 | 86.1128 | 17.9881 | 0 | 2018-05-04 01:00 | 1 | 6 | 86.5232 | 18.0738 | 0 | 2018-05-04 01:00 | 1 | 6 | 0 | 0 | 0 | 2018-05-04 01:00 | 1 | 6 | 32.8788 | 6.8681 | 0
2018-05-04 02:00 | 2 | 6 | 86.2791 | 18.0228 | 0 | 2018-05-04 02:00 | 2 | 6 | 86.6896 | 18.1086 | 0 | 2018-05-04 02:00 | 2 | 6 | 0 | 0 | 0 | 2018-05-04 02:00 | 2 | 6 | 32.942 | 6.8813 | 0
2018-05-04 03:00 | 3 | 6 | 86.0014 | 17.9648 | 0 | 2018-05-04 03:00 | 3 | 6 | 86.4485 | 18.0582 | 0 | 2018-05-04 03:00 | 3 | 6 | 0 | 0 | 0 | 2018-05-04 03:00 | 3 | 6 | 32.8504 | 6.8621 | 0
2018-05-04 04:00 | 4 | 6 | 86.0533 | 17.9757 | 0 | 2018-05-04 04:00 | 4 | 6 | 86.4347 | 18.0553 | 0 | 2018-05-04 04:00 | 4 | 6 | 0 | 0 | 0 | 2018-05-04 04:00 | 4 | 6 | 32.8452 | 6.861 | 0
2018-05-04 05:00 | 5 | 6 | 86.2257 | 18.0117 | 0 | 2018-05-04 05:00 | 5 | 6 | 86.6117 | 18.0923 | 0 | 2018-05-04 05:00 | 5 | 6 | 0 | 0 | 0 | 2018-05-04 05:00 | 5 | 6 | 32.9124 | 6.8751 | 0
2018-05-04 06:00 | 6 | 6 | 86.4332 | 18.055 | 0 | 2018-05-04 06:00 | 6 | 6 | 86.9352 | 18.1599 | 0 | 2018-05-04 06:00 | 6 | 6 | 0 | 0 | 0 | 2018-05-04 06:00 | 6 | 6 | 33.0354 | 6.9008 | 0
2018-05-04 07:00 | 7 | 6 | 86.5873 | 18.0872 | 0 | 2018-05-04 07:00 | 7 | 6 | 87.0619 | 18.1864 | 0 | 2018-05-04 07:00 | 7 | 6 | 0 | 0 | 0 | 2018-05-04 07:00 | 7 | 6 | 33.0835 | 6.9108 | 0
2018-05-04 08:00 | 8 | 6 | 86.3691 | 18.0416 | 0 | 2018-05-04 08:00 | 8 | 6 | 86.7811 | 18.1277 | 0 | 2018-05-04 08:00 | 8 | 6 | 0 | 0 | 0 | 2018-05-04 08:00 | 8 | 6 | 32.9768 | 6.8885 | 0
2018-05-04 09:00 | 9 | 6 | 86.334 | 18.0343 | 0 | 2018-05-04 09:00 | 9 | 6 | 86.7399 | 18.1191 | 0 | 2018-05-04 09:00 | 9 | 6 | 0 | 0 | 0 | 2018-05-04 09:00 | 9 | 6 | 32.9612 | 6.8853 | 0
2018-05-04 10:00 | 10 | 6 | 86.5126 | 18.0716 | 0 | 2018-05-04 10:00 | 10 | 6 | 86.862 | 18.1446 | 0 | 2018-05-04 10:00 | 10 | 6 | 0 | 0 | 0 | 2018-05-04 10:00 | 10 | 6 | 33.0076 | 6.8949 | 0
2018-05-04 11:00 | 11 | 6 | 86.5003 | 18.069 | 0 | 2018-05-04 11:00 | 11 | 6 | 86.9306 | 18.1589 | 0 | 2018-05-04 11:00 | 11 | 6 | 0 | 0 | 0 | 2018-05-04 11:00 | 11 | 6 | 33.0336 | 6.9004 | 0
2018-05-04 12:00 | 12 | 6 | 86.7002 | 18.1108 | 0 | 2018-05-04 12:00 | 12 | 6 | 87.1412 | 18.2029 | 0 | 2018-05-04 12:00 | 12 | 6 | 0 | 0 | 0 | 2018-05-04 12:00 | 12 | 6 | 33.1137 | 6.9171 | 0
2018-05-04 13:00 | 13 | 6 | 86.363 | 18.0404 | 0 | 2018-05-04 13:00 | 13 | 6 | 86.8009 | 18.1318 | 0 | 2018-05-04 13:00 | 13 | 6 | 0 | 0 | 0 | 2018-05-04 13:00 | 13 | 6 | 32.9843 | 6.8901 | 0
2018-05-04 14:00 | 14 | 6 | 86.4408 | 18.0566 | 0 | 2018-05-04 14:00 | 14 | 6 | 86.8635 | 18.1449 | 0 | 2018-05-04 14:00 | 14 | 6 | 0 | 0 | 0 | 2018-05-04 14:00 | 14 | 6 | 33.0081 | 6.8951 | 0
2018-05-04 15:00 | 15 | 6 | 86.2943 | 18.026 | 0 | 2018-05-04 15:00 | 15 | 6 | 86.6743 | 18.1054 | 0 | 2018-05-04 15:00 | 15 | 6 | 0 | 0 | 0 | 2018-05-04 15:00 | 15 | 6 | 32.9362 | 6.88 | 0
2018-05-04 16:00 | 16 | 6 | 86.3706 | 18.042 | 0 | 2018-05-04 16:00 | 16 | 6 | 86.7491 | 18.121 | 0 | 2018-05-04 16:00 | 16 | 6 | 0 | 0 | 0 | 2018-05-04 16:00 | 16 | 6 | 32.9647 | 6.886 | 0
2018-05-04 17:00 | 17 | 6 | 86.2882 | 18.0247 | 0 | 2018-05-04 17:00 | 17 | 6 | 86.7445 | 18.1201 | 0 | 2018-05-04 17:00 | 17 | 6 | 0 | 0 | 0 | 2018-05-04 17:00 | 17 | 6 | 32.9629 | 6.8856 | 0
2018-05-04 18:00 | 18 | 6 | 86.1875 | 18.0037 | 0 | 2018-05-04 18:00 | 18 | 6 | 86.6667 | 18.1038 | 0 | 2018-05-04 18:00 | 18 | 6 | 0 | 0 | 0 | 2018-05-04 18:00 | 18 | 6 | 32.9333 | 6.8794 | 0
2018-05-04 19:00 | 19 | 6 | 86.099 | 17.9852 | 0 | 2018-05-04 19:00 | 19 | 6 | 86.5431 | 18.078 | 0 | 2018-05-04 19:00 | 19 | 6 | 0 | 0 | 0 | 2018-05-04 19:00 | 19 | 6 | 32.8864 | 6.8696 | 0
2018-05-04 20:00 | 20 | 6 | 86.1997 | 18.0063 | 0 | 2018-05-04 20:00 | 20 | 6 | 86.5187 | 18.0729 | 0 | 2018-05-04 20:00 | 20 | 6 | 0 | 0 | 0 | 2018-05-04 20:00 | 20 | 6 | 32.8771 | 6.8677 | 0
2018-05-04 21:00 | 21 | 6 | 86.3767 | 18.0432 | 0 | 2018-05-04 21:00 | 21 | 6 | 86.7247 | 18.1159 | 0 | 2018-05-04 21:00 | 21 | 6 | 0 | 0 | 0 | 2018-05-04 21:00 | 21 | 6 | 32.9554 | 6.8841 | 0
2018-05-04 22:00 | 22 | 6 | 86.3691 | 18.0416 | 0 | 2018-05-04 22:00 | 22 | 6 | 86.7659 | 18.1245 | 0 | 2018-05-04 22:00 | 22 | 6 | 0 | 0 | 0 | 2018-05-04 22:00 | 22 | 6 | 32.971 | 6.8873 | 0
2018-05-04 23:00 | 23 | 6 | 86.4012 | 18.0483 | 0 | 2018-05-04 23:00 | 23 | 6 | 86.7918 | 18.1299 | 0 | 2018-05-04 23:00 | 23 | 6 | 0 | 0 | 0 | 2018-05-04 23:00 | 23 | 6 | 32.9809 | 6.8894 | 0
2018-05-05 | 0 | 7 | 86.0121 | 17.9671 | 0 | 2018-05-05 | 0 | 7 | 0 | 0 | 0 | 2018-05-05 | 0 | 7 | 86.5507 | 18.0796 | 0 | 2018-05-05 | 0 | 7 | 32.8893 | 6.8702 | 0
2018-05-05 01:00 | 1 | 7 | 85.919 | 17.9476 | 0 | 2018-05-05 01:00 | 1 | 7 | 0 | 0 | 0 | 2018-05-05 01:00 | 1 | 7 | 86.5324 | 18.0758 | 0 | 2018-05-05 01:00 | 1 | 7 | 32.8823 | 6.8688 | 0
2018-05-05 02:00 | 2 | 7 | 86.0533 | 17.9757 | 0 | 2018-05-05 02:00 | 2 | 7 | 0 | 0 | 0 | 2018-05-05 02:00 | 2 | 7 | 86.6453 | 18.0993 | 0 | 2018-05-05 02:00 | 2 | 7 | 32.9252 | 6.8777 | 0
2018-05-05 03:00 | 3 | 7 | 86.1677 | 17.9996 | 0 | 2018-05-05 03:00 | 3 | 7 | 0 | 0 | 0 | 2018-05-05 03:00 | 3 | 7 | 86.7002 | 18.1108 | 0 | 2018-05-05 03:00 | 3 | 7 | 32.9461 | 6.8821 | 0
2018-05-05 04:00 | 4 | 7 | 86.3081 | 18.0289 | 0 | 2018-05-05 04:00 | 4 | 7 | 0 | 0 | 0 | 2018-05-05 04:00 | 4 | 7 | 86.8513 | 18.1424 | 0 | 2018-05-05 04:00 | 4 | 7 | 33.0035 | 6.8941 | 0
2018-05-05 05:00 | 5 | 7 | 86.2562 | 18.0181 | 0 | 2018-05-05 05:00 | 5 | 7 | 0 | 0 | 0 | 2018-05-05 05:00 | 5 | 7 | 86.8605 | 18.1443 | 0 | 2018-05-05 05:00 | 5 | 7 | 33.007 | 6.8948 | 0
2018-05-05 06:00 | 6 | 7 | 86.1234 | 17.9903 | 0 | 2018-05-05 06:00 | 6 | 7 | 0 | 0 | 0 | 2018-05-05 06:00 | 6 | 7 | 86.6682 | 18.1041 | 0 | 2018-05-05 06:00 | 6 | 7 | 32.9339 | 6.8796 | 0
2018-05-05 07:00 | 7 | 7 | 86.1906 | 18.0044 | 0 | 2018-05-05 07:00 | 7 | 7 | 0 | 0 | 0 | 2018-05-05 07:00 | 7 | 7 | 86.7247 | 18.1159 | 0 | 2018-05-05 07:00 | 7 | 7 | 32.9554 | 6.8841 | 0
2018-05-05 08:00 | 8 | 7 | 86.36 | 18.0397 | 0 | 2018-05-05 08:00 | 8 | 7 | 0 | 0 | 0 | 2018-05-05 08:00 | 8 | 7 | 86.952 | 18.1634 | 0 | 2018-05-05 08:00 | 8 | 7 | 33.0418 | 6.9021 | 0
2018-05-05 09:00 | 9 | 7 | 86.4912 | 18.0671 | 0 | 2018-05-05 09:00 | 9 | 7 | 0 | 0 | 0 | 2018-05-05 09:00 | 9 | 7 | 87.0588 | 18.1857 | 0 | 2018-05-05 09:00 | 9 | 7 | 33.0823 | 6.9106 | 0
2018-05-05 10:00 | 10 | 7 | 86.1982 | 18.0059 | 0 | 2018-05-05 10:00 | 10 | 7 | 0 | 0 | 0 | 2018-05-05 10:00 | 10 | 7 | 86.6392 | 18.0981 | 0 | 2018-05-05 10:00 | 10 | 7 | 32.9229 | 6.8773 | 0
2018-05-05 11:00 | 11 | 7 | 86.1707 | 18.0002 | 0 | 2018-05-05 11:00 | 11 | 7 | 0 | 0 | 0 | 2018-05-05 11:00 | 11 | 7 | 86.8849 | 18.1494 | 0 | 2018-05-05 11:00 | 11 | 7 | 33.0163 | 6.8968 | 0
2018-05-05 12:00 | 12 | 7 | 86.5019 | 18.0694 | 0 | 2018-05-05 12:00 | 12 | 7 | 0 | 0 | 0 | 2018-05-05 12:00 | 12 | 7 | 87.1504 | 18.2048 | 0 | 2018-05-05 12:00 | 12 | 7 | 33.1172 | 6.9178 | 0
2018-05-05 13:00 | 13 | 7 | 86.6148 | 18.093 | 0 | 2018-05-05 13:00 | 13 | 7 | 0 | 0 | 0 | 2018-05-05 13:00 | 13 | 7 | 87.3167 | 18.2396 | 0 | 2018-05-05 13:00 | 13 | 7 | 33.1803 | 6.931 | 0
2018-05-05 14:00 | 14 | 7 | 86.4439 | 18.0573 | 0 | 2018-05-05 14:00 | 14 | 7 | 0 | 0 | 0 | 2018-05-05 14:00 | 14 | 7 | 87.0832 | 18.1908 | 0 | 2018-05-05 14:00 | 14 | 7 | 33.0916 | 6.9125 | 0
2018-05-05 15:00 | 15 | 7 | 86.5522 | 18.0799 | 0 | 2018-05-05 15:00 | 15 | 7 | 0 | 0 | 0 | 2018-05-05 15:00 | 15 | 7 | 87.2938 | 18.2348 | 0 | 2018-05-05 15:00 | 15 | 7 | 33.1716 | 6.9292 | 0
2018-05-05 16:00 | 16 | 7 | 86.5644 | 18.0824 | 0 | 2018-05-05 16:00 | 16 | 7 | 0 | 0 | 0 | 2018-05-05 16:00 | 16 | 7 | 87.3579 | 18.2482 | 0 | 2018-05-05 16:00 | 16 | 7 | 33.196 | 6.9343 | 0
2018-05-05 17:00 | 17 | 7 | 86.7445 | 18.1201 | 0 | 2018-05-05 17:00 | 17 | 7 | 0 | 0 | 0 | 2018-05-05 17:00 | 17 | 7 | 87.57 | 18.2925 | 0 | 2018-05-05 17:00 | 17 | 7 | 33.2766 | 6.9511 | 0
2018-05-05 18:00 | 18 | 7 | 86.4668 | 18.062 | 0 | 2018-05-05 18:00 | 18 | 7 | 0 | 0 | 0 | 2018-05-05 18:00 | 18 | 7 | 87.3014 | 18.2364 | 0 | 2018-05-05 18:00 | 18 | 7 | 33.1745 | 6.9298 | 0
2018-05-05 19:00 | 19 | 7 | 86.3661 | 18.041 | 0 | 2018-05-05 19:00 | 19 | 7 | 0 | 0 | 0 | 2018-05-05 19:00 | 19 | 7 | 87.0954 | 18.1934 | 0 | 2018-05-05 19:00 | 19 | 7 | 33.0963 | 6.9135 | 0
2018-05-05 20:00 | 20 | 7 | 86.1173 | 17.989 | 0 | 2018-05-05 20:00 | 20 | 7 | 0 | 0 | 0 | 2018-05-05 20:00 | 20 | 7 | 86.891 | 18.1507 | 0 | 2018-05-05 20:00 | 20 | 7 | 33.0186 | 6.8973 | 0
2018-05-05 21:00 | 21 | 7 | 86.1555 | 17.997 | 0 | 2018-05-05 21:00 | 21 | 7 | 0 | 0 | 0 | 2018-05-05 21:00 | 21 | 7 | 86.9245 | 18.1577 | 0 | 2018-05-05 21:00 | 21 | 7 | 33.0313 | 6.8999 | 0
2018-05-05 22:00 | 22 | 7 | 86.2211 | 18.0107 | 0 | 2018-05-05 22:00 | 22 | 7 | 0 | 0 | 0 | 2018-05-05 22:00 | 22 | 7 | 87.0054 | 18.1746 | 0 | 2018-05-05 22:00 | 22 | 7 | 33.0621 | 6.9063 | 0
2018-05-05 23:00 | 23 | 7 | 86.2226 | 18.011 | 0 | 2018-05-05 23:00 | 23 | 7 | 0 | 0 | 0 | 2018-05-05 23:00 | 23 | 7 | 87.0787 | 18.1899 | 0 | 2018-05-05 23:00 | 23 | 7 | 33.0899 | 6.9122 | 0
2018-05-06 | 0 | 1 | 86.2364 | 18.0139 | 0 | 2018-05-06 | 0 | 1 | 86.7994 | 18.1315 | 0 | 2018-05-06 | 0 | 1 | 0 | 0 | 0 | 2018-05-06 | 0 | 1 | 32.9838 | 6.89 | 0
2018-05-06 01:00 | 1 | 1 | 86.3188 | 18.0311 | 0 | 2018-05-06 01:00 | 1 | 1 | 86.952 | 18.1634 | 0 | 2018-05-06 01:00 | 1 | 1 | 0 | 0 | 0 | 2018-05-06 01:00 | 1 | 1 | 33.0418 | 6.9021 | 0
2018-05-06 02:00 | 2 | 1 | 86.2119 | 18.0088 | 0 | 2018-05-06 02:00 | 2 | 1 | 86.8177 | 18.1353 | 0 | 2018-05-06 02:00 | 2 | 1 | 0 | 0 | 0 | 2018-05-06 02:00 | 2 | 1 | 32.9907 | 6.8914 | 0
2018-05-06 03:00 | 3 | 1 | 86.1845 | 18.0031 | 0 | 2018-05-06 03:00 | 3 | 1 | 86.7857 | 18.1287 | 0 | 2018-05-06 03:00 | 3 | 1 | 0 | 0 | 0 | 2018-05-06 03:00 | 3 | 1 | 32.9786 | 6.8889 | 0
2018-05-06 04:00 | 4 | 1 | 86.2455 | 18.0158 | 0 | 2018-05-06 04:00 | 4 | 1 | 86.833 | 18.1385 | 0 | 2018-05-06 04:00 | 4 | 1 | 0 | 0 | 0 | 2018-05-06 04:00 | 4 | 1 | 32.9965 | 6.8926 | 0
2018-05-06 05:00 | 5 | 1 | 86.2333 | 18.0133 | 0 | 2018-05-06 05:00 | 5 | 1 | 86.833 | 18.1385 | 0 | 2018-05-06 05:00 | 5 | 1 | 0 | 0 | 0 | 2018-05-06 05:00 | 5 | 1 | 32.9965 | 6.8926 | 0
2018-05-06 06:00 | 6 | 1 | 86.2776 | 18.0225 | 0 | 2018-05-06 06:00 | 6 | 1 | 86.8528 | 18.1427 | 0 | 2018-05-06 06:00 | 6 | 1 | 0 | 0 | 0 | 2018-05-06 06:00 | 6 | 1 | 33.0041 | 6.8942 | 0
2018-05-06 07:00 | 7 | 1 | 86.2867 | 18.0244 | 0 | 2018-05-06 07:00 | 7 | 1 | 86.8452 | 18.1411 | 0 | 2018-05-06 07:00 | 7 | 1 | 0 | 0 | 0 | 2018-05-06 07:00 | 7 | 1 | 33.0012 | 6.8936 | 0
2018-05-06 08:00 | 8 | 1 | 86.2989 | 18.027 | 0 | 2018-05-06 08:00 | 8 | 1 | 86.9032 | 18.1532 | 0 | 2018-05-06 08:00 | 8 | 1 | 0 | 0 | 0 | 2018-05-06 08:00 | 8 | 1 | 33.0232 | 6.8982 | 0
2018-05-06 09:00 | 9 | 1 | 86.2867 | 18.0244 | 0 | 2018-05-06 09:00 | 9 | 1 | 86.8162 | 18.135 | 0 | 2018-05-06 09:00 | 9 | 1 | 0 | 0 | 0 | 2018-05-06 09:00 | 9 | 1 | 32.9902 | 6.8913 | 0
2018-05-06 10:00 | 10 | 1 | 86.2882 | 18.0247 | 0 | 2018-05-06 10:00 | 10 | 1 | 86.8528 | 18.1427 | 0 | 2018-05-06 10:00 | 10 | 1 | 0 | 0 | 0 | 2018-05-06 10:00 | 10 | 1 | 33.0041 | 6.8942 | 0
2018-05-06 11:00 | 11 | 1 | 86.1845 | 18.0031 | 0 | 2018-05-06 11:00 | 11 | 1 | 86.743 | 18.1197 | 0 | 2018-05-06 11:00 | 11 | 1 | 0 | 0 | 0 | 2018-05-06 11:00 | 11 | 1 | 32.9623 | 6.8855 | 0
2018-05-06 12:00 | 12 | 1 | 86.1418 | 17.9942 | 0 | 2018-05-06 12:00 | 12 | 1 | 86.714 | 18.1137 | 0 | 2018-05-06 12:00 | 12 | 1 | 0 | 0 | 0 | 2018-05-06 12:00 | 12 | 1 | 32.9513 | 6.8832 | 0
2018-05-06 13:00 | 13 | 1 | 86.1479 | 17.9954 | 0 | 2018-05-06 13:00 | 13 | 1 | 86.7659 | 18.1245 | 0 | 2018-05-06 13:00 | 13 | 1 | 0 | 0 | 0 | 2018-05-06 13:00 | 13 | 1 | 32.971 | 6.8873 | 0
2018-05-06 14:00 | 14 | 1 | 86.1112 | 17.9878 | 0 | 2018-05-06 14:00 | 14 | 1 | 86.7018 | 18.1111 | 0 | 2018-05-06 14:00 | 14 | 1 | 0 | 0 | 0 | 2018-05-06 14:00 | 14 | 1 | 32.9467 | 6.8822 | 0
2018-05-06 15:00 | 15 | 1 | 86.2455 | 18.0158 | 0 | 2018-05-06 15:00 | 15 | 1 | 86.8482 | 18.1417 | 0 | 2018-05-06 15:00 | 15 | 1 | 0 | 0 | 0 | 2018-05-06 15:00 | 15 | 1 | 33.0023 | 6.8939 | 0
2018-05-06 16:00 | 16 | 1 | 86.3447 | 18.0365 | 0 | 2018-05-06 16:00 | 16 | 1 | 86.9398 | 18.1609 | 0 | 2018-05-06 16:00 | 16 | 1 | 0 | 0 | 0 | 2018-05-06 16:00 | 16 | 1 | 33.0371 | 6.9011 | 0
2018-05-06 17:00 | 17 | 1 | 86.4805 | 18.0649 | 0 | 2018-05-06 17:00 | 17 | 1 | 86.9856 | 18.1704 | 0 | 2018-05-06 17:00 | 17 | 1 | 0 | 0 | 0 | 2018-05-06 17:00 | 17 | 1 | 33.0545 | 6.9048 | 0
2018-05-06 18:00 | 18 | 1 | 86.4332 | 18.055 | 0 | 2018-05-06 18:00 | 18 | 1 | 86.92 | 18.1567 | 0 | 2018-05-06 18:00 | 18 | 1 | 0 | 0 | 0 | 2018-05-06 18:00 | 18 | 1 | 33.0296 | 6.8996 | 0
2018-05-06 19:00 | 19 | 1 | 85.6794 | 17.8976 | 0 | 2018-05-06 19:00 | 19 | 1 | 85.9266 | 17.9492 | 0 | 2018-05-06 19:00 | 19 | 1 | 0 | 0 | 0 | 2018-05-06 19:00 | 19 | 1 | 32.6521 | 6.8207 | 0
2018-05-06 20:00 | 20 | 1 | 86.3294 | 18.0333 | 0 | 2018-05-06 20:00 | 20 | 1 | 86.5888 | 18.0875 | 0 | 2018-05-06 20:00 | 20 | 1 | 0 | 0 | 0 | 2018-05-06 20:00 | 20 | 1 | 32.9037 | 6.8733 | 0
2018-05-06 21:00 | 21 | 1 | 86.3569 | 18.0391 | 0 | 2018-05-06 21:00 | 21 | 1 | 86.6728 | 18.1051 | 0 | 2018-05-06 21:00 | 21 | 1 | 0 | 0 | 0 | 2018-05-06 21:00 | 21 | 1 | 32.9357 | 6.8799 | 0
2018-05-06 22:00 | 22 | 1 | 86.4881 | 18.0665 | 0 | 2018-05-06 22:00 | 22 | 1 | 86.8086 | 18.1334 | 0 | 2018-05-06 22:00 | 22 | 1 | 0 | 0 | 0 | 2018-05-06 22:00 | 22 | 1 | 32.9873 | 6.8907 | 0
2018-05-06 23:00 | 23 | 1 | 86.4332 | 18.055 | 0 | 2018-05-06 23:00 | 23 | 1 | 86.7353 | 18.1181 | 0 | 2018-05-06 23:00 | 23 | 1 | 0 | 0 | 0 | 2018-05-06 23:00 | 23 | 1 | 32.9594 | 6.8849 | 0
2018-05-07 | 0 | 2 | 86.4088 | 18.0499 | 0 | 2018-05-07 | 0 | 2 | 86.7002 | 18.1108 | 0 | 2018-05-07 | 0 | 2 | 86.9352 | 18.1599 | 0 | 2018-05-07 | 0 | 2 | 65.9815 | 13.7829 | 0
2018-05-07 01:00 | 1 | 2 | 86.0426 | 17.9734 | 0 | 2018-05-07 01:00 | 1 | 2 | 86.3127 | 18.0299 | 0 | 2018-05-07 01:00 | 1 | 2 | 86.5278 | 18.0748 | 0 | 2018-05-07 01:00 | 1 | 2 | 65.6794 | 13.7198 | 0
2018-05-07 02:00 | 2 | 2 | 86.392 | 18.0464 | 0 | 2018-05-07 02:00 | 2 | 2 | 86.6392 | 18.0981 | 0 | 2018-05-07 02:00 | 2 | 2 | 86.8421 | 18.1404 | 0 | 2018-05-07 02:00 | 2 | 2 | 65.9229 | 13.7706 | 0
2018-05-07 03:00 | 3 | 2 | 86.2776 | 18.0225 | 0 | 2018-05-07 03:00 | 3 | 2 | 86.5766 | 18.085 | 0 | 2018-05-07 03:00 | 3 | 2 | 86.7536 | 18.122 | 0 | 2018-05-07 03:00 | 3 | 2 | 65.8655 | 13.7586 | 0
2018-05-07 04:00 | 4 | 2 | 86.5034 | 18.0697 | 0 | 2018-05-07 04:00 | 4 | 2 | 86.8849 | 18.1494 | 0 | 2018-05-07 04:00 | 4 | 2 | 87.0283 | 18.1793 | 0 | 2018-05-07 04:00 | 4 | 2 | 66.087 | 13.8049 | 0
2018-05-07 05:00 | 5 | 2 | 86.3661 | 18.041 | 0 | 2018-05-07 05:00 | 5 | 2 | 86.772 | 18.1258 | 0 | 2018-05-07 05:00 | 5 | 2 | 87.0054 | 18.1746 | 0 | 2018-05-07 05:00 | 5 | 2 | 66.0354 | 13.7941 | 0
2018-05-07 06:00 | 6 | 2 | 86.2898 | 18.0251 | 0 | 2018-05-07 06:00 | 6 | 2 | 86.6499 | 18.1003 | 0 | 2018-05-07 06:00 | 6 | 2 | 86.8147 | 18.1347 | 0 | 2018-05-07 06:00 | 6 | 2 | 65.9165 | 13.7693 | 0
2018-05-07 07:00 | 7 | 2 | 86.2043 | 18.0072 | 0 | 2018-05-07 07:00 | 7 | 2 | 86.5278 | 18.0748 | 0 | 2018-05-07 07:00 | 7 | 2 | 86.7079 | 18.1124 | 0 | 2018-05-07 07:00 | 7 | 2 | 65.8296 | 13.7511 | 0
2018-05-07 08:00 | 8 | 2 | 86.3355 | 18.0346 | 0 | 2018-05-07 08:00 | 8 | 2 | 86.5461 | 18.0786 | 0 | 2018-05-07 08:00 | 8 | 2 | 86.8025 | 18.1322 | 0 | 2018-05-07 08:00 | 8 | 2 | 65.8725 | 13.7601 | 0
2018-05-07 09:00 | 9 | 2 | 86.3798 | 18.0439 | 0 | 2018-05-07 09:00 | 9 | 2 | 86.7262 | 18.1162 | 0 | 2018-05-07 09:00 | 9 | 2 | 86.8711 | 18.1465 | 0 | 2018-05-07 09:00 | 9 | 2 | 65.967 | 13.7798 | 0
2018-05-07 10:00 | 10 | 2 | 86.2272 | 18.012 | 0 | 2018-05-07 10:00 | 10 | 2 | 86.5156 | 18.0722 | 0 | 2018-05-07 10:00 | 10 | 2 | 86.714 | 18.1137 | 0 | 2018-05-07 10:00 | 10 | 2 | 65.8272 | 13.7507 | 0
2018-05-07 11:00 | 11 | 2 | 86.2119 | 18.0088 | 0 | 2018-05-07 11:00 | 11 | 2 | 86.5141 | 18.0719 | 0 | 2018-05-07 11:00 | 11 | 2 | 86.7201 | 18.115 | 0 | 2018-05-07 11:00 | 11 | 2 | 65.829 | 13.751 | 0
2018-05-07 12:00 | 12 | 2 | 86.389 | 18.0458 | 0 | 2018-05-07 12:00 | 12 | 2 | 86.6835 | 18.1073 | 0 | 2018-05-07 12:00 | 12 | 2 | 86.8574 | 18.1436 | 0 | 2018-05-07 12:00 | 12 | 2 | 65.9455 | 13.7754 | 0
2018-05-07 13:00 | 13 | 2 | 86.4027 | 18.0487 | 0 | 2018-05-07 13:00 | 13 | 2 | 86.6224 | 18.0946 | 0 | 2018-05-07 13:00 | 13 | 2 | 86.7475 | 18.1207 | 0 | 2018-05-07 13:00 | 13 | 2 | 65.8806 | 13.7618 | 0
2018-05-07 14:00 | 14 | 2 | 86.3783 | 18.0436 | 0 | 2018-05-07 14:00 | 14 | 2 | 86.6606 | 18.1025 | 0 | 2018-05-07 14:00 | 14 | 2 | 86.7903 | 18.1296 | 0 | 2018-05-07 14:00 | 14 | 2 | 65.9113 | 13.7682 | 0
2018-05-07 15:00 | 15 | 2 | 86.3355 | 18.0346 | 0 | 2018-05-07 15:00 | 15 | 2 | 86.5248 | 18.0742 | 0 | 2018-05-07 15:00 | 15 | 2 | 86.7384 | 18.1188 | 0 | 2018-05-07 15:00 | 15 | 2 | 65.84 | 13.7533 | 0
2018-05-07 16:00 | 16 | 2 | 86.3493 | 18.0375 | 0 | 2018-05-07 16:00 | 16 | 2 | 86.4912 | 18.0671 | 0 | 2018-05-07 16:00 | 16 | 2 | 86.685 | 18.1076 | 0 | 2018-05-07 16:00 | 16 | 2 | 65.807 | 13.7464 | 0
2018-05-07 17:00 | 17 | 2 | 86.244 | 18.0155 | 0 | 2018-05-07 17:00 | 17 | 2 | 86.4683 | 18.0624 | 0 | 2018-05-07 17:00 | 17 | 2 | 86.6743 | 18.1054 | 0 | 2018-05-07 17:00 | 17 | 2 | 65.7942 | 13.7437 | 0
2018-05-07 18:00 | 18 | 2 | 86.3142 | 18.0302 | 0 | 2018-05-07 18:00 | 18 | 2 | 86.4378 | 18.056 | 0 | 2018-05-07 18:00 | 18 | 2 | 86.5934 | 18.0885 | 0 | 2018-05-07 18:00 | 18 | 2 | 65.7519 | 13.7349 | 0
2018-05-07 19:00 | 19 | 2 | 86.2089 | 18.0082 | 0 | 2018-05-07 19:00 | 19 | 2 | 86.3508 | 18.0378 | 0 | 2018-05-07 19:00 | 19 | 2 | 86.5583 | 18.0812 | 0 | 2018-05-07 19:00 | 19 | 2 | 65.7055 | 13.7252 | 0
2018-05-07 20:00 | 20 | 2 | 86.2181 | 18.0101 | 0 | 2018-05-07 20:00 | 20 | 2 | 86.4836 | 18.0656 | 0 | 2018-05-07 20:00 | 20 | 2 | 86.6896 | 18.1086 | 0 | 2018-05-07 20:00 | 20 | 2 | 65.8058 | 13.7462 | 0
2018-05-07 21:00 | 21 | 2 | 86.1494 | 17.9957 | 0 | 2018-05-07 21:00 | 21 | 2 | 86.4759 | 18.064 | 0 | 2018-05-07 21:00 | 21 | 2 | 86.63 | 18.0961 | 0 | 2018-05-07 21:00 | 21 | 2 | 65.7802 | 13.7408 | 0
2018-05-07 22:00 | 22 | 2 | 86.2593 | 18.0187 | 0 | 2018-05-07 22:00 | 22 | 2 | 86.5522 | 18.0799 | 0 | 2018-05-07 22:00 | 22 | 2 | 86.6468 | 18.0997 | 0 | 2018-05-07 22:00 | 22 | 2 | 65.8156 | 13.7482 | 0
2018-05-07 23:00 | 23 | 2 | 86.4424 | 18.057 | 0 | 2018-05-07 23:00 | 23 | 2 | 86.8055 | 18.1328 | 0 | 2018-05-07 23:00 | 23 | 2 | 86.8864 | 18.1497 | 0 | 2018-05-07 23:00 | 23 | 2 | 66.0029 | 13.7874 | 0
2018-05-08 | 0 | 3 | 86.4637 | 18.0614 | 0 | 2018-05-08 | 0 | 3 | 0 | 0 | 0 | 2018-05-08 | 0 | 3 | 0 | 0 | 0 | 2018-05-08 | 0 | 3 | 0 | 0 | 0
2018-05-08 01:00 | 1 | 3 | 86.5629 | 18.0821 | 0 | 2018-05-08 01:00 | 1 | 3 | 0 | 0 | 0 | 2018-05-08 01:00 | 1 | 3 | 0 | 0 | 0 | 2018-05-08 01:00 | 1 | 3 | 0 | 0 | 0
2018-05-08 02:00 | 2 | 3 | 86.3706 | 18.042 | 0 | 2018-05-08 02:00 | 2 | 3 | 0 | 0 | 0 | 2018-05-08 02:00 | 2 | 3 | 0 | 0 | 0 | 2018-05-08 02:00 | 2 | 3 | 0 | 0 | 0
2018-05-08 03:00 | 3 | 3 | 86.3523 | 18.0381 | 0 | 2018-05-08 03:00 | 3 | 3 | 0 | 0 | 0 | 2018-05-08 03:00 | 3 | 3 | 0 | 0 | 0 | 2018-05-08 03:00 | 3 | 3 | 0 | 0 | 0
2018-05-08 04:00 | 4 | 3 | 86.3676 | 18.0413 | 0 | 2018-05-08 04:00 | 4 | 3 | 0 | 0 | 0 | 2018-05-08 04:00 | 4 | 3 | 0 | 0 | 0 | 2018-05-08 04:00 | 4 | 3 | 0 | 0 | 0
2018-05-08 05:00 | 5 | 3 | 86.4027 | 18.0487 | 0 | 2018-05-08 05:00 | 5 | 3 | 0 | 0 | 0 | 2018-05-08 05:00 | 5 | 3 | 0 | 0 | 0 | 2018-05-08 05:00 | 5 | 3 | 0 | 0 | 0
2018-05-08 06:00 | 6 | 3 | 86.4652 | 18.0617 | 0 | 2018-05-08 06:00 | 6 | 3 | 0 | 0 | 0 | 2018-05-08 06:00 | 6 | 3 | 0 | 0 | 0 | 2018-05-08 06:00 | 6 | 3 | 0 | 0 | 0
2018-05-08 07:00 | 7 | 3 | 86.4012 | 18.0483 | 0 | 2018-05-08 07:00 | 7 | 3 | 0 | 0 | 0 | 2018-05-08 07:00 | 7 | 3 | 0 | 0 | 0 | 2018-05-08 07:00 | 7 | 3 | 0 | 0 | 0
2018-05-08 08:00 | 8 | 3 | 86.4515 | 18.0589 | 0 | 2018-05-08 08:00 | 8 | 3 | 0 | 0 | 0 | 2018-05-08 08:00 | 8 | 3 | 0 | 0 | 0 | 2018-05-08 08:00 | 8 | 3 | 0 | 0 | 0
2018-05-08 09:00 | 9 | 3 | 86.2028 | 18.0069 | 0 | 2018-05-08 09:00 | 9 | 3 | 0 | 0 | 0 | 2018-05-08 09:00 | 9 | 3 | 0 | 0 | 0 | 2018-05-08 09:00 | 9 | 3 | 0 | 0 | 0
2018-05-08 10:00 | 10 | 3 | 86.2715 | 18.0213 | 0 | 2018-05-08 10:00 | 10 | 3 | 0 | 0 | 0 | 2018-05-08 10:00 | 10 | 3 | 0 | 0 | 0 | 2018-05-08 10:00 | 10 | 3 | 0 | 0 | 0
2018-05-08 11:00 | 11 | 3 | 86.7567 | 18.1226 | 0 | 2018-05-08 11:00 | 11 | 3 | 0 | 0 | 0 | 2018-05-08 11:00 | 11 | 3 | 0 | 0 | 0 | 2018-05-08 11:00 | 11 | 3 | 0 | 0 | 0
2018-05-08 12:00 | 12 | 3 | 86.6194 | 18.0939 | 0 | 2018-05-08 12:00 | 12 | 3 | 0 | 0 | 0 | 2018-05-08 12:00 | 12 | 3 | 0 | 0 | 0 | 2018-05-08 12:00 | 12 | 3 | 0 | 0 | 0
2018-05-08 13:00 | 13 | 3 | 86.6377 | 18.0977 | 0 | 2018-05-08 13:00 | 13 | 3 | 0 | 0 | 0 | 2018-05-08 13:00 | 13 | 3 | 0 | 0 | 0 | 2018-05-08 13:00 | 13 | 3 | 0 | 0 | 0
2018-05-08 14:00 | 14 | 3 | 86.8757 | 18.1475 | 0 | 2018-05-08 14:00 | 14 | 3 | 0 | 0 | 0 | 2018-05-08 14:00 | 14 | 3 | 0 | 0 | 0 | 2018-05-08 14:00 | 14 | 3 | 0 | 0 | 0
2018-05-08 15:00 | 15 | 3 | 86.7994 | 18.1315 | 0 | 2018-05-08 15:00 | 15 | 3 | 0 | 0 | 0 | 2018-05-08 15:00 | 15 | 3 | 0 | 0 | 0 | 2018-05-08 15:00 | 15 | 3 | 0 | 0 | 0
2018-05-08 16:00 | 16 | 3 | 86.7674 | 18.1248 | 0 | 2018-05-08 16:00 | 16 | 3 | 0 | 0 | 0 | 2018-05-08 16:00 | 16 | 3 | 0 | 0 | 0 | 2018-05-08 16:00 | 16 | 3 | 0 | 0 | 0
2018-05-08 17:00 | 17 | 3 | 86.7384 | 18.1188 | 0 | 2018-05-08 17:00 | 17 | 3 | 0 | 0 | 0 | 2018-05-08 17:00 | 17 | 3 | 0 | 0 | 0 | 2018-05-08 17:00 | 17 | 3 | 0 | 0 | 0
2018-05-08 18:00 | 18 | 3 | 86.7124 | 18.1134 | 0 | 2018-05-08 18:00 | 18 | 3 | 0 | 0 | 0 | 2018-05-08 18:00 | 18 | 3 | 0 | 0 | 0 | 2018-05-08 18:00 | 18 | 3 | 0 | 0 | 0
2018-05-08 19:00 | 19 | 3 | 86.8376 | 18.1395 | 0 | 2018-05-08 19:00 | 19 | 3 | 0 | 0 | 0 | 2018-05-08 19:00 | 19 | 3 | 0 | 0 | 0 | 2018-05-08 19:00 | 19 | 3 | 0 | 0 | 0
2018-05-08 20:00 | 20 | 3 | 86.627 | 18.0955 | 0 | 2018-05-08 20:00 | 20 | 3 | 0 | 0 | 0 | 2018-05-08 20:00 | 20 | 3 | 0 | 0 | 0 | 2018-05-08 20:00 | 20 | 3 | 0 | 0 | 0
2018-05-08 21:00 | 21 | 3 | 86.6239 | 18.0949 | 0 | 2018-05-08 21:00 | 21 | 3 | 0 | 0 | 0 | 2018-05-08 21:00 | 21 | 3 | 0 | 0 | 0 | 2018-05-08 21:00 | 21 | 3 | 0 | 0 | 0
2018-05-08 22:00 | 22 | 3 | 86.714 | 18.1137 | 0 | 2018-05-08 22:00 | 22 | 3 | 0 | 0 | 0 | 2018-05-08 22:00 | 22 | 3 | 0 | 0 | 0 | 2018-05-08 22:00 | 22 | 3 | 0 | 0 | 0
2018-05-08 23:00 | 23 | 3 | 86.8971 | 18.1519 | 0 | 2018-05-08 23:00 | 23 | 3 | 0 | 0 | 0 | 2018-05-08 23:00 | 23 | 3 | 0 | 0 | 0 | 2018-05-08 23:00 | 23 | 3 | 0 | 0 | 0
2018-05-09 | 0 | 4 | 0 | 0 | 0 | 2018-05-09 | 0 | 4 | 0 | 0 | 0 | 2018-05-09 | 0 | 4 | 86.6712 | 18.1047 | 0 | 2018-05-09 | 0 | 4 | 32.9351 | 6.8798 | 0
2018-05-09 01:00 | 1 | 4 | 0 | 0 | 0 | 2018-05-09 01:00 | 1 | 4 | 0 | 0 | 0 | 2018-05-09 01:00 | 1 | 4 | 86.511 | 18.0713 | 0 | 2018-05-09 01:00 | 1 | 4 | 32.8742 | 6.8671 | 0
2018-05-09 02:00 | 2 | 4 | 0 | 0 | 0 | 2018-05-09 02:00 | 2 | 4 | 0 | 0 | 0 | 2018-05-09 02:00 | 2 | 4 | 86.7628 | 18.1239 | 0 | 2018-05-09 02:00 | 2 | 4 | 32.9699 | 6.8871 | 0
2018-05-09 03:00 | 3 | 4 | 0 | 0 | 0 | 2018-05-09 03:00 | 3 | 4 | 0 | 0 | 0 | 2018-05-09 03:00 | 3 | 4 | 86.7384 | 18.1188 | 0 | 2018-05-09 03:00 | 3 | 4 | 32.9606 | 6.8851 | 0
2018-05-09 04:00 | 4 | 4 | 0 | 0 | 0 | 2018-05-09 04:00 | 4 | 4 | 0 | 0 | 0 | 2018-05-09 04:00 | 4 | 4 | 86.8376 | 18.1395 | 0 | 2018-05-09 04:00 | 4 | 4 | 32.9983 | 6.893 | 0
2018-05-09 05:00 | 5 | 4 | 0 | 0 | 0 | 2018-05-09 05:00 | 5 | 4 | 0 | 0 | 0 | 2018-05-09 05:00 | 5 | 4 | 87.0222 | 18.1781 | 0 | 2018-05-09 05:00 | 5 | 4 | 33.0684 | 6.9077 | 0
2018-05-09 06:00 | 6 | 4 | 0 | 0 | 0 | 2018-05-09 06:00 | 6 | 4 | 0 | 0 | 0 | 2018-05-09 06:00 | 6 | 4 | 86.9627 | 18.1656 | 0 | 2018-05-09 06:00 | 6 | 4 | 33.0458 | 6.9029 | 0
2018-05-09 07:00 | 7 | 4 | 0 | 0 | 0 | 2018-05-09 07:00 | 7 | 4 | 0 | 0 | 0 | 2018-05-09 07:00 | 7 | 4 | 87.1321 | 18.201 | 0 | 2018-05-09 07:00 | 7 | 4 | 33.1102 | 6.9164 | 0
2018-05-09 08:00 | 8 | 4 | 0 | 0 | 0 | 2018-05-09 08:00 | 8 | 4 | 0 | 0 | 0 | 2018-05-09 08:00 | 8 | 4 | 87.1931 | 18.2138 | 0 | 2018-05-09 08:00 | 8 | 4 | 33.1334 | 6.9212 | 0
2018-05-09 09:00 | 9 | 4 | 0 | 0 | 0 | 2018-05-09 09:00 | 9 | 4 | 0 | 0 | 0 | 2018-05-09 09:00 | 9 | 4 | 86.7155 | 18.114 | 0 | 2018-05-09 09:00 | 9 | 4 | 32.9519 | 6.8833 | 0
2018-05-09 10:00 | 10 | 4 | 0 | 0 | 0 | 2018-05-09 10:00 | 10 | 4 | 0 | 0 | 0 | 2018-05-09 10:00 | 10 | 4 | 86.6743 | 18.1054 | 0 | 2018-05-09 10:00 | 10 | 4 | 32.9362 | 6.88 | 0
2018-05-09 11:00 | 11 | 4 | 0 | 0 | 0 | 2018-05-09 11:00 | 11 | 4 | 0 | 0 | 0 | 2018-05-09 11:00 | 11 | 4 | 86.8956 | 18.1516 | 0 | 2018-05-09 11:00 | 11 | 4 | 33.0203 | 6.8976 | 0
2018-05-09 12:00 | 12 | 4 | 0 | 0 | 0 | 2018-05-09 12:00 | 12 | 4 | 0 | 0 | 0 | 2018-05-09 12:00 | 12 | 4 | 86.9276 | 18.1583 | 0 | 2018-05-09 12:00 | 12 | 4 | 33.0325 | 6.9002 | 0
2018-05-09 13:00 | 13 | 4 | 0 | 0 | 0 | 2018-05-09 13:00 | 13 | 4 | 0 | 0 | 0 | 2018-05-09 13:00 | 13 | 4 | 87.2541 | 18.2265 | 0 | 2018-05-09 13:00 | 13 | 4 | 33.1566 | 6.9261 | 0
2018-05-09 14:00 | 14 | 4 | 0 | 0 | 0 | 2018-05-09 14:00 | 14 | 4 | 0 | 0 | 0 | 2018-05-09 14:00 | 14 | 4 | 87.4037 | 18.2578 | 0 | 2018-05-09 14:00 | 14 | 4 | 33.2134 | 6.9379 | 0
2018-05-09 15:00 | 15 | 4 | 0 | 0 | 0 | 2018-05-09 15:00 | 15 | 4 | 0 | 0 | 0 | 2018-05-09 15:00 | 15 | 4 | 87.2129 | 18.2179 | 0 | 2018-05-09 15:00 | 15 | 4 | 33.1409 | 6.9228 | 0
2018-05-09 16:00 | 16 | 4 | 0 | 0 | 0 | 2018-05-09 16:00 | 16 | 4 | 0 | 0 | 0 | 2018-05-09 16:00 | 16 | 4 | 86.9718 | 18.1675 | 0 | 2018-05-09 16:00 | 16 | 4 | 33.0493 | 6.9037 | 0
2018-05-09 17:00 | 17 | 4 | 0 | 0 | 0 | 2018-05-09 17:00 | 17 | 4 | 0 | 0 | 0 | 2018-05-09 17:00 | 17 | 4 | 87.1397 | 18.2026 | 0 | 2018-05-09 17:00 | 17 | 4 | 33.1131 | 6.917 | 0
2018-05-09 18:00 | 18 | 4 | 0 | 0 | 0 | 2018-05-09 18:00 | 18 | 4 | 0 | 0 | 0 | 2018-05-09 18:00 | 18 | 4 | 87.2435 | 18.2243 | 0 | 2018-05-09 18:00 | 18 | 4 | 33.1525 | 6.9252 | 0
2018-05-09 19:00 | 19 | 4 | 0 | 0 | 0 | 2018-05-09 19:00 | 19 | 4 | 0 | 0 | 0 | 2018-05-09 19:00 | 19 | 4 | 86.8894 | 18.1503 | 0 | 2018-05-09 19:00 | 19 | 4 | 33.018 | 6.8971 | 0
2018-05-09 20:00 | 20 | 4 | 0 | 0 | 0 | 2018-05-09 20:00 | 20 | 4 | 0 | 0 | 0 | 2018-05-09 20:00 | 20 | 4 | 87.1839 | 18.2118 | 0 | 2018-05-09 20:00 | 20 | 4 | 33.1299 | 6.9205 | 0
2018-05-09 21:00 | 21 | 4 | 0 | 0 | 0 | 2018-05-09 21:00 | 21 | 4 | 0 | 0 | 0 | 2018-05-09 21:00 | 21 | 4 | 87.2419 | 18.224 | 0 | 2018-05-09 21:00 | 21 | 4 | 33.1519 | 6.9251 | 0
2018-05-09 22:00 | 22 | 4 | 0 | 0 | 0 | 2018-05-09 22:00 | 22 | 4 | 0 | 0 | 0 | 2018-05-09 22:00 | 22 | 4 | 87.1733 | 18.2096 | 0 | 2018-05-09 22:00 | 22 | 4 | 33.1259 | 6.9197 | 0
2018-05-09 23:00 | 23 | 4 | 0 | 0 | 0 | 2018-05-09 23:00 | 23 | 4 | 0 | 0 | 0 | 2018-05-09 23:00 | 23 | 4 | 87.2557 | 18.2268 | 0 | 2018-05-09 23:00 | 23 | 4 | 33.1572 | 6.9262 | 0
2018-05-10 | 0 | 5 | 86.5492 | 18.0793 | 0 | 2018-05-10 | 0 | 5 | 0 | 0 | 0 | 2018-05-10 | 0 | 5 | 0 | 0 | 0 | 2018-05-10 | 0 | 5 | 0 | 0 | 0
2018-05-10 01:00 | 1 | 5 | 86.7201 | 18.115 | 0 | 2018-05-10 01:00 | 1 | 5 | 0 | 0 | 0 | 2018-05-10 01:00 | 1 | 5 | 0 | 0 | 0 | 2018-05-10 01:00 | 1 | 5 | 0 | 0 | 0
2018-05-10 02:00 | 2 | 5 | 86.5095 | 18.071 | 0 | 2018-05-10 02:00 | 2 | 5 | 0 | 0 | 0 | 2018-05-10 02:00 | 2 | 5 | 0 | 0 | 0 | 2018-05-10 02:00 | 2 | 5 | 0 | 0 | 0
2018-05-10 03:00 | 3 | 5 | 86.4576 | 18.0601 | 0 | 2018-05-10 03:00 | 3 | 5 | 0 | 0 | 0 | 2018-05-10 03:00 | 3 | 5 | 0 | 0 | 0 | 2018-05-10 03:00 | 3 | 5 | 0 | 0 | 0
2018-05-10 04:00 | 4 | 5 | 86.6316 | 18.0965 | 0 | 2018-05-10 04:00 | 4 | 5 | 0 | 0 | 0 | 2018-05-10 04:00 | 4 | 5 | 0 | 0 | 0 | 2018-05-10 04:00 | 4 | 5 | 0 | 0 | 0
2018-05-10 05:00 | 5 | 5 | 86.569 | 18.0834 | 0 | 2018-05-10 05:00 | 5 | 5 | 0 | 0 | 0 | 2018-05-10 05:00 | 5 | 5 | 0 | 0 | 0 | 2018-05-10 05:00 | 5 | 5 | 0 | 0 | 0
2018-05-10 06:00 | 6 | 5 | 86.6468 | 18.0997 | 0 | 2018-05-10 06:00 | 6 | 5 | 0 | 0 | 0 | 2018-05-10 06:00 | 6 | 5 | 0 | 0 | 0 | 2018-05-10 06:00 | 6 | 5 | 0 | 0 | 0
2018-05-10 07:00 | 7 | 5 | 86.6361 | 18.0974 | 0 | 2018-05-10 07:00 | 7 | 5 | 0 | 0 | 0 | 2018-05-10 07:00 | 7 | 5 | 0 | 0 | 0 | 2018-05-10 07:00 | 7 | 5 | 0 | 0 | 0
2018-05-10 08:00 | 8 | 5 | 86.6819 | 18.107 | 0 | 2018-05-10 08:00 | 8 | 5 | 0 | 0 | 0 | 2018-05-10 08:00 | 8 | 5 | 0 | 0 | 0 | 2018-05-10 08:00 | 8 | 5 | 0 | 0 | 0
2018-05-10 09:00 | 9 | 5 | 86.7094 | 18.1127 | 0 | 2018-05-10 09:00 | 9 | 5 | 0 | 0 | 0 | 2018-05-10 09:00 | 9 | 5 | 0 | 0 | 0 | 2018-05-10 09:00 | 9 | 5 | 0 | 0 | 0
2018-05-10 10:00 | 10 | 5 | 86.7933 | 18.1303 | 0 | 2018-05-10 10:00 | 10 | 5 | 0 | 0 | 0 | 2018-05-10 10:00 | 10 | 5 | 0 | 0 | 0 | 2018-05-10 10:00 | 10 | 5 | 0 | 0 | 0
2018-05-10 11:00 | 11 | 5 | 86.8009 | 18.1318 | 0 | 2018-05-10 11:00 | 11 | 5 | 0 | 0 | 0 | 2018-05-10 11:00 | 11 | 5 | 0 | 0 | 0 | 2018-05-10 11:00 | 11 | 5 | 0 | 0 | 0
2018-05-10 12:00 | 12 | 5 | 86.6728 | 18.1051 | 0 | 2018-05-10 12:00 | 12 | 5 | 0 | 0 | 0 | 2018-05-10 12:00 | 12 | 5 | 0 | 0 | 0 | 2018-05-10 12:00 | 12 | 5 | 0 | 0 | 0
2018-05-10 13:00 | 13 | 5 | 86.6316 | 18.0965 | 0 | 2018-05-10 13:00 | 13 | 5 | 0 | 0 | 0 | 2018-05-10 13:00 | 13 | 5 | 0 | 0 | 0 | 2018-05-10 13:00 | 13 | 5 | 0 | 0 | 0
2018-05-10 14:00 | 14 | 5 | 86.6316 | 18.0965 | 0 | 2018-05-10 14:00 | 14 | 5 | 0 | 0 | 0 | 2018-05-10 14:00 | 14 | 5 | 0 | 0 | 0 | 2018-05-10 14:00 | 14 | 5 | 0 | 0 | 0
2018-05-10 15:00 | 15 | 5 | 86.6636 | 18.1032 | 0 | 2018-05-10 15:00 | 15 | 5 | 0 | 0 | 0 | 2018-05-10 15:00 | 15 | 5 | 0 | 0 | 0 | 2018-05-10 15:00 | 15 | 5 | 0 | 0 | 0
2018-05-10 16:00 | 16 | 5 | 86.5568 | 18.0808 | 0 | 2018-05-10 16:00 | 16 | 5 | 0 | 0 | 0 | 2018-05-10 16:00 | 16 | 5 | 0 | 0 | 0 | 2018-05-10 16:00 | 16 | 5 | 0 | 0 | 0
2018-05-10 17:00 | 17 | 5 | 86.6865 | 18.1079 | 0 | 2018-05-10 17:00 | 17 | 5 | 0 | 0 | 0 | 2018-05-10 17:00 | 17 | 5 | 0 | 0 | 0 | 2018-05-10 17:00 | 17 | 5 | 0 | 0 | 0
2018-05-10 18:00 | 18 | 5 | 86.7262 | 18.1162 | 0 | 2018-05-10 18:00 | 18 | 5 | 0 | 0 | 0 | 2018-05-10 18:00 | 18 | 5 | 0 | 0 | 0 | 2018-05-10 18:00 | 18 | 5 | 0 | 0 | 0
2018-05-10 19:00 | 19 | 5 | 86.5187 | 18.0729 | 0 | 2018-05-10 19:00 | 19 | 5 | 0 | 0 | 0 | 2018-05-10 19:00 | 19 | 5 | 0 | 0 | 0 | 2018-05-10 19:00 | 19 | 5 | 0 | 0 | 0
2018-05-10 20:00 | 20 | 5 | 86.5766 | 18.085 | 0 | 2018-05-10 20:00 | 20 | 5 | 0 | 0 | 0 | 2018-05-10 20:00 | 20 | 5 | 0 | 0 | 0 | 2018-05-10 20:00 | 20 | 5 | 0 | 0 | 0
2018-05-10 21:00 | 21 | 5 | 86.6194 | 18.0939 | 0 | 2018-05-10 21:00 | 21 | 5 | 0 | 0 | 0 | 2018-05-10 21:00 | 21 | 5 | 0 | 0 | 0 | 2018-05-10 21:00 | 21 | 5 | 0 | 0 | 0
2018-05-10 22:00 | 22 | 5 | 86.6743 | 18.1054 | 0 | 2018-05-10 22:00 | 22 | 5 | 0 | 0 | 0 | 2018-05-10 22:00 | 22 | 5 | 0 | 0 | 0 | 2018-05-10 22:00 | 22 | 5 | 0 | 0 | 0
2018-05-10 23:00 | 23 | 5 | 86.5644 | 18.0824 | 0 | 2018-05-10 23:00 | 23 | 5 | 0 | 0 | 0 | 2018-05-10 23:00 | 23 | 5 | 0 | 0 | 0 | 2018-05-10 23:00 | 23 | 5 | 0 | 0 | 0
2018-05-11 | 0 | 6 | 86.2226 | 18.011 | 0 | 2018-05-11 | 0 | 6 | 86.688 | 18.1083 | 0 | 2018-05-11 | 0 | 6 | 0 | 0 | 0 | 2018-05-11 | 0 | 6 | 32.9414 | 6.8811 | 0
2018-05-11 01:00 | 1 | 6 | 86.1128 | 17.9881 | 0 | 2018-05-11 01:00 | 1 | 6 | 86.5232 | 18.0738 | 0 | 2018-05-11 01:00 | 1 | 6 | 0 | 0 | 0 | 2018-05-11 01:00 | 1 | 6 | 32.8788 | 6.8681 | 0
2018-05-11 02:00 | 2 | 6 | 86.2791 | 18.0228 | 0 | 2018-05-11 02:00 | 2 | 6 | 86.6896 | 18.1086 | 0 | 2018-05-11 02:00 | 2 | 6 | 0 | 0 | 0 | 2018-05-11 02:00 | 2 | 6 | 32.942 | 6.8813 | 0
2018-05-11 03:00 | 3 | 6 | 86.0014 | 17.9648 | 0 | 2018-05-11 03:00 | 3 | 6 | 86.4485 | 18.0582 | 0 | 2018-05-11 03:00 | 3 | 6 | 0 | 0 | 0 | 2018-05-11 03:00 | 3 | 6 | 32.8504 | 6.8621 | 0
2018-05-11 04:00 | 4 | 6 | 86.0533 | 17.9757 | 0 | 2018-05-11 04:00 | 4 | 6 | 86.4347 | 18.0553 | 0 | 2018-05-11 04:00 | 4 | 6 | 0 | 0 | 0 | 2018-05-11 04:00 | 4 | 6 | 32.8452 | 6.861 | 0
2018-05-11 05:00 | 5 | 6 | 86.2257 | 18.0117 | 0 | 2018-05-11 05:00 | 5 | 6 | 86.6117 | 18.0923 | 0 | 2018-05-11 05:00 | 5 | 6 | 0 | 0 | 0 | 2018-05-11 05:00 | 5 | 6 | 32.9124 | 6.8751 | 0
2018-05-11 06:00 | 6 | 6 | 86.4332 | 18.055 | 0 | 2018-05-11 06:00 | 6 | 6 | 86.9352 | 18.1599 | 0 | 2018-05-11 06:00 | 6 | 6 | 0 | 0 | 0 | 2018-05-11 06:00 | 6 | 6 | 33.0354 | 6.9008 | 0
2018-05-11 07:00 | 7 | 6 | 86.5873 | 18.0872 | 0 | 2018-05-11 07:00 | 7 | 6 | 87.0619 | 18.1864 | 0 | 2018-05-11 07:00 | 7 | 6 | 0 | 0 | 0 | 2018-05-11 07:00 | 7 | 6 | 33.0835 | 6.9108 | 0
2018-05-11 08:00 | 8 | 6 | 86.3691 | 18.0416 | 0 | 2018-05-11 08:00 | 8 | 6 | 86.7811 | 18.1277 | 0 | 2018-05-11 08:00 | 8 | 6 | 0 | 0 | 0 | 2018-05-11 08:00 | 8 | 6 | 32.9768 | 6.8885 | 0
2018-05-11 09:00 | 9 | 6 | 86.334 | 18.0343 | 0 | 2018-05-11 09:00 | 9 | 6 | 86.7399 | 18.1191 | 0 | 2018-05-11 09:00 | 9 | 6 | 0 | 0 | 0 | 2018-05-11 09:00 | 9 | 6 | 32.9612 | 6.8853 | 0
2018-05-11 10:00 | 10 | 6 | 86.5126 | 18.0716 | 0 | 2018-05-11 10:00 | 10 | 6 | 86.862 | 18.1446 | 0 | 2018-05-11 10:00 | 10 | 6 | 0 | 0 | 0 | 2018-05-11 10:00 | 10 | 6 | 33.0076 | 6.8949 | 0
2018-05-11 11:00 | 11 | 6 | 86.5003 | 18.069 | 0 | 2018-05-11 11:00 | 11 | 6 | 86.9306 | 18.1589 | 0 | 2018-05-11 11:00 | 11 | 6 | 0 | 0 | 0 | 2018-05-11 11:00 | 11 | 6 | 33.0336 | 6.9004 | 0
2018-05-11 12:00 | 12 | 6 | 86.7002 | 18.1108 | 0 | 2018-05-11 12:00 | 12 | 6 | 87.1412 | 18.2029 | 0 | 2018-05-11 12:00 | 12 | 6 | 0 | 0 | 0 | 2018-05-11 12:00 | 12 | 6 | 33.1137 | 6.9171 | 0
2018-05-11 13:00 | 13 | 6 | 86.363 | 18.0404 | 0 | 2018-05-11 13:00 | 13 | 6 | 86.8009 | 18.1318 | 0 | 2018-05-11 13:00 | 13 | 6 | 0 | 0 | 0 | 2018-05-11 13:00 | 13 | 6 | 32.9843 | 6.8901 | 0
2018-05-11 14:00 | 14 | 6 | 86.4408 | 18.0566 | 0 | 2018-05-11 14:00 | 14 | 6 | 86.8635 | 18.1449 | 0 | 2018-05-11 14:00 | 14 | 6 | 0 | 0 | 0 | 2018-05-11 14:00 | 14 | 6 | 33.0081 | 6.8951 | 0
2018-05-11 15:00 | 15 | 6 | 86.2943 | 18.026 | 0 | 2018-05-11 15:00 | 15 | 6 | 86.6743 | 18.1054 | 0 | 2018-05-11 15:00 | 15 | 6 | 0 | 0 | 0 | 2018-05-11 15:00 | 15 | 6 | 32.9362 | 6.88 | 0
2018-05-11 16:00 | 16 | 6 | 86.3706 | 18.042 | 0 | 2018-05-11 16:00 | 16 | 6 | 86.7491 | 18.121 | 0 | 2018-05-11 16:00 | 16 | 6 | 0 | 0 | 0 | 2018-05-11 16:00 | 16 | 6 | 32.9647 | 6.886 | 0
2018-05-11 17:00 | 17 | 6 | 86.2882 | 18.0247 | 0 | 2018-05-11 17:00 | 17 | 6 | 86.7445 | 18.1201 | 0 | 2018-05-11 17:00 | 17 | 6 | 0 | 0 | 0 | 2018-05-11 17:00 | 17 | 6 | 32.9629 | 6.8856 | 0
2018-05-11 18:00 | 18 | 6 | 86.1875 | 18.0037 | 0 | 2018-05-11 18:00 | 18 | 6 | 86.6667 | 18.1038 | 0 | 2018-05-11 18:00 | 18 | 6 | 0 | 0 | 0 | 2018-05-11 18:00 | 18 | 6 | 32.9333 | 6.8794 | 0
2018-05-11 19:00 | 19 | 6 | 86.099 | 17.9852 | 0 | 2018-05-11 19:00 | 19 | 6 | 86.5431 | 18.078 | 0 | 2018-05-11 19:00 | 19 | 6 | 0 | 0 | 0 | 2018-05-11 19:00 | 19 | 6 | 32.8864 | 6.8696 | 0
2018-05-11 20:00 | 20 | 6 | 86.1997 | 18.0063 | 0 | 2018-05-11 20:00 | 20 | 6 | 86.5187 | 18.0729 | 0 | 2018-05-11 20:00 | 20 | 6 | 0 | 0 | 0 | 2018-05-11 20:00 | 20 | 6 | 32.8771 | 6.8677 | 0
2018-05-11 21:00 | 21 | 6 | 86.3767 | 18.0432 | 0 | 2018-05-11 21:00 | 21 | 6 | 86.7247 | 18.1159 | 0 | 2018-05-11 21:00 | 21 | 6 | 0 | 0 | 0 | 2018-05-11 21:00 | 21 | 6 | 32.9554 | 6.8841 | 0
2018-05-11 22:00 | 22 | 6 | 86.3691 | 18.0416 | 0 | 2018-05-11 22:00 | 22 | 6 | 86.7659 | 18.1245 | 0 | 2018-05-11 22:00 | 22 | 6 | 0 | 0 | 0 | 2018-05-11 22:00 | 22 | 6 | 32.971 | 6.8873 | 0
2018-05-11 23:00 | 23 | 6 | 86.4012 | 18.0483 | 0 | 2018-05-11 23:00 | 23 | 6 | 86.7918 | 18.1299 | 0 | 2018-05-11 23:00 | 23 | 6 | 0 | 0 | 0 | 2018-05-11 23:00 | 23 | 6 | 32.9809 | 6.8894 | 0
2018-05-12 | 0 | 7 | 86.0121 | 17.9671 | 0 | 2018-05-12 | 0 | 7 | 0 | 0 | 0 | 2018-05-12 | 0 | 7 | 86.5507 | 18.0796 | 0 | 2018-05-12 | 0 | 7 | 32.8893 | 6.8702 | 0
2018-05-12 01:00 | 1 | 7 | 85.919 | 17.9476 | 0 | 2018-05-12 01:00 | 1 | 7 | 0 | 0 | 0 | 2018-05-12 01:00 | 1 | 7 | 86.5324 | 18.0758 | 0 | 2018-05-12 01:00 | 1 | 7 | 32.8823 | 6.8688 | 0
2018-05-12 02:00 | 2 | 7 | 86.0533 | 17.9757 | 0 | 2018-05-12 02:00 | 2 | 7 | 0 | 0 | 0 | 2018-05-12 02:00 | 2 | 7 | 86.6453 | 18.0993 | 0 | 2018-05-12 02:00 | 2 | 7 | 32.9252 | 6.8777 | 0
2018-05-12 03:00 | 3 | 7 | 86.1677 | 17.9996 | 0 | 2018-05-12 03:00 | 3 | 7 | 0 | 0 | 0 | 2018-05-12 03:00 | 3 | 7 | 86.7002 | 18.1108 | 0 | 2018-05-12 03:00 | 3 | 7 | 32.9461 | 6.8821 | 0
2018-05-12 04:00 | 4 | 7 | 86.3081 | 18.0289 | 0 | 2018-05-12 04:00 | 4 | 7 | 0 | 0 | 0 | 2018-05-12 04:00 | 4 | 7 | 86.8513 | 18.1424 | 0 | 2018-05-12 04:00 | 4 | 7 | 33.0035 | 6.8941 | 0
2018-05-12 05:00 | 5 | 7 | 86.2562 | 18.0181 | 0 | 2018-05-12 05:00 | 5 | 7 | 0 | 0 | 0 | 2018-05-12 05:00 | 5 | 7 | 86.8605 | 18.1443 | 0 | 2018-05-12 05:00 | 5 | 7 | 33.007 | 6.8948 | 0
2018-05-12 06:00 | 6 | 7 | 86.1234 | 17.9903 | 0 | 2018-05-12 06:00 | 6 | 7 | 0 | 0 | 0 | 2018-05-12 06:00 | 6 | 7 | 86.6682 | 18.1041 | 0 | 2018-05-12 06:00 | 6 | 7 | 32.9339 | 6.8796 | 0
2018-05-12 07:00 | 7 | 7 | 86.1906 | 18.0044 | 0 | 2018-05-12 07:00 | 7 | 7 | 0 | 0 | 0 | 2018-05-12 07:00 | 7 | 7 | 86.7247 | 18.1159 | 0 | 2018-05-12 07:00 | 7 | 7 | 32.9554 | 6.8841 | 0
2018-05-12 08:00 | 8 | 7 | 86.36 | 18.0397 | 0 | 2018-05-12 08:00 | 8 | 7 | 0 | 0 | 0 | 2018-05-12 08:00 | 8 | 7 | 86.952 | 18.1634 | 0 | 2018-05-12 08:00 | 8 | 7 | 33.0418 | 6.9021 | 0
2018-05-12 09:00 | 9 | 7 | 86.4912 | 18.0671 | 0 | 2018-05-12 09:00 | 9 | 7 | 0 | 0 | 0 | 2018-05-12 09:00 | 9 | 7 | 87.0588 | 18.1857 | 0 | 2018-05-12 09:00 | 9 | 7 | 33.0823 | 6.9106 | 0
2018-05-12 10:00 | 10 | 7 | 86.1982 | 18.0059 | 0 | 2018-05-12 10:00 | 10 | 7 | 0 | 0 | 0 | 2018-05-12 10:00 | 10 | 7 | 86.6392 | 18.0981 | 0 | 2018-05-12 10:00 | 10 | 7 | 32.9229 | 6.8773 | 0
2018-05-12 11:00 | 11 | 7 | 86.1707 | 18.0002 | 0 | 2018-05-12 11:00 | 11 | 7 | 0 | 0 | 0 | 2018-05-12 11:00 | 11 | 7 | 86.8849 | 18.1494 | 0 | 2018-05-12 11:00 | 11 | 7 | 33.0163 | 6.8968 | 0
2018-05-12 12:00 | 12 | 7 | 86.5019 | 18.0694 | 0 | 2018-05-12 12:00 | 12 | 7 | 0 | 0 | 0 | 2018-05-12 12:00 | 12 | 7 | 87.1504 | 18.2048 | 0 | 2018-05-12 12:00 | 12 | 7 | 33.1172 | 6.9178 | 0
2018-05-12 13:00 | 13 | 7 | 86.6148 | 18.093 | 0 | 2018-05-12 13:00 | 13 | 7 | 0 | 0 | 0 | 2018-05-12 13:00 | 13 | 7 | 87.3167 | 18.2396 | 0 | 2018-05-12 13:00 | 13 | 7 | 33.1803 | 6.931 | 0
2018-05-12 14:00 | 14 | 7 | 86.4439 | 18.0573 | 0 | 2018-05-12 14:00 | 14 | 7 | 0 | 0 | 0 | 2018-05-12 14:00 | 14 | 7 | 87.0832 | 18.1908 | 0 | 2018-05-12 14:00 | 14 | 7 | 33.0916 | 6.9125 | 0
2018-05-12 15:00 | 15 | 7 | 86.5522 | 18.0799 | 0 | 2018-05-12 15:00 | 15 | 7 | 0 | 0 | 0 | 2018-05-12 15:00 | 15 | 7 | 87.2938 | 18.2348 | 0 | 2018-05-12 15:00 | 15 | 7 | 33.1716 | 6.9292 | 0
2018-05-12 16:00 | 16 | 7 | 86.5644 | 18.0824 | 0 | 2018-05-12 16:00 | 16 | 7 | 0 | 0 | 0 | 2018-05-12 16:00 | 16 | 7 | 87.3579 | 18.2482 | 0 | 2018-05-12 16:00 | 16 | 7 | 33.196 | 6.9343 | 0
2018-05-12 17:00 | 17 | 7 | 86.7445 | 18.1201 | 0 | 2018-05-12 17:00 | 17 | 7 | 0 | 0 | 0 | 2018-05-12 17:00 | 17 | 7 | 87.57 | 18.2925 | 0 | 2018-05-12 17:00 | 17 | 7 | 33.2766 | 6.9511 | 0
2018-05-12 18:00 | 18 | 7 | 86.4668 | 18.062 | 0 | 2018-05-12 18:00 | 18 | 7 | 0 | 0 | 0 | 2018-05-12 18:00 | 18 | 7 | 87.3014 | 18.2364 | 0 | 2018-05-12 18:00 | 18 | 7 | 33.1745 | 6.9298 | 0
2018-05-12 19:00 | 19 | 7 | 86.3661 | 18.041 | 0 | 2018-05-12 19:00 | 19 | 7 | 0 | 0 | 0 | 2018-05-12 19:00 | 19 | 7 | 87.0954 | 18.1934 | 0 | 2018-05-12 19:00 | 19 | 7 | 33.0963 | 6.9135 | 0
2018-05-12 20:00 | 20 | 7 | 86.1173 | 17.989 | 0 | 2018-05-12 20:00 | 20 | 7 | 0 | 0 | 0 | 2018-05-12 20:00 | 20 | 7 | 86.891 | 18.1507 | 0 | 2018-05-12 20:00 | 20 | 7 | 33.0186 | 6.8973 | 0
2018-05-12 21:00 | 21 | 7 | 86.1555 | 17.997 | 0 | 2018-05-12 21:00 | 21 | 7 | 0 | 0 | 0 | 2018-05-12 21:00 | 21 | 7 | 86.9245 | 18.1577 | 0 | 2018-05-12 21:00 | 21 | 7 | 33.0313 | 6.8999 | 0
2018-05-12 22:00 | 22 | 7 | 86.2211 | 18.0107 | 0 | 2018-05-12 22:00 | 22 | 7 | 0 | 0 | 0 | 2018-05-12 22:00 | 22 | 7 | 87.0054 | 18.1746 | 0 | 2018-05-12 22:00 | 22 | 7 | 33.0621 | 6.9063 | 0
2018-05-12 23:00 | 23 | 7 | 86.2226 | 18.011 | 0 | 2018-05-12 23:00 | 23 | 7 | 0 | 0 | 0 | 2018-05-12 23:00 | 23 | 7 | 87.0787 | 18.1899 | 0 | 2018-05-12 23:00 | 23 | 7 | 33.0899 | 6.9122 | 0
2018-05-13 | 0 | 1 | 86.2364 | 18.0139 | 0 | 2018-05-13 | 0 | 1 | 86.7994 | 18.1315 | 0 | 2018-05-13 | 0 | 1 | 0 | 0 | 0 | 2018-05-13 | 0 | 1 | 32.9838 | 6.89 | 0
2018-05-13 01:00 | 1 | 1 | 86.3188 | 18.0311 | 0 | 2018-05-13 01:00 | 1 | 1 | 86.952 | 18.1634 | 0 | 2018-05-13 01:00 | 1 | 1 | 0 | 0 | 0 | 2018-05-13 01:00 | 1 | 1 | 33.0418 | 6.9021 | 0
2018-05-13 02:00 | 2 | 1 | 86.2119 | 18.0088 | 0 | 2018-05-13 02:00 | 2 | 1 | 86.8177 | 18.1353 | 0 | 2018-05-13 02:00 | 2 | 1 | 0 | 0 | 0 | 2018-05-13 02:00 | 2 | 1 | 32.9907 | 6.8914 | 0
2018-05-13 03:00 | 3 | 1 | 86.1845 | 18.0031 | 0 | 2018-05-13 03:00 | 3 | 1 | 86.7857 | 18.1287 | 0 | 2018-05-13 03:00 | 3 | 1 | 0 | 0 | 0 | 2018-05-13 03:00 | 3 | 1 | 32.9786 | 6.8889 | 0
2018-05-13 04:00 | 4 | 1 | 86.2455 | 18.0158 | 0 | 2018-05-13 04:00 | 4 | 1 | 86.833 | 18.1385 | 0 | 2018-05-13 04:00 | 4 | 1 | 0 | 0 | 0 | 2018-05-13 04:00 | 4 | 1 | 32.9965 | 6.8926 | 0
2018-05-13 05:00 | 5 | 1 | 86.2333 | 18.0133 | 0 | 2018-05-13 05:00 | 5 | 1 | 86.833 | 18.1385 | 0 | 2018-05-13 05:00 | 5 | 1 | 0 | 0 | 0 | 2018-05-13 05:00 | 5 | 1 | 32.9965 | 6.8926 | 0
2018-05-13 06:00 | 6 | 1 | 86.2776 | 18.0225 | 0 | 2018-05-13 06:00 | 6 | 1 | 86.8528 | 18.1427 | 0 | 2018-05-13 06:00 | 6 | 1 | 0 | 0 | 0 | 2018-05-13 06:00 | 6 | 1 | 33.0041 | 6.8942 | 0
2018-05-13 07:00 | 7 | 1 | 86.2867 | 18.0244 | 0 | 2018-05-13 07:00 | 7 | 1 | 86.8452 | 18.1411 | 0 | 2018-05-13 07:00 | 7 | 1 | 0 | 0 | 0 | 2018-05-13 07:00 | 7 | 1 | 33.0012 | 6.8936 | 0
2018-05-13 08:00 | 8 | 1 | 86.2989 | 18.027 | 0 | 2018-05-13 08:00 | 8 | 1 | 86.9032 | 18.1532 | 0 | 2018-05-13 08:00 | 8 | 1 | 0 | 0 | 0 | 2018-05-13 08:00 | 8 | 1 | 33.0232 | 6.8982 | 0
2018-05-13 09:00 | 9 | 1 | 86.2867 | 18.0244 | 0 | 2018-05-13 09:00 | 9 | 1 | 86.8162 | 18.135 | 0 | 2018-05-13 09:00 | 9 | 1 | 0 | 0 | 0 | 2018-05-13 09:00 | 9 | 1 | 32.9902 | 6.8913 | 0
2018-05-13 10:00 | 10 | 1 | 86.2882 | 18.0247 | 0 | 2018-05-13 10:00 | 10 | 1 | 86.8528 | 18.1427 | 0 | 2018-05-13 10:00 | 10 | 1 | 0 | 0 | 0 | 2018-05-13 10:00 | 10 | 1 | 33.0041 | 6.8942 | 0
2018-05-13 11:00 | 11 | 1 | 86.1845 | 18.0031 | 0 | 2018-05-13 11:00 | 11 | 1 | 86.743 | 18.1197 | 0 | 2018-05-13 11:00 | 11 | 1 | 0 | 0 | 0 | 2018-05-13 11:00 | 11 | 1 | 32.9623 | 6.8855 | 0
2018-05-13 12:00 | 12 | 1 | 86.1418 | 17.9942 | 0 | 2018-05-13 12:00 | 12 | 1 | 86.714 | 18.1137 | 0 | 2018-05-13 12:00 | 12 | 1 | 0 | 0 | 0 | 2018-05-13 12:00 | 12 | 1 | 32.9513 | 6.8832 | 0
2018-05-13 13:00 | 13 | 1 | 86.1479 | 17.9954 | 0 | 2018-05-13 13:00 | 13 | 1 | 86.7659 | 18.1245 | 0 | 2018-05-13 13:00 | 13 | 1 | 0 | 0 | 0 | 2018-05-13 13:00 | 13 | 1 | 32.971 | 6.8873 | 0
2018-05-13 14:00 | 14 | 1 | 86.1112 | 17.9878 | 0 | 2018-05-13 14:00 | 14 | 1 | 86.7018 | 18.1111 | 0 | 2018-05-13 14:00 | 14 | 1 | 0 | 0 | 0 | 2018-05-13 14:00 | 14 | 1 | 32.9467 | 6.8822 | 0
2018-05-13 15:00 | 15 | 1 | 86.2455 | 18.0158 | 0 | 2018-05-13 15:00 | 15 | 1 | 86.8482 | 18.1417 | 0 | 2018-05-13 15:00 | 15 | 1 | 0 | 0 | 0 | 2018-05-13 15:00 | 15 | 1 | 33.0023 | 6.8939 | 0
2018-05-13 16:00 | 16 | 1 | 86.3447 | 18.0365 | 0 | 2018-05-13 16:00 | 16 | 1 | 86.9398 | 18.1609 | 0 | 2018-05-13 16:00 | 16 | 1 | 0 | 0 | 0 | 2018-05-13 16:00 | 16 | 1 | 33.0371 | 6.9011 | 0
2018-05-13 17:00 | 17 | 1 | 86.4805 | 18.0649 | 0 | 2018-05-13 17:00 | 17 | 1 | 86.9856 | 18.1704 | 0 | 2018-05-13 17:00 | 17 | 1 | 0 | 0 | 0 | 2018-05-13 17:00 | 17 | 1 | 33.0545 | 6.9048 | 0
2018-05-13 18:00 | 18 | 1 | 86.4332 | 18.055 | 0 | 2018-05-13 18:00 | 18 | 1 | 86.92 | 18.1567 | 0 | 2018-05-13 18:00 | 18 | 1 | 0 | 0 | 0 | 2018-05-13 18:00 | 18 | 1 | 33.0296 | 6.8996 | 0
2018-05-13 19:00 | 19 | 1 | 85.6794 | 17.8976 | 0 | 2018-05-13 19:00 | 19 | 1 | 85.9266 | 17.9492 | 0 | 2018-05-13 19:00 | 19 | 1 | 0 | 0 | 0 | 2018-05-13 19:00 | 19 | 1 | 32.6521 | 6.8207 | 0
2018-05-13 20:00 | 20 | 1 | 86.3294 | 18.0333 | 0 | 2018-05-13 20:00 | 20 | 1 | 86.5888 | 18.0875 | 0 | 2018-05-13 20:00 | 20 | 1 | 0 | 0 | 0 | 2018-05-13 20:00 | 20 | 1 | 32.9037 | 6.8733 | 0
2018-05-13 21:00 | 21 | 1 | 86.3569 | 18.0391 | 0 | 2018-05-13 21:00 | 21 | 1 | 86.6728 | 18.1051 | 0 | 2018-05-13 21:00 | 21 | 1 | 0 | 0 | 0 | 2018-05-13 21:00 | 21 | 1 | 32.9357 | 6.8799 | 0
2018-05-13 22:00 | 22 | 1 | 86.4881 | 18.0665 | 0 | 2018-05-13 22:00 | 22 | 1 | 86.8086 | 18.1334 | 0 | 2018-05-13 22:00 | 22 | 1 | 0 | 0 | 0 | 2018-05-13 22:00 | 22 | 1 | 32.9873 | 6.8907 | 0
2018-05-13 23:00 | 23 | 1 | 86.4332 | 18.055 | 0 | 2018-05-13 23:00 | 23 | 1 | 86.7353 | 18.1181 | 0 | 2018-05-13 23:00 | 23 | 1 | 0 | 0 | 0 | 2018-05-13 23:00 | 23 | 1 | 32.9594 | 6.8849 | 0
2018-05-14 | 0 | 2 | 86.4088 | 18.0499 | 0 | 2018-05-14 | 0 | 2 | 86.7002 | 18.1108 | 0 | 2018-05-14 | 0 | 2 | 86.9352 | 18.1599 | 0 | 2018-05-14 | 0 | 2 | 65.9815 | 13.7829 | 0
2018-05-14 01:00 | 1 | 2 | 86.0426 | 17.9734 | 0 | 2018-05-14 01:00 | 1 | 2 | 86.3127 | 18.0299 | 0 | 2018-05-14 01:00 | 1 | 2 | 86.5278 | 18.0748 | 0 | 2018-05-14 01:00 | 1 | 2 | 65.6794 | 13.7198 | 0
2018-05-14 02:00 | 2 | 2 | 86.392 | 18.0464 | 0 | 2018-05-14 02:00 | 2 | 2 | 86.6392 | 18.0981 | 0 | 2018-05-14 02:00 | 2 | 2 | 86.8421 | 18.1404 | 0 | 2018-05-14 02:00 | 2 | 2 | 65.9229 | 13.7706 | 0
2018-05-14 03:00 | 3 | 2 | 86.2776 | 18.0225 | 0 | 2018-05-14 03:00 | 3 | 2 | 86.5766 | 18.085 | 0 | 2018-05-14 03:00 | 3 | 2 | 86.7536 | 18.122 | 0 | 2018-05-14 03:00 | 3 | 2 | 65.8655 | 13.7586 | 0
2018-05-14 04:00 | 4 | 2 | 86.5034 | 18.0697 | 0 | 2018-05-14 04:00 | 4 | 2 | 86.8849 | 18.1494 | 0 | 2018-05-14 04:00 | 4 | 2 | 87.0283 | 18.1793 | 0 | 2018-05-14 04:00 | 4 | 2 | 66.087 | 13.8049 | 0
2018-05-14 05:00 | 5 | 2 | 86.3661 | 18.041 | 0 | 2018-05-14 05:00 | 5 | 2 | 86.772 | 18.1258 | 0 | 2018-05-14 05:00 | 5 | 2 | 87.0054 | 18.1746 | 0 | 2018-05-14 05:00 | 5 | 2 | 66.0354 | 13.7941 | 0
2018-05-14 06:00 | 6 | 2 | 86.2898 | 18.0251 | 0 | 2018-05-14 06:00 | 6 | 2 | 86.6499 | 18.1003 | 0 | 2018-05-14 06:00 | 6 | 2 | 86.8147 | 18.1347 | 0 | 2018-05-14 06:00 | 6 | 2 | 65.9165 | 13.7693 | 0
2018-05-14 07:00 | 7 | 2 | 86.2043 | 18.0072 | 0 | 2018-05-14 07:00 | 7 | 2 | 86.5278 | 18.0748 | 0 | 2018-05-14 07:00 | 7 | 2 | 86.7079 | 18.1124 | 0 | 2018-05-14 07:00 | 7 | 2 | 65.8296 | 13.7511 | 0
2018-05-14 08:00 | 8 | 2 | 86.3355 | 18.0346 | 0 | 2018-05-14 08:00 | 8 | 2 | 86.5461 | 18.0786 | 0 | 2018-05-14 08:00 | 8 | 2 | 86.8025 | 18.1322 | 0 | 2018-05-14 08:00 | 8 | 2 | 65.8725 | 13.7601 | 0
2018-05-14 09:00 | 9 | 2 | 86.3798 | 18.0439 | 0 | 2018-05-14 09:00 | 9 | 2 | 86.7262 | 18.1162 | 0 | 2018-05-14 09:00 | 9 | 2 | 86.8711 | 18.1465 | 0 | 2018-05-14 09:00 | 9 | 2 | 65.967 | 13.7798 | 0
2018-05-14 10:00 | 10 | 2 | 86.2272 | 18.012 | 0 | 2018-05-14 10:00 | 10 | 2 | 86.5156 | 18.0722 | 0 | 2018-05-14 10:00 | 10 | 2 | 86.714 | 18.1137 | 0 | 2018-05-14 10:00 | 10 | 2 | 65.8272 | 13.7507 | 0
2018-05-14 11:00 | 11 | 2 | 86.2119 | 18.0088 | 0 | 2018-05-14 11:00 | 11 | 2 | 86.5141 | 18.0719 | 0 | 2018-05-14 11:00 | 11 | 2 | 86.7201 | 18.115 | 0 | 2018-05-14 11:00 | 11 | 2 | 65.829 | 13.751 | 0
2018-05-14 12:00 | 12 | 2 | 86.389 | 18.0458 | 0 | 2018-05-14 12:00 | 12 | 2 | 86.6835 | 18.1073 | 0 | 2018-05-14 12:00 | 12 | 2 | 86.8574 | 18.1436 | 0 | 2018-05-14 12:00 | 12 | 2 | 65.9455 | 13.7754 | 0
2018-05-14 13:00 | 13 | 2 | 86.4027 | 18.0487 | 0 | 2018-05-14 13:00 | 13 | 2 | 86.6224 | 18.0946 | 0 | 2018-05-14 13:00 | 13 | 2 | 86.7475 | 18.1207 | 0 | 2018-05-14 13:00 | 13 | 2 | 65.8806 | 13.7618 | 0
2018-05-14 14:00 | 14 | 2 | 86.3783 | 18.0436 | 0 | 2018-05-14 14:00 | 14 | 2 | 86.6606 | 18.1025 | 0 | 2018-05-14 14:00 | 14 | 2 | 86.7903 | 18.1296 | 0 | 2018-05-14 14:00 | 14 | 2 | 65.9113 | 13.7682 | 0
2018-05-14 15:00 | 15 | 2 | 86.3355 | 18.0346 | 0 | 2018-05-14 15:00 | 15 | 2 | 86.5248 | 18.0742 | 0 | 2018-05-14 15:00 | 15 | 2 | 86.7384 | 18.1188 | 0 | 2018-05-14 15:00 | 15 | 2 | 65.84 | 13.7533 | 0
2018-05-14 16:00 | 16 | 2 | 86.3493 | 18.0375 | 0 | 2018-05-14 16:00 | 16 | 2 | 86.4912 | 18.0671 | 0 | 2018-05-14 16:00 | 16 | 2 | 86.685 | 18.1076 | 0 | 2018-05-14 16:00 | 16 | 2 | 65.807 | 13.7464 | 0
2018-05-14 17:00 | 17 | 2 | 86.244 | 18.0155 | 0 | 2018-05-14 17:00 | 17 | 2 | 86.4683 | 18.0624 | 0 | 2018-05-14 17:00 | 17 | 2 | 86.6743 | 18.1054 | 0 | 2018-05-14 17:00 | 17 | 2 | 65.7942 | 13.7437 | 0
2018-05-14 18:00 | 18 | 2 | 86.3142 | 18.0302 | 0 | 2018-05-14 18:00 | 18 | 2 | 86.4378 | 18.056 | 0 | 2018-05-14 18:00 | 18 | 2 | 86.5934 | 18.0885 | 0 | 2018-05-14 18:00 | 18 | 2 | 65.7519 | 13.7349 | 0
2018-05-14 19:00 | 19 | 2 | 86.2089 | 18.0082 | 0 | 2018-05-14 19:00 | 19 | 2 | 86.3508 | 18.0378 | 0 | 2018-05-14 19:00 | 19 | 2 | 86.5583 | 18.0812 | 0 | 2018-05-14 19:00 | 19 | 2 | 65.7055 | 13.7252 | 0
2018-05-14 20:00 | 20 | 2 | 86.2181 | 18.0101 | 0 | 2018-05-14 20:00 | 20 | 2 | 86.4836 | 18.0656 | 0 | 2018-05-14 20:00 | 20 | 2 | 86.6896 | 18.1086 | 0 | 2018-05-14 20:00 | 20 | 2 | 65.8058 | 13.7462 | 0
2018-05-14 21:00 | 21 | 2 | 86.1494 | 17.9957 | 0 | 2018-05-14 21:00 | 21 | 2 | 86.4759 | 18.064 | 0 | 2018-05-14 21:00 | 21 | 2 | 86.63 | 18.0961 | 0 | 2018-05-14 21:00 | 21 | 2 | 65.7802 | 13.7408 | 0
2018-05-14 22:00 | 22 | 2 | 86.2593 | 18.0187 | 0 | 2018-05-14 22:00 | 22 | 2 | 86.5522 | 18.0799 | 0 | 2018-05-14 22:00 | 22 | 2 | 86.6468 | 18.0997 | 0 | 2018-05-14 22:00 | 22 | 2 | 65.8156 | 13.7482 | 0
2018-05-14 23:00 | 23 | 2 | 86.4424 | 18.057 | 0 | 2018-05-14 23:00 | 23 | 2 | 86.8055 | 18.1328 | 0 | 2018-05-14 23:00 | 23 | 2 | 86.8864 | 18.1497 | 0 | 2018-05-14 23:00 | 23 | 2 | 66.0029 | 13.7874 | 0
2018-05-15 | 0 | 3 | 86.4637 | 18.0614 | 0 | 2018-05-15 | 0 | 3 | 0 | 0 | 0 | 2018-05-15 | 0 | 3 | 0 | 0 | 0 | 2018-05-15 | 0 | 3 | 0 | 0 | 0
2018-05-15 01:00 | 1 | 3 | 86.5629 | 18.0821 | 0 | 2018-05-15 01:00 | 1 | 3 | 0 | 0 | 0 | 2018-05-15 01:00 | 1 | 3 | 0 | 0 | 0 | 2018-05-15 01:00 | 1 | 3 | 0 | 0 | 0
2018-05-15 02:00 | 2 | 3 | 86.3706 | 18.042 | 0 | 2018-05-15 02:00 | 2 | 3 | 0 | 0 | 0 | 2018-05-15 02:00 | 2 | 3 | 0 | 0 | 0 | 2018-05-15 02:00 | 2 | 3 | 0 | 0 | 0
2018-05-15 03:00 | 3 | 3 | 86.3523 | 18.0381 | 0 | 2018-05-15 03:00 | 3 | 3 | 0 | 0 | 0 | 2018-05-15 03:00 | 3 | 3 | 0 | 0 | 0 | 2018-05-15 03:00 | 3 | 3 | 0 | 0 | 0
2018-05-15 04:00 | 4 | 3 | 86.3676 | 18.0413 | 0 | 2018-05-15 04:00 | 4 | 3 | 0 | 0 | 0 | 2018-05-15 04:00 | 4 | 3 | 0 | 0 | 0 | 2018-05-15 04:00 | 4 | 3 | 0 | 0 | 0
2018-05-15 05:00 | 5 | 3 | 86.4027 | 18.0487 | 0 | 2018-05-15 05:00 | 5 | 3 | 0 | 0 | 0 | 2018-05-15 05:00 | 5 | 3 | 0 | 0 | 0 | 2018-05-15 05:00 | 5 | 3 | 0 | 0 | 0
2018-05-15 06:00 | 6 | 3 | 86.4652 | 18.0617 | 0 | 2018-05-15 06:00 | 6 | 3 | 0 | 0 | 0 | 2018-05-15 06:00 | 6 | 3 | 0 | 0 | 0 | 2018-05-15 06:00 | 6 | 3 | 0 | 0 | 0
2018-05-15 07:00 | 7 | 3 | 86.4012 | 18.0483 | 0 | 2018-05-15 07:00 | 7 | 3 | 0 | 0 | 0 | 2018-05-15 07:00 | 7 | 3 | 0 | 0 | 0 | 2018-05-15 07:00 | 7 | 3 | 0 | 0 | 0
2018-05-15 08:00 | 8 | 3 | 86.4515 | 18.0589 | 0 | 2018-05-15 08:00 | 8 | 3 | 0 | 0 | 0 | 2018-05-15 08:00 | 8 | 3 | 0 | 0 | 0 | 2018-05-15 08:00 | 8 | 3 | 0 | 0 | 0
2018-05-15 09:00 | 9 | 3 | 86.2028 | 18.0069 | 0 | 2018-05-15 09:00 | 9 | 3 | 0 | 0 | 0 | 2018-05-15 09:00 | 9 | 3 | 0 | 0 | 0 | 2018-05-15 09:00 | 9 | 3 | 0 | 0 | 0
2018-05-15 10:00 | 10 | 3 | 86.2715 | 18.0213 | 0 | 2018-05-15 10:00 | 10 | 3 | 0 | 0 | 0 | 2018-05-15 10:00 | 10 | 3 | 0 | 0 | 0 | 2018-05-15 10:00 | 10 | 3 | 0 | 0 | 0
2018-05-15 11:00 | 11 | 3 | 86.7567 | 18.1226 | 0 | 2018-05-15 11:00 | 11 | 3 | 0 | 0 | 0 | 2018-05-15 11:00 | 11 | 3 | 0 | 0 | 0 | 2018-05-15 11:00 | 11 | 3 | 0 | 0 | 0
2018-05-15 12:00 | 12 | 3 | 86.6194 | 18.0939 | 0 | 2018-05-15 12:00 | 12 | 3 | 0 | 0 | 0 | 2018-05-15 12:00 | 12 | 3 | 0 | 0 | 0 | 2018-05-15 12:00 | 12 | 3 | 0 | 0 | 0
2018-05-15 13:00 | 13 | 3 | 86.6377 | 18.0977 | 0 | 2018-05-15 13:00 | 13 | 3 | 0 | 0 | 0 | 2018-05-15 13:00 | 13 | 3 | 0 | 0 | 0 | 2018-05-15 13:00 | 13 | 3 | 0 | 0 | 0
2018-05-15 14:00 | 14 | 3 | 86.8757 | 18.1475 | 0 | 2018-05-15 14:00 | 14 | 3 | 0 | 0 | 0 | 2018-05-15 14:00 | 14 | 3 | 0 | 0 | 0 | 2018-05-15 14:00 | 14 | 3 | 0 | 0 | 0
2018-05-15 15:00 | 15 | 3 | 86.7994 | 18.1315 | 0 | 2018-05-15 15:00 | 15 | 3 | 0 | 0 | 0 | 2018-05-15 15:00 | 15 | 3 | 0 | 0 | 0 | 2018-05-15 15:00 | 15 | 3 | 0 | 0 | 0
2018-05-15 16:00 | 16 | 3 | 86.7674 | 18.1248 | 0 | 2018-05-15 16:00 | 16 | 3 | 0 | 0 | 0 | 2018-05-15 16:00 | 16 | 3 | 0 | 0 | 0 | 2018-05-15 16:00 | 16 | 3 | 0 | 0 | 0
2018-05-15 17:00 | 17 | 3 | 86.7384 | 18.1188 | 0 | 2018-05-15 17:00 | 17 | 3 | 0 | 0 | 0 | 2018-05-15 17:00 | 17 | 3 | 0 | 0 | 0 | 2018-05-15 17:00 | 17 | 3 | 0 | 0 | 0
2018-05-15 18:00 | 18 | 3 | 86.7124 | 18.1134 | 0 | 2018-05-15 18:00 | 18 | 3 | 0 | 0 | 0 | 2018-05-15 18:00 | 18 | 3 | 0 | 0 | 0 | 2018-05-15 18:00 | 18 | 3 | 0 | 0 | 0
2018-05-15 19:00 | 19 | 3 | 86.8376 | 18.1395 | 0 | 2018-05-15 19:00 | 19 | 3 | 0 | 0 | 0 | 2018-05-15 19:00 | 19 | 3 | 0 | 0 | 0 | 2018-05-15 19:00 | 19 | 3 | 0 | 0 | 0
2018-05-15 20:00 | 20 | 3 | 86.627 | 18.0955 | 0 | 2018-05-15 20:00 | 20 | 3 | 0 | 0 | 0 | 2018-05-15 20:00 | 20 | 3 | 0 | 0 | 0 | 2018-05-15 20:00 | 20 | 3 | 0 | 0 | 0
2018-05-15 21:00 | 21 | 3 | 86.6239 | 18.0949 | 0 | 2018-05-15 21:00 | 21 | 3 | 0 | 0 | 0 | 2018-05-15 21:00 | 21 | 3 | 0 | 0 | 0 | 2018-05-15 21:00 | 21 | 3 | 0 | 0 | 0
2018-05-15 22:00 | 22 | 3 | 86.714 | 18.1137 | 0 | 2018-05-15 22:00 | 22 | 3 | 0 | 0 | 0 | 2018-05-15 22:00 | 22 | 3 | 0 | 0 | 0 | 2018-05-15 22:00 | 22 | 3 | 0 | 0 | 0
2018-05-15 23:00 | 23 | 3 | 86.8971 | 18.1519 | 0 | 2018-05-15 23:00 | 23 | 3 | 0 | 0 | 0 | 2018-05-15 23:00 | 23 | 3 | 0 | 0 | 0 | 2018-05-15 23:00 | 23 | 3 | 0 | 0 | 0
2018-05-16 | 0 | 4 | 0 | 0 | 0 | 2018-05-16 | 0 | 4 | 0 | 0 | 0 | 2018-05-16 | 0 | 4 | 86.6712 | 18.1047 | 0 | 2018-05-16 | 0 | 4 | 32.9351 | 6.8798 | 0
2018-05-16 01:00 | 1 | 4 | 0 | 0 | 0 | 2018-05-16 01:00 | 1 | 4 | 0 | 0 | 0 | 2018-05-16 01:00 | 1 | 4 | 86.511 | 18.0713 | 0 | 2018-05-16 01:00 | 1 | 4 | 32.8742 | 6.8671 | 0
2018-05-16 02:00 | 2 | 4 | 0 | 0 | 0 | 2018-05-16 02:00 | 2 | 4 | 0 | 0 | 0 | 2018-05-16 02:00 | 2 | 4 | 86.7628 | 18.1239 | 0 | 2018-05-16 02:00 | 2 | 4 | 32.9699 | 6.8871 | 0
2018-05-16 03:00 | 3 | 4 | 0 | 0 | 0 | 2018-05-16 03:00 | 3 | 4 | 0 | 0 | 0 | 2018-05-16 03:00 | 3 | 4 | 86.7384 | 18.1188 | 0 | 2018-05-16 03:00 | 3 | 4 | 32.9606 | 6.8851 | 0
2018-05-16 04:00 | 4 | 4 | 0 | 0 | 0 | 2018-05-16 04:00 | 4 | 4 | 0 | 0 | 0 | 2018-05-16 04:00 | 4 | 4 | 86.8376 | 18.1395 | 0 | 2018-05-16 04:00 | 4 | 4 | 32.9983 | 6.893 | 0
2018-05-16 05:00 | 5 | 4 | 0 | 0 | 0 | 2018-05-16 05:00 | 5 | 4 | 0 | 0 | 0 | 2018-05-16 05:00 | 5 | 4 | 87.0222 | 18.1781 | 0 | 2018-05-16 05:00 | 5 | 4 | 33.0684 | 6.9077 | 0
2018-05-16 06:00 | 6 | 4 | 0 | 0 | 0 | 2018-05-16 06:00 | 6 | 4 | 0 | 0 | 0 | 2018-05-16 06:00 | 6 | 4 | 86.9627 | 18.1656 | 0 | 2018-05-16 06:00 | 6 | 4 | 33.0458 | 6.9029 | 0
2018-05-16 07:00 | 7 | 4 | 0 | 0 | 0 | 2018-05-16 07:00 | 7 | 4 | 0 | 0 | 0 | 2018-05-16 07:00 | 7 | 4 | 87.1321 | 18.201 | 0 | 2018-05-16 07:00 | 7 | 4 | 33.1102 | 6.9164 | 0
2018-05-16 08:00 | 8 | 4 | 0 | 0 | 0 | 2018-05-16 08:00 | 8 | 4 | 0 | 0 | 0 | 2018-05-16 08:00 | 8 | 4 | 87.1931 | 18.2138 | 0 | 2018-05-16 08:00 | 8 | 4 | 33.1334 | 6.9212 | 0
2018-05-16 09:00 | 9 | 4 | 0 | 0 | 0 | 2018-05-16 09:00 | 9 | 4 | 0 | 0 | 0 | 2018-05-16 09:00 | 9 | 4 | 86.7155 | 18.114 | 0 | 2018-05-16 09:00 | 9 | 4 | 32.9519 | 6.8833 | 0
2018-05-16 10:00 | 10 | 4 | 0 | 0 | 0 | 2018-05-16 10:00 | 10 | 4 | 0 | 0 | 0 | 2018-05-16 10:00 | 10 | 4 | 86.6743 | 18.1054 | 0 | 2018-05-16 10:00 | 10 | 4 | 32.9362 | 6.88 | 0
2018-05-16 11:00 | 11 | 4 | 0 | 0 | 0 | 2018-05-16 11:00 | 11 | 4 | 0 | 0 | 0 | 2018-05-16 11:00 | 11 | 4 | 86.8956 | 18.1516 | 0 | 2018-05-16 11:00 | 11 | 4 | 33.0203 | 6.8976 | 0
2018-05-16 12:00 | 12 | 4 | 0 | 0 | 0 | 2018-05-16 12:00 | 12 | 4 | 0 | 0 | 0 | 2018-05-16 12:00 | 12 | 4 | 86.9276 | 18.1583 | 0 | 2018-05-16 12:00 | 12 | 4 | 33.0325 | 6.9002 | 0
2018-05-16 13:00 | 13 | 4 | 0 | 0 | 0 | 2018-05-16 13:00 | 13 | 4 | 0 | 0 | 0 | 2018-05-16 13:00 | 13 | 4 | 87.2541 | 18.2265 | 0 | 2018-05-16 13:00 | 13 | 4 | 33.1566 | 6.9261 | 0
2018-05-16 14:00 | 14 | 4 | 0 | 0 | 0 | 2018-05-16 14:00 | 14 | 4 | 0 | 0 | 0 | 2018-05-16 14:00 | 14 | 4 | 87.4037 | 18.2578 | 0 | 2018-05-16 14:00 | 14 | 4 | 33.2134 | 6.9379 | 0
2018-05-16 15:00 | 15 | 4 | 0 | 0 | 0 | 2018-05-16 15:00 | 15 | 4 | 0 | 0 | 0 | 2018-05-16 15:00 | 15 | 4 | 87.2129 | 18.2179 | 0 | 2018-05-16 15:00 | 15 | 4 | 33.1409 | 6.9228 | 0
2018-05-16 16:00 | 16 | 4 | 0 | 0 | 0 | 2018-05-16 16:00 | 16 | 4 | 0 | 0 | 0 | 2018-05-16 16:00 | 16 | 4 | 86.9718 | 18.1675 | 0 | 2018-05-16 16:00 | 16 | 4 | 33.0493 | 6.9037 | 0
2018-05-16 17:00 | 17 | 4 | 0 | 0 | 0 | 2018-05-16 17:00 | 17 | 4 | 0 | 0 | 0 | 2018-05-16 17:00 | 17 | 4 | 87.1397 | 18.2026 | 0 | 2018-05-16 17:00 | 17 | 4 | 33.1131 | 6.917 | 0
2018-05-16 18:00 | 18 | 4 | 0 | 0 | 0 | 2018-05-16 18:00 | 18 | 4 | 0 | 0 | 0 | 2018-05-16 18:00 | 18 | 4 | 87.2435 | 18.2243 | 0 | 2018-05-16 18:00 | 18 | 4 | 33.1525 | 6.9252 | 0
2018-05-16 19:00 | 19 | 4 | 0 | 0 | 0 | 2018-05-16 19:00 | 19 | 4 | 0 | 0 | 0 | 2018-05-16 19:00 | 19 | 4 | 86.8894 | 18.1503 | 0 | 2018-05-16 19:00 | 19 | 4 | 33.018 | 6.8971 | 0
2018-05-16 20:00 | 20 | 4 | 0 | 0 | 0 | 2018-05-16 20:00 | 20 | 4 | 0 | 0 | 0 | 2018-05-16 20:00 | 20 | 4 | 87.1839 | 18.2118 | 0 | 2018-05-16 20:00 | 20 | 4 | 33.1299 | 6.9205 | 0
2018-05-16 21:00 | 21 | 4 | 0 | 0 | 0 | 2018-05-16 21:00 | 21 | 4 | 0 | 0 | 0 | 2018-05-16 21:00 | 21 | 4 | 87.2419 | 18.224 | 0 | 2018-05-16 21:00 | 21 | 4 | 33.1519 | 6.9251 | 0
2018-05-16 22:00 | 22 | 4 | 0 | 0 | 0 | 2018-05-16 22:00 | 22 | 4 | 0 | 0 | 0 | 2018-05-16 22:00 | 22 | 4 | 87.1733 | 18.2096 | 0 | 2018-05-16 22:00 | 22 | 4 | 33.1259 | 6.9197 | 0
2018-05-16 23:00 | 23 | 4 | 0 | 0 | 0 | 2018-05-16 23:00 | 23 | 4 | 0 | 0 | 0 | 2018-05-16 23:00 | 23 | 4 | 87.2557 | 18.2268 | 0 | 2018-05-16 23:00 | 23 | 4 | 33.1572 | 6.9262 | 0
2018-05-17 | 0 | 5 | 86.5492 | 18.0793 | 0 | 2018-05-17 | 0 | 5 | 0 | 0 | 0 | 2018-05-17 | 0 | 5 | 0 | 0 | 0 | 2018-05-17 | 0 | 5 | 0 | 0 | 0
2018-05-17 01:00 | 1 | 5 | 86.7201 | 18.115 | 0 | 2018-05-17 01:00 | 1 | 5 | 0 | 0 | 0 | 2018-05-17 01:00 | 1 | 5 | 0 | 0 | 0 | 2018-05-17 01:00 | 1 | 5 | 0 | 0 | 0
2018-05-17 02:00 | 2 | 5 | 86.5095 | 18.071 | 0 | 2018-05-17 02:00 | 2 | 5 | 0 | 0 | 0 | 2018-05-17 02:00 | 2 | 5 | 0 | 0 | 0 | 2018-05-17 02:00 | 2 | 5 | 0 | 0 | 0
2018-05-17 03:00 | 3 | 5 | 86.4576 | 18.0601 | 0 | 2018-05-17 03:00 | 3 | 5 | 0 | 0 | 0 | 2018-05-17 03:00 | 3 | 5 | 0 | 0 | 0 | 2018-05-17 03:00 | 3 | 5 | 0 | 0 | 0
2018-05-17 04:00 | 4 | 5 | 86.6316 | 18.0965 | 0 | 2018-05-17 04:00 | 4 | 5 | 0 | 0 | 0 | 2018-05-17 04:00 | 4 | 5 | 0 | 0 | 0 | 2018-05-17 04:00 | 4 | 5 | 0 | 0 | 0
2018-05-17 05:00 | 5 | 5 | 86.569 | 18.0834 | 0 | 2018-05-17 05:00 | 5 | 5 | 0 | 0 | 0 | 2018-05-17 05:00 | 5 | 5 | 0 | 0 | 0 | 2018-05-17 05:00 | 5 | 5 | 0 | 0 | 0
2018-05-17 06:00 | 6 | 5 | 86.6468 | 18.0997 | 0 | 2018-05-17 06:00 | 6 | 5 | 0 | 0 | 0 | 2018-05-17 06:00 | 6 | 5 | 0 | 0 | 0 | 2018-05-17 06:00 | 6 | 5 | 0 | 0 | 0
2018-05-17 07:00 | 7 | 5 | 86.6361 | 18.0974 | 0 | 2018-05-17 07:00 | 7 | 5 | 0 | 0 | 0 | 2018-05-17 07:00 | 7 | 5 | 0 | 0 | 0 | 2018-05-17 07:00 | 7 | 5 | 0 | 0 | 0
2018-05-17 08:00 | 8 | 5 | 86.6819 | 18.107 | 0 | 2018-05-17 08:00 | 8 | 5 | 0 | 0 | 0 | 2018-05-17 08:00 | 8 | 5 | 0 | 0 | 0 | 2018-05-17 08:00 | 8 | 5 | 0 | 0 | 0
2018-05-17 09:00 | 9 | 5 | 86.7094 | 18.1127 | 0 | 2018-05-17 09:00 | 9 | 5 | 0 | 0 | 0 | 2018-05-17 09:00 | 9 | 5 | 0 | 0 | 0 | 2018-05-17 09:00 | 9 | 5 | 0 | 0 | 0
2018-05-17 10:00 | 10 | 5 | 86.7933 | 18.1303 | 0 | 2018-05-17 10:00 | 10 | 5 | 0 | 0 | 0 | 2018-05-17 10:00 | 10 | 5 | 0 | 0 | 0 | 2018-05-17 10:00 | 10 | 5 | 0 | 0 | 0
2018-05-17 11:00 | 11 | 5 | 86.8009 | 18.1318 | 0 | 2018-05-17 11:00 | 11 | 5 | 0 | 0 | 0 | 2018-05-17 11:00 | 11 | 5 | 0 | 0 | 0 | 2018-05-17 11:00 | 11 | 5 | 0 | 0 | 0
2018-05-17 12:00 | 12 | 5 | 86.6728 | 18.1051 | 0 | 2018-05-17 12:00 | 12 | 5 | 0 | 0 | 0 | 2018-05-17 12:00 | 12 | 5 | 0 | 0 | 0 | 2018-05-17 12:00 | 12 | 5 | 0 | 0 | 0
2018-05-17 13:00 | 13 | 5 | 86.6316 | 18.0965 | 0 | 2018-05-17 13:00 | 13 | 5 | 0 | 0 | 0 | 2018-05-17 13:00 | 13 | 5 | 0 | 0 | 0 | 2018-05-17 13:00 | 13 | 5 | 0 | 0 | 0
2018-05-17 14:00 | 14 | 5 | 86.6316 | 18.0965 | 0 | 2018-05-17 14:00 | 14 | 5 | 0 | 0 | 0 | 2018-05-17 14:00 | 14 | 5 | 0 | 0 | 0 | 2018-05-17 14:00 | 14 | 5 | 0 | 0 | 0
2018-05-17 15:00 | 15 | 5 | 86.6636 | 18.1032 | 0 | 2018-05-17 15:00 | 15 | 5 | 0 | 0 | 0 | 2018-05-17 15:00 | 15 | 5 | 0 | 0 | 0 | 2018-05-17 15:00 | 15 | 5 | 0 | 0 | 0
2018-05-17 16:00 | 16 | 5 | 86.5568 | 18.0808 | 0 | 2018-05-17 16:00 | 16 | 5 | 0 | 0 | 0 | 2018-05-17 16:00 | 16 | 5 | 0 | 0 | 0 | 2018-05-17 16:00 | 16 | 5 | 0 | 0 | 0
2018-05-17 17:00 | 17 | 5 | 86.6865 | 18.1079 | 0 | 2018-05-17 17:00 | 17 | 5 | 0 | 0 | 0 | 2018-05-17 17:00 | 17 | 5 | 0 | 0 | 0 | 2018-05-17 17:00 | 17 | 5 | 0 | 0 | 0
2018-05-17 18:00 | 18 | 5 | 86.7262 | 18.1162 | 0 | 2018-05-17 18:00 | 18 | 5 | 0 | 0 | 0 | 2018-05-17 18:00 | 18 | 5 | 0 | 0 | 0 | 2018-05-17 18:00 | 18 | 5 | 0 | 0 | 0
2018-05-17 19:00 | 19 | 5 | 86.5187 | 18.0729 | 0 | 2018-05-17 19:00 | 19 | 5 | 0 | 0 | 0 | 2018-05-17 19:00 | 19 | 5 | 0 | 0 | 0 | 2018-05-17 19:00 | 19 | 5 | 0 | 0 | 0
2018-05-17 20:00 | 20 | 5 | 86.5766 | 18.085 | 0 | 2018-05-17 20:00 | 20 | 5 | 0 | 0 | 0 | 2018-05-17 20:00 | 20 | 5 | 0 | 0 | 0 | 2018-05-17 20:00 | 20 | 5 | 0 | 0 | 0
2018-05-17 21:00 | 21 | 5 | 86.6194 | 18.0939 | 0 | 2018-05-17 21:00 | 21 | 5 | 0 | 0 | 0 | 2018-05-17 21:00 | 21 | 5 | 0 | 0 | 0 | 2018-05-17 21:00 | 21 | 5 | 0 | 0 | 0
2018-05-17 22:00 | 22 | 5 | 86.6743 | 18.1054 | 0 | 2018-05-17 22:00 | 22 | 5 | 0 | 0 | 0 | 2018-05-17 22:00 | 22 | 5 | 0 | 0 | 0 | 2018-05-17 22:00 | 22 | 5 | 0 | 0 | 0
2018-05-17 23:00 | 23 | 5 | 86.5644 | 18.0824 | 0 | 2018-05-17 23:00 | 23 | 5 | 0 | 0 | 0 | 2018-05-17 23:00 | 23 | 5 | 0 | 0 | 0 | 2018-05-17 23:00 | 23 | 5 | 0 | 0 | 0
2018-05-18 | 0 | 6 | 86.2226 | 18.011 | 0 | 2018-05-18 | 0 | 6 | 86.688 | 18.1083 | 0 | 2018-05-18 | 0 | 6 | 0 | 0 | 0 | 2018-05-18 | 0 | 6 | 32.9414 | 6.8811 | 0
2018-05-18 01:00 | 1 | 6 | 86.1128 | 17.9881 | 0 | 2018-05-18 01:00 | 1 | 6 | 86.5232 | 18.0738 | 0 | 2018-05-18 01:00 | 1 | 6 | 0 | 0 | 0 | 2018-05-18 01:00 | 1 | 6 | 32.8788 | 6.8681 | 0
2018-05-18 02:00 | 2 | 6 | 86.2791 | 18.0228 | 0 | 2018-05-18 02:00 | 2 | 6 | 86.6896 | 18.1086 | 0 | 2018-05-18 02:00 | 2 | 6 | 0 | 0 | 0 | 2018-05-18 02:00 | 2 | 6 | 32.942 | 6.8813 | 0
2018-05-18 03:00 | 3 | 6 | 86.0014 | 17.9648 | 0 | 2018-05-18 03:00 | 3 | 6 | 86.4485 | 18.0582 | 0 | 2018-05-18 03:00 | 3 | 6 | 0 | 0 | 0 | 2018-05-18 03:00 | 3 | 6 | 32.8504 | 6.8621 | 0
2018-05-18 04:00 | 4 | 6 | 86.0533 | 17.9757 | 0 | 2018-05-18 04:00 | 4 | 6 | 86.4347 | 18.0553 | 0 | 2018-05-18 04:00 | 4 | 6 | 0 | 0 | 0 | 2018-05-18 04:00 | 4 | 6 | 32.8452 | 6.861 | 0
2018-05-18 05:00 | 5 | 6 | 86.2257 | 18.0117 | 0 | 2018-05-18 05:00 | 5 | 6 | 86.6117 | 18.0923 | 0 | 2018-05-18 05:00 | 5 | 6 | 0 | 0 | 0 | 2018-05-18 05:00 | 5 | 6 | 32.9124 | 6.8751 | 0
2018-05-18 06:00 | 6 | 6 | 86.4332 | 18.055 | 0 | 2018-05-18 06:00 | 6 | 6 | 86.9352 | 18.1599 | 0 | 2018-05-18 06:00 | 6 | 6 | 0 | 0 | 0 | 2018-05-18 06:00 | 6 | 6 | 33.0354 | 6.9008 | 0
2018-05-18 07:00 | 7 | 6 | 86.5873 | 18.0872 | 0 | 2018-05-18 07:00 | 7 | 6 | 87.0619 | 18.1864 | 0 | 2018-05-18 07:00 | 7 | 6 | 0 | 0 | 0 | 2018-05-18 07:00 | 7 | 6 | 33.0835 | 6.9108 | 0
2018-05-18 08:00 | 8 | 6 | 86.3691 | 18.0416 | 0 | 2018-05-18 08:00 | 8 | 6 | 86.7811 | 18.1277 | 0 | 2018-05-18 08:00 | 8 | 6 | 0 | 0 | 0 | 2018-05-18 08:00 | 8 | 6 | 32.9768 | 6.8885 | 0
2018-05-18 09:00 | 9 | 6 | 86.334 | 18.0343 | 0 | 2018-05-18 09:00 | 9 | 6 | 86.7399 | 18.1191 | 0 | 2018-05-18 09:00 | 9 | 6 | 0 | 0 | 0 | 2018-05-18 09:00 | 9 | 6 | 32.9612 | 6.8853 | 0
2018-05-18 10:00 | 10 | 6 | 86.5126 | 18.0716 | 0 | 2018-05-18 10:00 | 10 | 6 | 86.862 | 18.1446 | 0 | 2018-05-18 10:00 | 10 | 6 | 0 | 0 | 0 | 2018-05-18 10:00 | 10 | 6 | 33.0076 | 6.8949 | 0
2018-05-18 11:00 | 11 | 6 | 86.5003 | 18.069 | 0 | 2018-05-18 11:00 | 11 | 6 | 86.9306 | 18.1589 | 0 | 2018-05-18 11:00 | 11 | 6 | 0 | 0 | 0 | 2018-05-18 11:00 | 11 | 6 | 33.0336 | 6.9004 | 0
2018-05-18 12:00 | 12 | 6 | 86.7002 | 18.1108 | 0 | 2018-05-18 12:00 | 12 | 6 | 87.1412 | 18.2029 | 0 | 2018-05-18 12:00 | 12 | 6 | 0 | 0 | 0 | 2018-05-18 12:00 | 12 | 6 | 33.1137 | 6.9171 | 0
2018-05-18 13:00 | 13 | 6 | 86.363 | 18.0404 | 0 | 2018-05-18 13:00 | 13 | 6 | 86.8009 | 18.1318 | 0 | 2018-05-18 13:00 | 13 | 6 | 0 | 0 | 0 | 2018-05-18 13:00 | 13 | 6 | 32.9843 | 6.8901 | 0
2018-05-18 14:00 | 14 | 6 | 86.4408 | 18.0566 | 0 | 2018-05-18 14:00 | 14 | 6 | 86.8635 | 18.1449 | 0 | 2018-05-18 14:00 | 14 | 6 | 0 | 0 | 0 | 2018-05-18 14:00 | 14 | 6 | 33.0081 | 6.8951 | 0
2018-05-18 15:00 | 15 | 6 | 86.2943 | 18.026 | 0 | 2018-05-18 15:00 | 15 | 6 | 86.6743 | 18.1054 | 0 | 2018-05-18 15:00 | 15 | 6 | 0 | 0 | 0 | 2018-05-18 15:00 | 15 | 6 | 32.9362 | 6.88 | 0
2018-05-18 16:00 | 16 | 6 | 86.3706 | 18.042 | 0 | 2018-05-18 16:00 | 16 | 6 | 86.7491 | 18.121 | 0 | 2018-05-18 16:00 | 16 | 6 | 0 | 0 | 0 | 2018-05-18 16:00 | 16 | 6 | 32.9647 | 6.886 | 0
2018-05-18 17:00 | 17 | 6 | 86.2882 | 18.0247 | 0 | 2018-05-18 17:00 | 17 | 6 | 86.7445 | 18.1201 | 0 | 2018-05-18 17:00 | 17 | 6 | 0 | 0 | 0 | 2018-05-18 17:00 | 17 | 6 | 32.9629 | 6.8856 | 0
2018-05-18 18:00 | 18 | 6 | 86.1875 | 18.0037 | 0 | 2018-05-18 18:00 | 18 | 6 | 86.6667 | 18.1038 | 0 | 2018-05-18 18:00 | 18 | 6 | 0 | 0 | 0 | 2018-05-18 18:00 | 18 | 6 | 32.9333 | 6.8794 | 0
2018-05-18 19:00 | 19 | 6 | 86.099 | 17.9852 | 0 | 2018-05-18 19:00 | 19 | 6 | 86.5431 | 18.078 | 0 | 2018-05-18 19:00 | 19 | 6 | 0 | 0 | 0 | 2018-05-18 19:00 | 19 | 6 | 32.8864 | 6.8696 | 0
2018-05-18 20:00 | 20 | 6 | 86.1997 | 18.0063 | 0 | 2018-05-18 20:00 | 20 | 6 | 86.5187 | 18.0729 | 0 | 2018-05-18 20:00 | 20 | 6 | 0 | 0 | 0 | 2018-05-18 20:00 | 20 | 6 | 32.8771 | 6.8677 | 0
2018-05-18 21:00 | 21 | 6 | 86.3767 | 18.0432 | 0 | 2018-05-18 21:00 | 21 | 6 | 86.7247 | 18.1159 | 0 | 2018-05-18 21:00 | 21 | 6 | 0 | 0 | 0 | 2018-05-18 21:00 | 21 | 6 | 32.9554 | 6.8841 | 0
2018-05-18 22:00 | 22 | 6 | 86.3691 | 18.0416 | 0 | 2018-05-18 22:00 | 22 | 6 | 86.7659 | 18.1245 | 0 | 2018-05-18 22:00 | 22 | 6 | 0 | 0 | 0 | 2018-05-18 22:00 | 22 | 6 | 32.971 | 6.8873 | 0
2018-05-18 23:00 | 23 | 6 | 86.4012 | 18.0483 | 0 | 2018-05-18 23:00 | 23 | 6 | 86.7918 | 18.1299 | 0 | 2018-05-18 23:00 | 23 | 6 | 0 | 0 | 0 | 2018-05-18 23:00 | 23 | 6 | 32.9809 | 6.8894 | 0
2018-05-19 | 0 | 7 | 86.0121 | 17.9671 | 0 | 2018-05-19 | 0 | 7 | 0 | 0 | 0 | 2018-05-19 | 0 | 7 | 86.5507 | 18.0796 | 0 | 2018-05-19 | 0 | 7 | 32.8893 | 6.8702 | 0
2018-05-19 01:00 | 1 | 7 | 85.919 | 17.9476 | 0 | 2018-05-19 01:00 | 1 | 7 | 0 | 0 | 0 | 2018-05-19 01:00 | 1 | 7 | 86.5324 | 18.0758 | 0 | 2018-05-19 01:00 | 1 | 7 | 32.8823 | 6.8688 | 0
2018-05-19 02:00 | 2 | 7 | 86.0533 | 17.9757 | 0 | 2018-05-19 02:00 | 2 | 7 | 0 | 0 | 0 | 2018-05-19 02:00 | 2 | 7 | 86.6453 | 18.0993 | 0 | 2018-05-19 02:00 | 2 | 7 | 32.9252 | 6.8777 | 0
2018-05-19 03:00 | 3 | 7 | 86.1677 | 17.9996 | 0 | 2018-05-19 03:00 | 3 | 7 | 0 | 0 | 0 | 2018-05-19 03:00 | 3 | 7 | 86.7002 | 18.1108 | 0 | 2018-05-19 03:00 | 3 | 7 | 32.9461 | 6.8821 | 0
2018-05-19 04:00 | 4 | 7 | 86.3081 | 18.0289 | 0 | 2018-05-19 04:00 | 4 | 7 | 0 | 0 | 0 | 2018-05-19 04:00 | 4 | 7 | 86.8513 | 18.1424 | 0 | 2018-05-19 04:00 | 4 | 7 | 33.0035 | 6.8941 | 0
2018-05-19 05:00 | 5 | 7 | 86.2562 | 18.0181 | 0 | 2018-05-19 05:00 | 5 | 7 | 0 | 0 | 0 | 2018-05-19 05:00 | 5 | 7 | 86.8605 | 18.1443 | 0 | 2018-05-19 05:00 | 5 | 7 | 33.007 | 6.8948 | 0
2018-05-19 06:00 | 6 | 7 | 86.1234 | 17.9903 | 0 | 2018-05-19 06:00 | 6 | 7 | 0 | 0 | 0 | 2018-05-19 06:00 | 6 | 7 | 86.6682 | 18.1041 | 0 | 2018-05-19 06:00 | 6 | 7 | 32.9339 | 6.8796 | 0
2018-05-19 07:00 | 7 | 7 | 86.1906 | 18.0044 | 0 | 2018-05-19 07:00 | 7 | 7 | 0 | 0 | 0 | 2018-05-19 07:00 | 7 | 7 | 86.7247 | 18.1159 | 0 | 2018-05-19 07:00 | 7 | 7 | 32.9554 | 6.8841 | 0
2018-05-19 08:00 | 8 | 7 | 86.36 | 18.0397 | 0 | 2018-05-19 08:00 | 8 | 7 | 0 | 0 | 0 | 2018-05-19 08:00 | 8 | 7 | 86.952 | 18.1634 | 0 | 2018-05-19 08:00 | 8 | 7 | 33.0418 | 6.9021 | 0
2018-05-19 09:00 | 9 | 7 | 86.4912 | 18.0671 | 0 | 2018-05-19 09:00 | 9 | 7 | 0 | 0 | 0 | 2018-05-19 09:00 | 9 | 7 | 87.0588 | 18.1857 | 0 | 2018-05-19 09:00 | 9 | 7 | 33.0823 | 6.9106 | 0
2018-05-19 10:00 | 10 | 7 | 86.1982 | 18.0059 | 0 | 2018-05-19 10:00 | 10 | 7 | 0 | 0 | 0 | 2018-05-19 10:00 | 10 | 7 | 86.6392 | 18.0981 | 0 | 2018-05-19 10:00 | 10 | 7 | 32.9229 | 6.8773 | 0
2018-05-19 11:00 | 11 | 7 | 86.1707 | 18.0002 | 0 | 2018-05-19 11:00 | 11 | 7 | 0 | 0 | 0 | 2018-05-19 11:00 | 11 | 7 | 86.8849 | 18.1494 | 0 | 2018-05-19 11:00 | 11 | 7 | 33.0163 | 6.8968 | 0
2018-05-19 12:00 | 12 | 7 | 86.5019 | 18.0694 | 0 | 2018-05-19 12:00 | 12 | 7 | 0 | 0 | 0 | 2018-05-19 12:00 | 12 | 7 | 87.1504 | 18.2048 | 0 | 2018-05-19 12:00 | 12 | 7 | 33.1172 | 6.9178 | 0
2018-05-19 13:00 | 13 | 7 | 86.6148 | 18.093 | 0 | 2018-05-19 13:00 | 13 | 7 | 0 | 0 | 0 | 2018-05-19 13:00 | 13 | 7 | 87.3167 | 18.2396 | 0 | 2018-05-19 13:00 | 13 | 7 | 33.1803 | 6.931 | 0
2018-05-19 14:00 | 14 | 7 | 86.4439 | 18.0573 | 0 | 2018-05-19 14:00 | 14 | 7 | 0 | 0 | 0 | 2018-05-19 14:00 | 14 | 7 | 87.0832 | 18.1908 | 0 | 2018-05-19 14:00 | 14 | 7 | 33.0916 | 6.9125 | 0
2018-05-19 15:00 | 15 | 7 | 86.5522 | 18.0799 | 0 | 2018-05-19 15:00 | 15 | 7 | 0 | 0 | 0 | 2018-05-19 15:00 | 15 | 7 | 87.2938 | 18.2348 | 0 | 2018-05-19 15:00 | 15 | 7 | 33.1716 | 6.9292 | 0
2018-05-19 16:00 | 16 | 7 | 86.5644 | 18.0824 | 0 | 2018-05-19 16:00 | 16 | 7 | 0 | 0 | 0 | 2018-05-19 16:00 | 16 | 7 | 87.3579 | 18.2482 | 0 | 2018-05-19 16:00 | 16 | 7 | 33.196 | 6.9343 | 0
2018-05-19 17:00 | 17 | 7 | 86.7445 | 18.1201 | 0 | 2018-05-19 17:00 | 17 | 7 | 0 | 0 | 0 | 2018-05-19 17:00 | 17 | 7 | 87.57 | 18.2925 | 0 | 2018-05-19 17:00 | 17 | 7 | 33.2766 | 6.9511 | 0
2018-05-19 18:00 | 18 | 7 | 86.4668 | 18.062 | 0 | 2018-05-19 18:00 | 18 | 7 | 0 | 0 | 0 | 2018-05-19 18:00 | 18 | 7 | 87.3014 | 18.2364 | 0 | 2018-05-19 18:00 | 18 | 7 | 33.1745 | 6.9298 | 0
2018-05-19 19:00 | 19 | 7 | 86.3661 | 18.041 | 0 | 2018-05-19 19:00 | 19 | 7 | 0 | 0 | 0 | 2018-05-19 19:00 | 19 | 7 | 87.0954 | 18.1934 | 0 | 2018-05-19 19:00 | 19 | 7 | 33.0963 | 6.9135 | 0
2018-05-19 20:00 | 20 | 7 | 86.1173 | 17.989 | 0 | 2018-05-19 20:00 | 20 | 7 | 0 | 0 | 0 | 2018-05-19 20:00 | 20 | 7 | 86.891 | 18.1507 | 0 | 2018-05-19 20:00 | 20 | 7 | 33.0186 | 6.8973 | 0
2018-05-19 21:00 | 21 | 7 | 86.1555 | 17.997 | 0 | 2018-05-19 21:00 | 21 | 7 | 0 | 0 | 0 | 2018-05-19 21:00 | 21 | 7 | 86.9245 | 18.1577 | 0 | 2018-05-19 21:00 | 21 | 7 | 33.0313 | 6.8999 | 0
2018-05-19 22:00 | 22 | 7 | 86.2211 | 18.0107 | 0 | 2018-05-19 22:00 | 22 | 7 | 0 | 0 | 0 | 2018-05-19 22:00 | 22 | 7 | 87.0054 | 18.1746 | 0 | 2018-05-19 22:00 | 22 | 7 | 33.0621 | 6.9063 | 0
2018-05-19 23:00 | 23 | 7 | 86.2226 | 18.011 | 0 | 2018-05-19 23:00 | 23 | 7 | 0 | 0 | 0 | 2018-05-19 23:00 | 23 | 7 | 87.0787 | 18.1899 | 0 | 2018-05-19 23:00 | 23 | 7 | 33.0899 | 6.9122 | 0
2018-05-20 | 0 | 1 | 86.2364 | 18.0139 | 0 | 2018-05-20 | 0 | 1 | 86.7994 | 18.1315 | 0 | 2018-05-20 | 0 | 1 | 0 | 0 | 0 | 2018-05-20 | 0 | 1 | 32.9838 | 6.89 | 0
2018-05-20 01:00 | 1 | 1 | 86.3188 | 18.0311 | 0 | 2018-05-20 01:00 | 1 | 1 | 86.952 | 18.1634 | 0 | 2018-05-20 01:00 | 1 | 1 | 0 | 0 | 0 | 2018-05-20 01:00 | 1 | 1 | 33.0418 | 6.9021 | 0
2018-05-20 02:00 | 2 | 1 | 86.2119 | 18.0088 | 0 | 2018-05-20 02:00 | 2 | 1 | 86.8177 | 18.1353 | 0 | 2018-05-20 02:00 | 2 | 1 | 0 | 0 | 0 | 2018-05-20 02:00 | 2 | 1 | 32.9907 | 6.8914 | 0
2018-05-20 03:00 | 3 | 1 | 86.1845 | 18.0031 | 0 | 2018-05-20 03:00 | 3 | 1 | 86.7857 | 18.1287 | 0 | 2018-05-20 03:00 | 3 | 1 | 0 | 0 | 0 | 2018-05-20 03:00 | 3 | 1 | 32.9786 | 6.8889 | 0
2018-05-20 04:00 | 4 | 1 | 86.2455 | 18.0158 | 0 | 2018-05-20 04:00 | 4 | 1 | 86.833 | 18.1385 | 0 | 2018-05-20 04:00 | 4 | 1 | 0 | 0 | 0 | 2018-05-20 04:00 | 4 | 1 | 32.9965 | 6.8926 | 0
2018-05-20 05:00 | 5 | 1 | 86.2333 | 18.0133 | 0 | 2018-05-20 05:00 | 5 | 1 | 86.833 | 18.1385 | 0 | 2018-05-20 05:00 | 5 | 1 | 0 | 0 | 0 | 2018-05-20 05:00 | 5 | 1 | 32.9965 | 6.8926 | 0
2018-05-20 06:00 | 6 | 1 | 86.2776 | 18.0225 | 0 | 2018-05-20 06:00 | 6 | 1 | 86.8528 | 18.1427 | 0 | 2018-05-20 06:00 | 6 | 1 | 0 | 0 | 0 | 2018-05-20 06:00 | 6 | 1 | 33.0041 | 6.8942 | 0
2018-05-20 07:00 | 7 | 1 | 86.2867 | 18.0244 | 0 | 2018-05-20 07:00 | 7 | 1 | 86.8452 | 18.1411 | 0 | 2018-05-20 07:00 | 7 | 1 | 0 | 0 | 0 | 2018-05-20 07:00 | 7 | 1 | 33.0012 | 6.8936 | 0
2018-05-20 08:00 | 8 | 1 | 86.2989 | 18.027 | 0 | 2018-05-20 08:00 | 8 | 1 | 86.9032 | 18.1532 | 0 | 2018-05-20 08:00 | 8 | 1 | 0 | 0 | 0 | 2018-05-20 08:00 | 8 | 1 | 33.0232 | 6.8982 | 0
2018-05-20 09:00 | 9 | 1 | 86.2867 | 18.0244 | 0 | 2018-05-20 09:00 | 9 | 1 | 86.8162 | 18.135 | 0 | 2018-05-20 09:00 | 9 | 1 | 0 | 0 | 0 | 2018-05-20 09:00 | 9 | 1 | 32.9902 | 6.8913 | 0
2018-05-20 10:00 | 10 | 1 | 86.2882 | 18.0247 | 0 | 2018-05-20 10:00 | 10 | 1 | 86.8528 | 18.1427 | 0 | 2018-05-20 10:00 | 10 | 1 | 0 | 0 | 0 | 2018-05-20 10:00 | 10 | 1 | 33.0041 | 6.8942 | 0
2018-05-20 11:00 | 11 | 1 | 86.1845 | 18.0031 | 0 | 2018-05-20 11:00 | 11 | 1 | 86.743 | 18.1197 | 0 | 2018-05-20 11:00 | 11 | 1 | 0 | 0 | 0 | 2018-05-20 11:00 | 11 | 1 | 32.9623 | 6.8855 | 0
2018-05-20 12:00 | 12 | 1 | 86.1418 | 17.9942 | 0 | 2018-05-20 12:00 | 12 | 1 | 86.714 | 18.1137 | 0 | 2018-05-20 12:00 | 12 | 1 | 0 | 0 | 0 | 2018-05-20 12:00 | 12 | 1 | 32.9513 | 6.8832 | 0
2018-05-20 13:00 | 13 | 1 | 86.1479 | 17.9954 | 0 | 2018-05-20 13:00 | 13 | 1 | 86.7659 | 18.1245 | 0 | 2018-05-20 13:00 | 13 | 1 | 0 | 0 | 0 | 2018-05-20 13:00 | 13 | 1 | 32.971 | 6.8873 | 0
2018-05-20 14:00 | 14 | 1 | 86.1112 | 17.9878 | 0 | 2018-05-20 14:00 | 14 | 1 | 86.7018 | 18.1111 | 0 | 2018-05-20 14:00 | 14 | 1 | 0 | 0 | 0 | 2018-05-20 14:00 | 14 | 1 | 32.9467 | 6.8822 | 0
2018-05-20 15:00 | 15 | 1 | 86.2455 | 18.0158 | 0 | 2018-05-20 15:00 | 15 | 1 | 86.8482 | 18.1417 | 0 | 2018-05-20 15:00 | 15 | 1 | 0 | 0 | 0 | 2018-05-20 15:00 | 15 | 1 | 33.0023 | 6.8939 | 0
2018-05-20 16:00 | 16 | 1 | 86.3447 | 18.0365 | 0 | 2018-05-20 16:00 | 16 | 1 | 86.9398 | 18.1609 | 0 | 2018-05-20 16:00 | 16 | 1 | 0 | 0 | 0 | 2018-05-20 16:00 | 16 | 1 | 33.0371 | 6.9011 | 0
2018-05-20 17:00 | 17 | 1 | 86.4805 | 18.0649 | 0 | 2018-05-20 17:00 | 17 | 1 | 86.9856 | 18.1704 | 0 | 2018-05-20 17:00 | 17 | 1 | 0 | 0 | 0 | 2018-05-20 17:00 | 17 | 1 | 33.0545 | 6.9048 | 0
2018-05-20 18:00 | 18 | 1 | 86.4332 | 18.055 | 0 | 2018-05-20 18:00 | 18 | 1 | 86.92 | 18.1567 | 0 | 2018-05-20 18:00 | 18 | 1 | 0 | 0 | 0 | 2018-05-20 18:00 | 18 | 1 | 33.0296 | 6.8996 | 0
2018-05-20 19:00 | 19 | 1 | 85.6794 | 17.8976 | 0 | 2018-05-20 19:00 | 19 | 1 | 85.9266 | 17.9492 | 0 | 2018-05-20 19:00 | 19 | 1 | 0 | 0 | 0 | 2018-05-20 19:00 | 19 | 1 | 32.6521 | 6.8207 | 0
2018-05-20 20:00 | 20 | 1 | 86.3294 | 18.0333 | 0 | 2018-05-20 20:00 | 20 | 1 | 86.5888 | 18.0875 | 0 | 2018-05-20 20:00 | 20 | 1 | 0 | 0 | 0 | 2018-05-20 20:00 | 20 | 1 | 32.9037 | 6.8733 | 0
2018-05-20 21:00 | 21 | 1 | 86.3569 | 18.0391 | 0 | 2018-05-20 21:00 | 21 | 1 | 86.6728 | 18.1051 | 0 | 2018-05-20 21:00 | 21 | 1 | 0 | 0 | 0 | 2018-05-20 21:00 | 21 | 1 | 32.9357 | 6.8799 | 0
2018-05-20 22:00 | 22 | 1 | 86.4881 | 18.0665 | 0 | 2018-05-20 22:00 | 22 | 1 | 86.8086 | 18.1334 | 0 | 2018-05-20 22:00 | 22 | 1 | 0 | 0 | 0 | 2018-05-20 22:00 | 22 | 1 | 32.9873 | 6.8907 | 0
2018-05-20 23:00 | 23 | 1 | 86.4332 | 18.055 | 0 | 2018-05-20 23:00 | 23 | 1 | 86.7353 | 18.1181 | 0 | 2018-05-20 23:00 | 23 | 1 | 0 | 0 | 0 | 2018-05-20 23:00 | 23 | 1 | 32.9594 | 6.8849 | 0
2018-05-21 | 0 | 2 | 86.4088 | 18.0499 | 0 | 2018-05-21 | 0 | 2 | 86.7002 | 18.1108 | 0 | 2018-05-21 | 0 | 2 | 86.9352 | 18.1599 | 0 | 2018-05-21 | 0 | 2 | 65.9815 | 13.7829 | 0
2018-05-21 01:00 | 1 | 2 | 86.0426 | 17.9734 | 0 | 2018-05-21 01:00 | 1 | 2 | 86.3127 | 18.0299 | 0 | 2018-05-21 01:00 | 1 | 2 | 86.5278 | 18.0748 | 0 | 2018-05-21 01:00 | 1 | 2 | 65.6794 | 13.7198 | 0
2018-05-21 02:00 | 2 | 2 | 86.392 | 18.0464 | 0 | 2018-05-21 02:00 | 2 | 2 | 86.6392 | 18.0981 | 0 | 2018-05-21 02:00 | 2 | 2 | 86.8421 | 18.1404 | 0 | 2018-05-21 02:00 | 2 | 2 | 65.9229 | 13.7706 | 0
2018-05-21 03:00 | 3 | 2 | 86.2776 | 18.0225 | 0 | 2018-05-21 03:00 | 3 | 2 | 86.5766 | 18.085 | 0 | 2018-05-21 03:00 | 3 | 2 | 86.7536 | 18.122 | 0 | 2018-05-21 03:00 | 3 | 2 | 65.8655 | 13.7586 | 0
2018-05-21 04:00 | 4 | 2 | 86.5034 | 18.0697 | 0 | 2018-05-21 04:00 | 4 | 2 | 86.8849 | 18.1494 | 0 | 2018-05-21 04:00 | 4 | 2 | 87.0283 | 18.1793 | 0 | 2018-05-21 04:00 | 4 | 2 | 66.087 | 13.8049 | 0
2018-05-21 05:00 | 5 | 2 | 86.3661 | 18.041 | 0 | 2018-05-21 05:00 | 5 | 2 | 86.772 | 18.1258 | 0 | 2018-05-21 05:00 | 5 | 2 | 87.0054 | 18.1746 | 0 | 2018-05-21 05:00 | 5 | 2 | 66.0354 | 13.7941 | 0
2018-05-21 06:00 | 6 | 2 | 86.2898 | 18.0251 | 0 | 2018-05-21 06:00 | 6 | 2 | 86.6499 | 18.1003 | 0 | 2018-05-21 06:00 | 6 | 2 | 86.8147 | 18.1347 | 0 | 2018-05-21 06:00 | 6 | 2 | 65.9165 | 13.7693 | 0
2018-05-21 07:00 | 7 | 2 | 86.2043 | 18.0072 | 0 | 2018-05-21 07:00 | 7 | 2 | 86.5278 | 18.0748 | 0 | 2018-05-21 07:00 | 7 | 2 | 86.7079 | 18.1124 | 0 | 2018-05-21 07:00 | 7 | 2 | 65.8296 | 13.7511 | 0
2018-05-21 08:00 | 8 | 2 | 86.3355 | 18.0346 | 0 | 2018-05-21 08:00 | 8 | 2 | 86.5461 | 18.0786 | 0 | 2018-05-21 08:00 | 8 | 2 | 86.8025 | 18.1322 | 0 | 2018-05-21 08:00 | 8 | 2 | 65.8725 | 13.7601 | 0
2018-05-21 09:00 | 9 | 2 | 86.3798 | 18.0439 | 0 | 2018-05-21 09:00 | 9 | 2 | 86.7262 | 18.1162 | 0 | 2018-05-21 09:00 | 9 | 2 | 86.8711 | 18.1465 | 0 | 2018-05-21 09:00 | 9 | 2 | 65.967 | 13.7798 | 0
2018-05-21 10:00 | 10 | 2 | 86.2272 | 18.012 | 0 | 2018-05-21 10:00 | 10 | 2 | 86.5156 | 18.0722 | 0 | 2018-05-21 10:00 | 10 | 2 | 86.714 | 18.1137 | 0 | 2018-05-21 10:00 | 10 | 2 | 65.8272 | 13.7507 | 0
2018-05-21 11:00 | 11 | 2 | 86.2119 | 18.0088 | 0 | 2018-05-21 11:00 | 11 | 2 | 86.5141 | 18.0719 | 0 | 2018-05-21 11:00 | 11 | 2 | 86.7201 | 18.115 | 0 | 2018-05-21 11:00 | 11 | 2 | 65.829 | 13.751 | 0
2018-05-21 12:00 | 12 | 2 | 86.389 | 18.0458 | 0 | 2018-05-21 12:00 | 12 | 2 | 86.6835 | 18.1073 | 0 | 2018-05-21 12:00 | 12 | 2 | 86.8574 | 18.1436 | 0 | 2018-05-21 12:00 | 12 | 2 | 65.9455 | 13.7754 | 0
2018-05-21 13:00 | 13 | 2 | 86.4027 | 18.0487 | 0 | 2018-05-21 13:00 | 13 | 2 | 86.6224 | 18.0946 | 0 | 2018-05-21 13:00 | 13 | 2 | 86.7475 | 18.1207 | 0 | 2018-05-21 13:00 | 13 | 2 | 65.8806 | 13.7618 | 0
2018-05-21 14:00 | 14 | 2 | 86.3783 | 18.0436 | 0 | 2018-05-21 14:00 | 14 | 2 | 86.6606 | 18.1025 | 0 | 2018-05-21 14:00 | 14 | 2 | 86.7903 | 18.1296 | 0 | 2018-05-21 14:00 | 14 | 2 | 65.9113 | 13.7682 | 0
2018-05-21 15:00 | 15 | 2 | 86.3355 | 18.0346 | 0 | 2018-05-21 15:00 | 15 | 2 | 86.5248 | 18.0742 | 0 | 2018-05-21 15:00 | 15 | 2 | 86.7384 | 18.1188 | 0 | 2018-05-21 15:00 | 15 | 2 | 65.84 | 13.7533 | 0
2018-05-21 16:00 | 16 | 2 | 86.3493 | 18.0375 | 0 | 2018-05-21 16:00 | 16 | 2 | 86.4912 | 18.0671 | 0 | 2018-05-21 16:00 | 16 | 2 | 86.685 | 18.1076 | 0 | 2018-05-21 16:00 | 16 | 2 | 65.807 | 13.7464 | 0
2018-05-21 17:00 | 17 | 2 | 86.244 | 18.0155 | 0 | 2018-05-21 17:00 | 17 | 2 | 86.4683 | 18.0624 | 0 | 2018-05-21 17:00 | 17 | 2 | 86.6743 | 18.1054 | 0 | 2018-05-21 17:00 | 17 | 2 | 65.7942 | 13.7437 | 0
2018-05-21 18:00 | 18 | 2 | 86.3142 | 18.0302 | 0 | 2018-05-21 18:00 | 18 | 2 | 86.4378 | 18.056 | 0 | 2018-05-21 18:00 | 18 | 2 | 86.5934 | 18.0885 | 0 | 2018-05-21 18:00 | 18 | 2 | 65.7519 | 13.7349 | 0
2018-05-21 19:00 | 19 | 2 | 86.2089 | 18.0082 | 0 | 2018-05-21 19:00 | 19 | 2 | 86.3508 | 18.0378 | 0 | 2018-05-21 19:00 | 19 | 2 | 86.5583 | 18.0812 | 0 | 2018-05-21 19:00 | 19 | 2 | 65.7055 | 13.7252 | 0
2018-05-21 20:00 | 20 | 2 | 86.2181 | 18.0101 | 0 | 2018-05-21 20:00 | 20 | 2 | 86.4836 | 18.0656 | 0 | 2018-05-21 20:00 | 20 | 2 | 86.6896 | 18.1086 | 0 | 2018-05-21 20:00 | 20 | 2 | 65.8058 | 13.7462 | 0
2018-05-21 21:00 | 21 | 2 | 86.1494 | 17.9957 | 0 | 2018-05-21 21:00 | 21 | 2 | 86.4759 | 18.064 | 0 | 2018-05-21 21:00 | 21 | 2 | 86.63 | 18.0961 | 0 | 2018-05-21 21:00 | 21 | 2 | 65.7802 | 13.7408 | 0
2018-05-21 22:00 | 22 | 2 | 86.2593 | 18.0187 | 0 | 2018-05-21 22:00 | 22 | 2 | 86.5522 | 18.0799 | 0 | 2018-05-21 22:00 | 22 | 2 | 86.6468 | 18.0997 | 0 | 2018-05-21 22:00 | 22 | 2 | 65.8156 | 13.7482 | 0
2018-05-21 23:00 | 23 | 2 | 86.4424 | 18.057 | 0 | 2018-05-21 23:00 | 23 | 2 | 86.8055 | 18.1328 | 0 | 2018-05-21 23:00 | 23 | 2 | 86.8864 | 18.1497 | 0 | 2018-05-21 23:00 | 23 | 2 | 66.0029 | 13.7874 | 0
2018-05-22 | 0 | 3 | 86.4637 | 18.0614 | 0 | 2018-05-22 | 0 | 3 | 0 | 0 | 0 | 2018-05-22 | 0 | 3 | 0 | 0 | 0 | 2018-05-22 | 0 | 3 | 0 | 0 | 0
2018-05-22 01:00 | 1 | 3 | 86.5629 | 18.0821 | 0 | 2018-05-22 01:00 | 1 | 3 | 0 | 0 | 0 | 2018-05-22 01:00 | 1 | 3 | 0 | 0 | 0 | 2018-05-22 01:00 | 1 | 3 | 0 | 0 | 0
2018-05-22 02:00 | 2 | 3 | 86.3706 | 18.042 | 0 | 2018-05-22 02:00 | 2 | 3 | 0 | 0 | 0 | 2018-05-22 02:00 | 2 | 3 | 0 | 0 | 0 | 2018-05-22 02:00 | 2 | 3 | 0 | 0 | 0
2018-05-22 03:00 | 3 | 3 | 86.3523 | 18.0381 | 0 | 2018-05-22 03:00 | 3 | 3 | 0 | 0 | 0 | 2018-05-22 03:00 | 3 | 3 | 0 | 0 | 0 | 2018-05-22 03:00 | 3 | 3 | 0 | 0 | 0
2018-05-22 04:00 | 4 | 3 | 86.3676 | 18.0413 | 0 | 2018-05-22 04:00 | 4 | 3 | 0 | 0 | 0 | 2018-05-22 04:00 | 4 | 3 | 0 | 0 | 0 | 2018-05-22 04:00 | 4 | 3 | 0 | 0 | 0
2018-05-22 05:00 | 5 | 3 | 86.4027 | 18.0487 | 0 | 2018-05-22 05:00 | 5 | 3 | 0 | 0 | 0 | 2018-05-22 05:00 | 5 | 3 | 0 | 0 | 0 | 2018-05-22 05:00 | 5 | 3 | 0 | 0 | 0
2018-05-22 06:00 | 6 | 3 | 86.4652 | 18.0617 | 0 | 2018-05-22 06:00 | 6 | 3 | 0 | 0 | 0 | 2018-05-22 06:00 | 6 | 3 | 0 | 0 | 0 | 2018-05-22 06:00 | 6 | 3 | 0 | 0 | 0
2018-05-22 07:00 | 7 | 3 | 86.4012 | 18.0483 | 0 | 2018-05-22 07:00 | 7 | 3 | 0 | 0 | 0 | 2018-05-22 07:00 | 7 | 3 | 0 | 0 | 0 | 2018-05-22 07:00 | 7 | 3 | 0 | 0 | 0
2018-05-22 08:00 | 8 | 3 | 86.4515 | 18.0589 | 0 | 2018-05-22 08:00 | 8 | 3 | 0 | 0 | 0 | 2018-05-22 08:00 | 8 | 3 | 0 | 0 | 0 | 2018-05-22 08:00 | 8 | 3 | 0 | 0 | 0
2018-05-22 09:00 | 9 | 3 | 86.2028 | 18.0069 | 0 | 2018-05-22 09:00 | 9 | 3 | 0 | 0 | 0 | 2018-05-22 09:00 | 9 | 3 | 0 | 0 | 0 | 2018-05-22 09:00 | 9 | 3 | 0 | 0 | 0
2018-05-22 10:00 | 10 | 3 | 86.2715 | 18.0213 | 0 | 2018-05-22 10:00 | 10 | 3 | 0 | 0 | 0 | 2018-05-22 10:00 | 10 | 3 | 0 | 0 | 0 | 2018-05-22 10:00 | 10 | 3 | 0 | 0 | 0
2018-05-22 11:00 | 11 | 3 | 86.7567 | 18.1226 | 0 | 2018-05-22 11:00 | 11 | 3 | 0 | 0 | 0 | 2018-05-22 11:00 | 11 | 3 | 0 | 0 | 0 | 2018-05-22 11:00 | 11 | 3 | 0 | 0 | 0
2018-05-22 12:00 | 12 | 3 | 86.6194 | 18.0939 | 0 | 2018-05-22 12:00 | 12 | 3 | 0 | 0 | 0 | 2018-05-22 12:00 | 12 | 3 | 0 | 0 | 0 | 2018-05-22 12:00 | 12 | 3 | 0 | 0 | 0
2018-05-22 13:00 | 13 | 3 | 86.6377 | 18.0977 | 0 | 2018-05-22 13:00 | 13 | 3 | 0 | 0 | 0 | 2018-05-22 13:00 | 13 | 3 | 0 | 0 | 0 | 2018-05-22 13:00 | 13 | 3 | 0 | 0 | 0
2018-05-22 14:00 | 14 | 3 | 86.8757 | 18.1475 | 0 | 2018-05-22 14:00 | 14 | 3 | 0 | 0 | 0 | 2018-05-22 14:00 | 14 | 3 | 0 | 0 | 0 | 2018-05-22 14:00 | 14 | 3 | 0 | 0 | 0
2018-05-22 15:00 | 15 | 3 | 86.7994 | 18.1315 | 0 | 2018-05-22 15:00 | 15 | 3 | 0 | 0 | 0 | 2018-05-22 15:00 | 15 | 3 | 0 | 0 | 0 | 2018-05-22 15:00 | 15 | 3 | 0 | 0 | 0
2018-05-22 16:00 | 16 | 3 | 86.7674 | 18.1248 | 0 | 2018-05-22 16:00 | 16 | 3 | 0 | 0 | 0 | 2018-05-22 16:00 | 16 | 3 | 0 | 0 | 0 | 2018-05-22 16:00 | 16 | 3 | 0 | 0 | 0
2018-05-22 17:00 | 17 | 3 | 86.7384 | 18.1188 | 0 | 2018-05-22 17:00 | 17 | 3 | 0 | 0 | 0 | 2018-05-22 17:00 | 17 | 3 | 0 | 0 | 0 | 2018-05-22 17:00 | 17 | 3 | 0 | 0 | 0
2018-05-22 18:00 | 18 | 3 | 86.7124 | 18.1134 | 0 | 2018-05-22 18:00 | 18 | 3 | 0 | 0 | 0 | 2018-05-22 18:00 | 18 | 3 | 0 | 0 | 0 | 2018-05-22 18:00 | 18 | 3 | 0 | 0 | 0
2018-05-22 19:00 | 19 | 3 | 86.8376 | 18.1395 | 0 | 2018-05-22 19:00 | 19 | 3 | 0 | 0 | 0 | 2018-05-22 19:00 | 19 | 3 | 0 | 0 | 0 | 2018-05-22 19:00 | 19 | 3 | 0 | 0 | 0
2018-05-22 20:00 | 20 | 3 | 86.627 | 18.0955 | 0 | 2018-05-22 20:00 | 20 | 3 | 0 | 0 | 0 | 2018-05-22 20:00 | 20 | 3 | 0 | 0 | 0 | 2018-05-22 20:00 | 20 | 3 | 0 | 0 | 0
2018-05-22 21:00 | 21 | 3 | 86.6239 | 18.0949 | 0 | 2018-05-22 21:00 | 21 | 3 | 0 | 0 | 0 | 2018-05-22 21:00 | 21 | 3 | 0 | 0 | 0 | 2018-05-22 21:00 | 21 | 3 | 0 | 0 | 0
2018-05-22 22:00 | 22 | 3 | 86.714 | 18.1137 | 0 | 2018-05-22 22:00 | 22 | 3 | 0 | 0 | 0 | 2018-05-22 22:00 | 22 | 3 | 0 | 0 | 0 | 2018-05-22 22:00 | 22 | 3 | 0 | 0 | 0
2018-05-22 23:00 | 23 | 3 | 86.8971 | 18.1519 | 0 | 2018-05-22 23:00 | 23 | 3 | 0 | 0 | 0 | 2018-05-22 23:00 | 23 | 3 | 0 | 0 | 0 | 2018-05-22 23:00 | 23 | 3 | 0 | 0 | 0
2018-05-23 | 0 | 4 | 0 | 0 | 0 | 2018-05-23 | 0 | 4 | 0 | 0 | 0 | 2018-05-23 | 0 | 4 | 86.6712 | 18.1047 | 0 | 2018-05-23 | 0 | 4 | 32.9351 | 6.8798 | 0
2018-05-23 01:00 | 1 | 4 | 0 | 0 | 0 | 2018-05-23 01:00 | 1 | 4 | 0 | 0 | 0 | 2018-05-23 01:00 | 1 | 4 | 86.511 | 18.0713 | 0 | 2018-05-23 01:00 | 1 | 4 | 32.8742 | 6.8671 | 0
2018-05-23 02:00 | 2 | 4 | 0 | 0 | 0 | 2018-05-23 02:00 | 2 | 4 | 0 | 0 | 0 | 2018-05-23 02:00 | 2 | 4 | 86.7628 | 18.1239 | 0 | 2018-05-23 02:00 | 2 | 4 | 32.9699 | 6.8871 | 0
2018-05-23 03:00 | 3 | 4 | 0 | 0 | 0 | 2018-05-23 03:00 | 3 | 4 | 0 | 0 | 0 | 2018-05-23 03:00 | 3 | 4 | 86.7384 | 18.1188 | 0 | 2018-05-23 03:00 | 3 | 4 | 32.9606 | 6.8851 | 0
2018-05-23 04:00 | 4 | 4 | 0 | 0 | 0 | 2018-05-23 04:00 | 4 | 4 | 0 | 0 | 0 | 2018-05-23 04:00 | 4 | 4 | 86.8376 | 18.1395 | 0 | 2018-05-23 04:00 | 4 | 4 | 32.9983 | 6.893 | 0
2018-05-23 05:00 | 5 | 4 | 0 | 0 | 0 | 2018-05-23 05:00 | 5 | 4 | 0 | 0 | 0 | 2018-05-23 05:00 | 5 | 4 | 87.0222 | 18.1781 | 0 | 2018-05-23 05:00 | 5 | 4 | 33.0684 | 6.9077 | 0
2018-05-23 06:00 | 6 | 4 | 0 | 0 | 0 | 2018-05-23 06:00 | 6 | 4 | 0 | 0 | 0 | 2018-05-23 06:00 | 6 | 4 | 86.9627 | 18.1656 | 0 | 2018-05-23 06:00 | 6 | 4 | 33.0458 | 6.9029 | 0
2018-05-23 07:00 | 7 | 4 | 0 | 0 | 0 | 2018-05-23 07:00 | 7 | 4 | 0 | 0 | 0 | 2018-05-23 07:00 | 7 | 4 | 87.1321 | 18.201 | 0 | 2018-05-23 07:00 | 7 | 4 | 33.1102 | 6.9164 | 0
2018-05-23 08:00 | 8 | 4 | 0 | 0 | 0 | 2018-05-23 08:00 | 8 | 4 | 0 | 0 | 0 | 2018-05-23 08:00 | 8 | 4 | 87.1931 | 18.2138 | 0 | 2018-05-23 08:00 | 8 | 4 | 33.1334 | 6.9212 | 0
2018-05-23 09:00 | 9 | 4 | 0 | 0 | 0 | 2018-05-23 09:00 | 9 | 4 | 0 | 0 | 0 | 2018-05-23 09:00 | 9 | 4 | 86.7155 | 18.114 | 0 | 2018-05-23 09:00 | 9 | 4 | 32.9519 | 6.8833 | 0
2018-05-23 10:00 | 10 | 4 | 0 | 0 | 0 | 2018-05-23 10:00 | 10 | 4 | 0 | 0 | 0 | 2018-05-23 10:00 | 10 | 4 | 86.6743 | 18.1054 | 0 | 2018-05-23 10:00 | 10 | 4 | 32.9362 | 6.88 | 0
2018-05-23 11:00 | 11 | 4 | 0 | 0 | 0 | 2018-05-23 11:00 | 11 | 4 | 0 | 0 | 0 | 2018-05-23 11:00 | 11 | 4 | 86.8956 | 18.1516 | 0 | 2018-05-23 11:00 | 11 | 4 | 33.0203 | 6.8976 | 0
2018-05-23 12:00 | 12 | 4 | 0 | 0 | 0 | 2018-05-23 12:00 | 12 | 4 | 0 | 0 | 0 | 2018-05-23 12:00 | 12 | 4 | 86.9276 | 18.1583 | 0 | 2018-05-23 12:00 | 12 | 4 | 33.0325 | 6.9002 | 0
2018-05-23 13:00 | 13 | 4 | 0 | 0 | 0 | 2018-05-23 13:00 | 13 | 4 | 0 | 0 | 0 | 2018-05-23 13:00 | 13 | 4 | 87.2541 | 18.2265 | 0 | 2018-05-23 13:00 | 13 | 4 | 33.1566 | 6.9261 | 0
2018-05-23 14:00 | 14 | 4 | 0 | 0 | 0 | 2018-05-23 14:00 | 14 | 4 | 0 | 0 | 0 | 2018-05-23 14:00 | 14 | 4 | 87.4037 | 18.2578 | 0 | 2018-05-23 14:00 | 14 | 4 | 33.2134 | 6.9379 | 0
2018-05-23 15:00 | 15 | 4 | 0 | 0 | 0 | 2018-05-23 15:00 | 15 | 4 | 0 | 0 | 0 | 2018-05-23 15:00 | 15 | 4 | 87.2129 | 18.2179 | 0 | 2018-05-23 15:00 | 15 | 4 | 33.1409 | 6.9228 | 0
2018-05-23 16:00 | 16 | 4 | 0 | 0 | 0 | 2018-05-23 16:00 | 16 | 4 | 0 | 0 | 0 | 2018-05-23 16:00 | 16 | 4 | 86.9718 | 18.1675 | 0 | 2018-05-23 16:00 | 16 | 4 | 33.0493 | 6.9037 | 0
2018-05-23 17:00 | 17 | 4 | 0 | 0 | 0 | 2018-05-23 17:00 | 17 | 4 | 0 | 0 | 0 | 2018-05-23 17:00 | 17 | 4 | 87.1397 | 18.2026 | 0 | 2018-05-23 17:00 | 17 | 4 | 33.1131 | 6.917 | 0
2018-05-23 18:00 | 18 | 4 | 0 | 0 | 0 | 2018-05-23 18:00 | 18 | 4 | 0 | 0 | 0 | 2018-05-23 18:00 | 18 | 4 | 87.2435 | 18.2243 | 0 | 2018-05-23 18:00 | 18 | 4 | 33.1525 | 6.9252 | 0
2018-05-23 19:00 | 19 | 4 | 0 | 0 | 0 | 2018-05-23 19:00 | 19 | 4 | 0 | 0 | 0 | 2018-05-23 19:00 | 19 | 4 | 86.8894 | 18.1503 | 0 | 2018-05-23 19:00 | 19 | 4 | 33.018 | 6.8971 | 0
2018-05-23 20:00 | 20 | 4 | 0 | 0 | 0 | 2018-05-23 20:00 | 20 | 4 | 0 | 0 | 0 | 2018-05-23 20:00 | 20 | 4 | 87.1839 | 18.2118 | 0 | 2018-05-23 20:00 | 20 | 4 | 33.1299 | 6.9205 | 0
2018-05-23 21:00 | 21 | 4 | 0 | 0 | 0 | 2018-05-23 21:00 | 21 | 4 | 0 | 0 | 0 | 2018-05-23 21:00 | 21 | 4 | 87.2419 | 18.224 | 0 | 2018-05-23 21:00 | 21 | 4 | 33.1519 | 6.9251 | 0
2018-05-23 22:00 | 22 | 4 | 0 | 0 | 0 | 2018-05-23 22:00 | 22 | 4 | 0 | 0 | 0 | 2018-05-23 22:00 | 22 | 4 | 87.1733 | 18.2096 | 0 | 2018-05-23 22:00 | 22 | 4 | 33.1259 | 6.9197 | 0
2018-05-23 23:00 | 23 | 4 | 0 | 0 | 0 | 2018-05-23 23:00 | 23 | 4 | 0 | 0 | 0 | 2018-05-23 23:00 | 23 | 4 | 87.2557 | 18.2268 | 0 | 2018-05-23 23:00 | 23 | 4 | 33.1572 | 6.9262 | 0
2018-05-24 | 0 | 5 | 86.5492 | 18.0793 | 0 | 2018-05-24 | 0 | 5 | 0 | 0 | 0 | 2018-05-24 | 0 | 5 | 0 | 0 | 0 | 2018-05-24 | 0 | 5 | 0 | 0 | 0
2018-05-24 01:00 | 1 | 5 | 86.7201 | 18.115 | 0 | 2018-05-24 01:00 | 1 | 5 | 0 | 0 | 0 | 2018-05-24 01:00 | 1 | 5 | 0 | 0 | 0 | 2018-05-24 01:00 | 1 | 5 | 0 | 0 | 0
2018-05-24 02:00 | 2 | 5 | 86.5095 | 18.071 | 0 | 2018-05-24 02:00 | 2 | 5 | 0 | 0 | 0 | 2018-05-24 02:00 | 2 | 5 | 0 | 0 | 0 | 2018-05-24 02:00 | 2 | 5 | 0 | 0 | 0
2018-05-24 03:00 | 3 | 5 | 86.4576 | 18.0601 | 0 | 2018-05-24 03:00 | 3 | 5 | 0 | 0 | 0 | 2018-05-24 03:00 | 3 | 5 | 0 | 0 | 0 | 2018-05-24 03:00 | 3 | 5 | 0 | 0 | 0
2018-05-24 04:00 | 4 | 5 | 86.6316 | 18.0965 | 0 | 2018-05-24 04:00 | 4 | 5 | 0 | 0 | 0 | 2018-05-24 04:00 | 4 | 5 | 0 | 0 | 0 | 2018-05-24 04:00 | 4 | 5 | 0 | 0 | 0
2018-05-24 05:00 | 5 | 5 | 86.569 | 18.0834 | 0 | 2018-05-24 05:00 | 5 | 5 | 0 | 0 | 0 | 2018-05-24 05:00 | 5 | 5 | 0 | 0 | 0 | 2018-05-24 05:00 | 5 | 5 | 0 | 0 | 0
2018-05-24 06:00 | 6 | 5 | 86.6468 | 18.0997 | 0 | 2018-05-24 06:00 | 6 | 5 | 0 | 0 | 0 | 2018-05-24 06:00 | 6 | 5 | 0 | 0 | 0 | 2018-05-24 06:00 | 6 | 5 | 0 | 0 | 0
2018-05-24 07:00 | 7 | 5 | 86.6361 | 18.0974 | 0 | 2018-05-24 07:00 | 7 | 5 | 0 | 0 | 0 | 2018-05-24 07:00 | 7 | 5 | 0 | 0 | 0 | 2018-05-24 07:00 | 7 | 5 | 0 | 0 | 0
2018-05-24 08:00 | 8 | 5 | 86.6819 | 18.107 | 0 | 2018-05-24 08:00 | 8 | 5 | 0 | 0 | 0 | 2018-05-24 08:00 | 8 | 5 | 0 | 0 | 0 | 2018-05-24 08:00 | 8 | 5 | 0 | 0 | 0
2018-05-24 09:00 | 9 | 5 | 86.7094 | 18.1127 | 0 | 2018-05-24 09:00 | 9 | 5 | 0 | 0 | 0 | 2018-05-24 09:00 | 9 | 5 | 0 | 0 | 0 | 2018-05-24 09:00 | 9 | 5 | 0 | 0 | 0
2018-05-24 10:00 | 10 | 5 | 86.7933 | 18.1303 | 0 | 2018-05-24 10:00 | 10 | 5 | 0 | 0 | 0 | 2018-05-24 10:00 | 10 | 5 | 0 | 0 | 0 | 2018-05-24 10:00 | 10 | 5 | 0 | 0 | 0
2018-05-24 11:00 | 11 | 5 | 86.8009 | 18.1318 | 0 | 2018-05-24 11:00 | 11 | 5 | 0 | 0 | 0 | 2018-05-24 11:00 | 11 | 5 | 0 | 0 | 0 | 2018-05-24 11:00 | 11 | 5 | 0 | 0 | 0
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -

## Step 3. Avg Energy Calcs
Day of Week | Hour | Circuit #1 Average Energy (kWh) | Circuit #2 Average Energy (kWh) | Circuit #3 Average Energy (kWh) | Circuit #4 Average Energy (kWh) | Total Average kWh | % Light on per hour | % Light off per hour
1 | 0 | 18.0139 | 18.1315 | 0 | 6.89 | 43.0354 | 21.52% | 78.48%
1 | 1 | 18.0311 | 18.1634 | 0 | 6.9021 | 43.0966 | 21.55% | 78.45%
1 | 2 | 18.0088 | 18.1353 | 0 | 6.8914 | 43.0356 | 21.52% | 78.48%
1 | 3 | 18.0031 | 18.1287 | 0 | 6.8889 | 43.0206 | 21.51% | 78.49%
1 | 4 | 18.0158 | 18.1385 | 0 | 6.8926 | 43.047 | 21.52% | 78.48%
1 | 5 | 18.0133 | 18.1385 | 0 | 6.8926 | 43.0445 | 21.52% | 78.48%
1 | 6 | 18.0225 | 18.1427 | 0 | 6.8942 | 43.0594 | 21.53% | 78.47%
1 | 7 | 18.0244 | 18.1411 | 0 | 6.8936 | 43.0591 | 21.53% | 78.47%
1 | 8 | 18.027 | 18.1532 | 0 | 6.8982 | 43.0784 | 21.54% | 78.46%
1 | 9 | 18.0244 | 18.135 | 0 | 6.8913 | 43.0508 | 21.53% | 78.47%
1 | 10 | 18.0247 | 18.1427 | 0 | 6.8942 | 43.0616 | 21.53% | 78.47%
1 | 11 | 18.0031 | 18.1197 | 0 | 6.8855 | 43.0083 | 21.5% | 78.5%
1 | 12 | 17.9942 | 18.1137 | 0 | 6.8832 | 42.991 | 21.5% | 78.5%
1 | 13 | 17.9954 | 18.1245 | 0 | 6.8873 | 43.0073 | 21.5% | 78.5%
1 | 14 | 17.9878 | 18.1111 | 0 | 6.8822 | 42.9811 | 21.49% | 78.51%
1 | 15 | 18.0158 | 18.1417 | 0 | 6.8939 | 43.0514 | 21.53% | 78.47%
1 | 16 | 18.0365 | 18.1609 | 0 | 6.9011 | 43.0985 | 21.55% | 78.45%
1 | 17 | 18.0649 | 18.1704 | 0 | 6.9048 | 43.1401 | 21.57% | 78.43%
1 | 18 | 18.055 | 18.1567 | 0 | 6.8996 | 43.1113 | 21.56% | 78.44%
1 | 19 | 17.8976 | 17.9492 | 0 | 6.8207 | 42.6675 | 21.33% | 78.67%
1 | 20 | 18.0333 | 18.0875 | 0 | 6.8733 | 42.9941 | 21.5% | 78.5%
1 | 21 | 18.0391 | 18.1051 | 0 | 6.8799 | 43.0241 | 21.51% | 78.49%
1 | 22 | 18.0665 | 18.1334 | 0 | 6.8907 | 43.0907 | 21.55% | 78.45%
1 | 23 | 18.055 | 18.1181 | 0 | 6.8849 | 43.0581 | 21.53% | 78.47%
2 | 0 | 18.0499 | 18.1108 | 18.1599 | 13.7829 | 68.1035 | 34.05% | 65.95%
2 | 1 | 17.9734 | 18.0299 | 18.0748 | 13.7198 | 67.7979 | 33.9% | 66.1%
2 | 2 | 18.0464 | 18.0981 | 18.1404 | 13.7706 | 68.0556 | 34.03% | 65.97%
2 | 3 | 18.0225 | 18.085 | 18.122 | 13.7586 | 67.9881 | 33.99% | 66.01%
2 | 4 | 18.0697 | 18.1494 | 18.1793 | 13.8049 | 68.2033 | 34.1% | 65.9%
2 | 5 | 18.041 | 18.1258 | 18.1746 | 13.7941 | 68.1355 | 34.07% | 65.93%
2 | 6 | 18.0251 | 18.1003 | 18.1347 | 13.7693 | 68.0294 | 34.01% | 65.99%
2 | 7 | 18.0072 | 18.0748 | 18.1124 | 13.7511 | 67.9456 | 33.97% | 66.03%
2 | 8 | 18.0346 | 18.0786 | 18.1322 | 13.7601 | 68.0055 | 34% | 66%
2 | 9 | 18.0439 | 18.1162 | 18.1465 | 13.7798 | 68.0865 | 34.04% | 65.96%
2 | 10 | 18.012 | 18.0722 | 18.1137 | 13.7507 | 67.9486 | 33.97% | 66.03%
2 | 11 | 18.0088 | 18.0719 | 18.115 | 13.751 | 67.9467 | 33.97% | 66.03%
2 | 12 | 18.0458 | 18.1073 | 18.1436 | 13.7754 | 68.0721 | 34.04% | 65.96%
2 | 13 | 18.0487 | 18.0946 | 18.1207 | 13.7618 | 68.0257 | 34.01% | 65.99%
2 | 14 | 18.0436 | 18.1025 | 18.1296 | 13.7682 | 68.0439 | 34.02% | 65.98%
2 | 15 | 18.0346 | 18.0742 | 18.1188 | 13.7533 | 67.9809 | 33.99% | 66.01%
2 | 16 | 18.0375 | 18.0671 | 18.1076 | 13.7464 | 67.9587 | 33.98% | 66.02%
2 | 17 | 18.0155 | 18.0624 | 18.1054 | 13.7437 | 67.927 | 33.96% | 66.04%
2 | 18 | 18.0302 | 18.056 | 18.0885 | 13.7349 | 67.9096 | 33.95% | 66.05%
2 | 19 | 18.0082 | 18.0378 | 18.0812 | 13.7252 | 67.8524 | 33.93% | 66.07%
2 | 20 | 18.0101 | 18.0656 | 18.1086 | 13.7462 | 67.9304 | 33.97% | 66.03%
2 | 21 | 17.9957 | 18.064 | 18.0961 | 13.7408 | 67.8967 | 33.95% | 66.05%
2 | 22 | 18.0187 | 18.0799 | 18.0997 | 13.7482 | 67.9465 | 33.97% | 66.03%
2 | 23 | 18.057 | 18.1328 | 18.1497 | 13.7874 | 68.1268 | 34.06% | 65.94%
3 | 0 | 18.0614 | 0 | 0 | 0 | 18.0614 | 9.031% | 90.97%
3 | 1 | 18.0821 | 0 | 0 | 0 | 18.0821 | 9.041% | 90.96%
3 | 2 | 18.042 | 0 | 0 | 0 | 18.042 | 9.021% | 90.98%
3 | 3 | 18.0381 | 0 | 0 | 0 | 18.0381 | 9.019% | 90.98%
3 | 4 | 18.0413 | 0 | 0 | 0 | 18.0413 | 9.021% | 90.98%
3 | 5 | 18.0487 | 0 | 0 | 0 | 18.0487 | 9.024% | 90.98%
3 | 6 | 18.0617 | 0 | 0 | 0 | 18.0617 | 9.031% | 90.97%
3 | 7 | 18.0483 | 0 | 0 | 0 | 18.0483 | 9.024% | 90.98%
3 | 8 | 18.0589 | 0 | 0 | 0 | 18.0589 | 9.029% | 90.97%
3 | 9 | 18.0069 | 0 | 0 | 0 | 18.0069 | 9.003% | 91%
3 | 10 | 18.0213 | 0 | 0 | 0 | 18.0213 | 9.011% | 90.99%
3 | 11 | 18.1226 | 0 | 0 | 0 | 18.1226 | 9.061% | 90.94%
3 | 12 | 18.0939 | 0 | 0 | 0 | 18.0939 | 9.047% | 90.95%
3 | 13 | 18.0977 | 0 | 0 | 0 | 18.0977 | 9.049% | 90.95%
3 | 14 | 18.1475 | 0 | 0 | 0 | 18.1475 | 9.074% | 90.93%
3 | 15 | 18.1315 | 0 | 0 | 0 | 18.1315 | 9.066% | 90.93%
3 | 16 | 18.1248 | 0 | 0 | 0 | 18.1248 | 9.062% | 90.94%
3 | 17 | 18.1188 | 0 | 0 | 0 | 18.1188 | 9.059% | 90.94%
3 | 18 | 18.1134 | 0 | 0 | 0 | 18.1134 | 9.057% | 90.94%
3 | 19 | 18.1395 | 0 | 0 | 0 | 18.1395 | 9.07% | 90.93%
3 | 20 | 18.0955 | 0 | 0 | 0 | 18.0955 | 9.048% | 90.95%
3 | 21 | 18.0949 | 0 | 0 | 0 | 18.0949 | 9.047% | 90.95%
3 | 22 | 18.1137 | 0 | 0 | 0 | 18.1137 | 9.057% | 90.94%
3 | 23 | 18.1519 | 0 | 0 | 0 | 18.1519 | 9.076% | 90.92%
4 | 0 | 0 | 0 | 18.1047 | 6.8798 | 24.9846 | 12.49% | 87.51%
4 | 1 | 0 | 0 | 18.0713 | 6.8671 | 24.9384 | 12.47% | 87.53%
4 | 2 | 0 | 0 | 18.1239 | 6.8871 | 25.011 | 12.51% | 87.49%
4 | 3 | 0 | 0 | 18.1188 | 6.8851 | 25.0039 | 12.5% | 87.5%
4 | 4 | 0 | 0 | 18.1395 | 6.893 | 25.0325 | 12.52% | 87.48%
4 | 5 | 0 | 0 | 18.1781 | 6.9077 | 25.0857 | 12.54% | 87.46%
4 | 6 | 0 | 0 | 18.1656 | 6.9029 | 25.0686 | 12.53% | 87.47%
4 | 7 | 0 | 0 | 18.201 | 6.9164 | 25.1174 | 12.56% | 87.44%
4 | 8 | 0 | 0 | 18.2138 | 6.9212 | 25.135 | 12.57% | 87.43%
4 | 9 | 0 | 0 | 18.114 | 6.8833 | 24.9973 | 12.5% | 87.5%
4 | 10 | 0 | 0 | 18.1054 | 6.88 | 24.9854 | 12.49% | 87.51%
4 | 11 | 0 | 0 | 18.1516 | 6.8976 | 25.0492 | 12.52% | 87.48%
4 | 12 | 0 | 0 | 18.1583 | 6.9002 | 25.0585 | 12.53% | 87.47%
4 | 13 | 0 | 0 | 18.2265 | 6.9261 | 25.1526 | 12.58% | 87.42%
4 | 14 | 0 | 0 | 18.2578 | 6.9379 | 25.1957 | 12.6% | 87.4%
4 | 15 | 0 | 0 | 18.2179 | 6.9228 | 25.1407 | 12.57% | 87.43%
4 | 16 | 0 | 0 | 18.1675 | 6.9037 | 25.0712 | 12.54% | 87.46%
4 | 17 | 0 | 0 | 18.2026 | 6.917 | 25.1196 | 12.56% | 87.44%
4 | 18 | 0 | 0 | 18.2243 | 6.9252 | 25.1495 | 12.57% | 87.43%
4 | 19 | 0 | 0 | 18.1503 | 6.8971 | 25.0475 | 12.52% | 87.48%
4 | 20 | 0 | 0 | 18.2118 | 6.9205 | 25.1323 | 12.57% | 87.43%
4 | 21 | 0 | 0 | 18.224 | 6.9251 | 25.1491 | 12.57% | 87.43%
4 | 22 | 0 | 0 | 18.2096 | 6.9197 | 25.1293 | 12.56% | 87.44%
4 | 23 | 0 | 0 | 18.2268 | 6.9262 | 25.153 | 12.58% | 87.42%
5 | 0 | 18.0793 | 0 | 0 | 0 | 18.0793 | 9.04% | 90.96%
5 | 1 | 18.115 | 0 | 0 | 0 | 18.115 | 9.057% | 90.94%
5 | 2 | 18.071 | 0 | 0 | 0 | 18.071 | 9.035% | 90.96%
5 | 3 | 18.0601 | 0 | 0 | 0 | 18.0601 | 9.03% | 90.97%
5 | 4 | 18.0965 | 0 | 0 | 0 | 18.0965 | 9.048% | 90.95%
5 | 5 | 18.0834 | 0 | 0 | 0 | 18.0834 | 9.042% | 90.96%
5 | 6 | 18.0997 | 0 | 0 | 0 | 18.0997 | 9.05% | 90.95%
5 | 7 | 18.0974 | 0 | 0 | 0 | 18.0974 | 9.049% | 90.95%
5 | 8 | 18.107 | 0 | 0 | 0 | 18.107 | 9.053% | 90.95%
5 | 9 | 18.1127 | 0 | 0 | 0 | 18.1127 | 9.056% | 90.94%
5 | 10 | 18.1294 | 1.0654 | 1.0694 | 0.21348 | 20.4776 | 10.24% | 89.76%
5 | 11 | 18.1302 | 1.068 | 1.0698 | 0.8124 | 21.0805 | 10.54% | 89.46%
5 | 12 | 18.1044 | 1.1339 | 1.1371 | 0.86297 | 21.2383 | 10.62% | 89.38%
5 | 13 | 18.0948 | 1.1323 | 1.1362 | 0.86204 | 21.2253 | 10.61% | 89.39%
5 | 14 | 18.0953 | 1.1317 | 1.1355 | 0.8615 | 21.2239 | 10.61% | 89.39%
5 | 15 | 18.101 | 1.132 | 1.1365 | 0.86206 | 21.2316 | 10.62% | 89.38%
5 | 16 | 18.0803 | 1.133 | 1.1364 | 0.86238 | 21.2121 | 10.61% | 89.39%
5 | 17 | 18.104 | 1.1311 | 1.136 | 0.86149 | 21.2325 | 10.62% | 89.38%
5 | 18 | 18.1138 | 1.1311 | 1.1367 | 0.8618 | 21.2435 | 10.62% | 89.38%
5 | 19 | 18.0742 | 1.1339 | 1.1376 | 0.8632 | 21.209 | 10.6% | 89.4%
5 | 20 | 18.0845 | 1.1327 | 1.1377 | 0.86278 | 21.2177 | 10.61% | 89.39%
5 | 21 | 18.0926 | 1.1325 | 1.1356 | 0.86188 | 21.2226 | 10.61% | 89.39%
5 | 22 | 18.1035 | 1.1323 | 1.1351 | 0.86162 | 21.2325 | 10.62% | 89.38%
5 | 23 | 18.0822 | 1.1343 | 1.1376 | 0.86332 | 21.2174 | 10.61% | 89.39%
6 | 0 | 16.8853 | 18.1095 | 1.1378 | 7.314 | 43.4466 | 21.72% | 78.28%
6 | 1 | 16.8638 | 18.0782 | 1.136 | 7.3014 | 43.3795 | 21.69% | 78.31%
6 | 2 | 16.8964 | 18.1107 | 1.1383 | 7.3146 | 43.46 | 21.73% | 78.27%
6 | 3 | 16.842 | 18.0637 | 1.138 | 7.2966 | 43.3404 | 21.67% | 78.33%
6 | 4 | 16.8522 | 18.0601 | 1.1374 | 7.2951 | 43.3448 | 21.67% | 78.33%
6 | 5 | 16.886 | 18.0948 | 1.1383 | 7.3086 | 43.4278 | 21.71% | 78.29%
6 | 6 | 16.9266 | 18.1582 | 1.1382 | 7.3326 | 43.5556 | 21.78% | 78.22%
6 | 7 | 16.9568 | 18.1838 | 1.1392 | 7.3427 | 43.6225 | 21.81% | 78.19%
6 | 8 | 16.914 | 18.1279 | 1.1378 | 7.321 | 43.5007 | 21.75% | 78.25%
6 | 9 | 16.9072 | 18.1211 | 1.138 | 7.3184 | 43.4847 | 21.74% | 78.26%
6 | 10 | 16.9421 | 18.145 | 1.1388 | 7.3279 | 43.5539 | 21.78% | 78.22%
6 | 11 | 16.9397 | 18.1568 | 1.1372 | 7.3317 | 43.5655 | 21.78% | 78.22%
6 | 12 | 16.9789 | 18.1986 | 1.1363 | 7.3473 | 43.661 | 21.83% | 78.17%
6 | 13 | 16.9128 | 18.1328 | 1.1376 | 7.3228 | 43.506 | 21.75% | 78.25%
6 | 14 | 16.9281 | 18.144 | 1.1363 | 7.3265 | 43.5349 | 21.77% | 78.23%
6 | 15 | 16.8994 | 18.1045 | 1.1363 | 7.3115 | 43.4516 | 21.73% | 78.27%
6 | 16 | 16.9143 | 18.1222 | 1.1376 | 7.3187 | 43.4928 | 21.75% | 78.25%
6 | 17 | 16.8982 | 18.1208 | 1.1354 | 7.3174 | 43.4718 | 21.74% | 78.26%
6 | 18 | 16.8785 | 18.1069 | 1.1383 | 7.3132 | 43.4368 | 21.72% | 78.28%
6 | 19 | 16.8611 | 18.0765 | 1.1312 | 7.2989 | 43.3677 | 21.68% | 78.32%
6 | 20 | 16.8809 | 18.0746 | 1.1339 | 7.2992 | 43.3886 | 21.69% | 78.31%
6 | 21 | 16.9155 | 18.1149 | 1.1355 | 7.3151 | 43.481 | 21.74% | 78.26%
6 | 22 | 16.914 | 18.123 | 1.1356 | 7.3182 | 43.4908 | 21.75% | 78.25%
6 | 23 | 16.9203 | 18.1264 | 1.1346 | 7.3192 | 43.5005 | 21.75% | 78.25%
7 | 0 | 17.9671 | 0 | 18.0796 | 6.8702 | 42.9169 | 21.46% | 78.54%
7 | 1 | 17.9476 | 0 | 18.0758 | 6.8688 | 42.8922 | 21.45% | 78.55%
7 | 2 | 17.9757 | 0 | 18.0993 | 6.8777 | 42.9528 | 21.48% | 78.52%
7 | 3 | 17.9996 | 0 | 18.1108 | 6.8821 | 42.9925 | 21.5% | 78.5%
7 | 4 | 18.0289 | 0 | 18.1424 | 6.8941 | 43.0654 | 21.53% | 78.47%
7 | 5 | 18.0181 | 0 | 18.1443 | 6.8948 | 43.0572 | 21.53% | 78.47%
7 | 6 | 17.9903 | 0 | 18.1041 | 6.8796 | 42.974 | 21.49% | 78.51%
7 | 7 | 18.0044 | 0 | 18.1159 | 6.8841 | 43.0043 | 21.5% | 78.5%
7 | 8 | 18.0397 | 0 | 18.1634 | 6.9021 | 43.1052 | 21.55% | 78.45%
7 | 9 | 18.0671 | 0 | 18.1857 | 6.9106 | 43.1634 | 21.58% | 78.42%
7 | 10 | 18.0059 | 0 | 18.0981 | 6.8773 | 42.9813 | 21.49% | 78.51%
7 | 11 | 18.0002 | 0 | 18.1494 | 6.8968 | 43.0464 | 21.52% | 78.48%
7 | 12 | 18.0694 | 0 | 18.2048 | 6.9178 | 43.1921 | 21.6% | 78.4%
7 | 13 | 18.093 | 0 | 18.2396 | 6.931 | 43.2636 | 21.63% | 78.37%
7 | 14 | 18.0573 | 0 | 18.1908 | 6.9125 | 43.1606 | 21.58% | 78.42%
7 | 15 | 18.0799 | 0 | 18.2348 | 6.9292 | 43.2439 | 21.62% | 78.38%
7 | 16 | 18.0824 | 0 | 18.2482 | 6.9343 | 43.2649 | 21.63% | 78.37%
7 | 17 | 18.1201 | 0 | 18.2925 | 6.9511 | 43.3637 | 21.68% | 78.32%
7 | 18 | 18.062 | 0 | 18.2364 | 6.9298 | 43.2283 | 21.61% | 78.39%
7 | 19 | 18.041 | 0 | 18.1934 | 6.9135 | 43.1478 | 21.57% | 78.43%
7 | 20 | 17.989 | 0 | 18.1507 | 6.8973 | 43.037 | 21.52% | 78.48%
7 | 21 | 17.997 | 0 | 18.1577 | 6.8999 | 43.0546 | 21.53% | 78.47%
7 | 22 | 18.0107 | 0 | 18.1746 | 6.9063 | 43.0916 | 21.55% | 78.45%
7 | 23 | 18.011 | 0 | 18.1899 | 6.9122 | 43.1131 | 21.56% | 78.44%

## Step 4. Results
Day | Average Hourly kWh of all Circuits | Average Daily Weekday Electricity Usage (kWh) | Annual Weekday Electricity Usage (kWh/year) | TOTAL ANNUAL ELECTRICITY USAGE (kWh/year)
Monday | 67.9965 | 837.7067 | 218641.445 | 326131.9614
Tuesday | 18.0857
Wednesday | 25.0795 | Average Daily Weekend Electricity Usage (kWh) | Annual Weekend Electricity Usage (kWh/year) | Approximate % of measured lighting load
Thursday | 19.8828 | 1033.5627 | 107490.5164 | 34.23%
Friday | 43.4777
Saturday | 43.0964 |  |  | Remaining Unmeasured Lighting Load (kWh/year)
Sunday | 43.0339 |  |  | 626507.7273
Total Days used in Measurement Period
112.0418

## Step 4a. Hourly Results
Average kWh per HOUR
DAY | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | Total
Sunday | 43.0354 | 43.0966 | 43.0356 | 43.0206 | 43.047 | 43.0445 | 43.0594 | 43.0591 | 43.0784 | 43.0508 | 43.0616 | 43.0083 | 42.991 | 43.0073 | 42.9811 | 43.0514 | 43.0985 | 43.1401 | 43.1113 | 42.6675 | 42.9941 | 43.0241 | 43.0907 | 43.0581 | 1032.8127
Monday | 68.1035 | 67.7979 | 68.0556 | 67.9881 | 68.2033 | 68.1355 | 68.0294 | 67.9456 | 68.0055 | 68.0865 | 67.9486 | 67.9467 | 68.0721 | 68.0257 | 68.0439 | 67.9809 | 67.9587 | 67.927 | 67.9096 | 67.8524 | 67.9304 | 67.8967 | 67.9465 | 68.1268 | 1631.9168
Tuesday | 18.0614 | 18.0821 | 18.042 | 18.0381 | 18.0413 | 18.0487 | 18.0617 | 18.0483 | 18.0589 | 18.0069 | 18.0213 | 18.1226 | 18.0939 | 18.0977 | 18.1475 | 18.1315 | 18.1248 | 18.1188 | 18.1134 | 18.1395 | 18.0955 | 18.0949 | 18.1137 | 18.1519 | 434.0564
Wednesday | 24.9846 | 24.9384 | 25.011 | 25.0039 | 25.0325 | 25.0857 | 25.0686 | 25.1174 | 25.135 | 24.9973 | 24.9854 | 25.0492 | 25.0585 | 25.1526 | 25.1957 | 25.1407 | 25.0712 | 25.1196 | 25.1495 | 25.0475 | 25.1323 | 25.1491 | 25.1293 | 25.153 | 601.908
Thursday | 18.0793 | 18.115 | 18.071 | 18.0601 | 18.0965 | 18.0834 | 18.0997 | 18.0974 | 18.107 | 18.1127 | 20.4776 | 21.0805 | 21.2383 | 21.2253 | 21.2239 | 21.2316 | 21.2121 | 21.2325 | 21.2435 | 21.209 | 21.2177 | 21.2226 | 21.2325 | 21.2174 | 477.1866
Friday | 43.4466 | 43.3795 | 43.46 | 43.3404 | 43.3448 | 43.4278 | 43.5556 | 43.6225 | 43.5007 | 43.4847 | 43.5539 | 43.5655 | 43.661 | 43.506 | 43.5349 | 43.4516 | 43.4928 | 43.4718 | 43.4368 | 43.3677 | 43.3886 | 43.481 | 43.4908 | 43.5005 | 1043.4655
Saturday | 42.9169 | 42.8922 | 42.9528 | 42.9925 | 43.0654 | 43.0572 | 42.974 | 43.0043 | 43.1052 | 43.1634 | 42.9813 | 43.0464 | 43.1921 | 43.2636 | 43.1606 | 43.2439 | 43.2649 | 43.3637 | 43.2283 | 43.1478 | 43.037 | 43.0546 | 43.0916 | 43.1131 | 1034.3126