## Change Log
Entry # | Date | Name | New Document Name | Cell/Range Modified | Changes Made | Comments
1 | 2020-04-14 | Duncan Prahl | 2020_0414_ac_current_circuits_hourly | Change Log sheet | Change log sheet created
Orlando, Please change the following: 1. Put four columns on each Step1.x sheet, one for each circuit on a single datalogger. That way a single logger export will go into each sheet, with up to four channels from the logger per sheet 2. We need to develop an hourly schedule that can be used by the DEM team in thier calc tool to estimate the interactive effects. What we need to derive is an estimate of hours on and off on a weekday and weekend by comparing the total connected load to the time when the lights start being used and the hours when the lights are turned off.
| 2020-04-27 | Orlando Castillo | 2020_0427_ac_current_circuits_hourly | Results | Results sheet modified calcs | 1. changed the calculations include holiday days
[5 empty] | Raw Data tab | 1. included cells for user to input amount of holiday days that affect schedule 2. added cells that ask user if the panelboard is mixed or dedicated, based on that input the spreadsheet will determine what calculation to perform to determine the % measured load.
| 2020-06-10 | Duncan Prahl | 2020_0610_... | Step4 |  | Formatted Text, modified so calcs matched methodology in guide (Ave hour, day, etc.)
|  |  |  | Step4A |  | Rearranged Days
|  |  | 2020_0625 | Step 1.1 | Raw Data tab | 1. added cell that asks user if load is balanced or unbalanced. 2. user input cells for RMS V, PF and True RMS kW for each phase if load is unbalanced.
|  |  | 2020_0625 | step 2 | power calc | 1. added columns for each circuit that shows kW result for balanced and unbalanced load depending on user input in step 1.1 2. removed sqrt(3) factor in kW calculations since that is only necessary when calculating total panelboard kW
|  |  | 2020_0625 | step 3 | Ave Energy Calc | 1. adjusted function for kWh to determine if the input data is from a balanced or unbalanced load

## Intro
Introduction and Instructions
Input Facility Name, Type
Model Description
Measured variables: Average hourly amperage per circuit, Circuit voltage and power facto, true RMS power (kW) of all lighting measured.
General annual equation: Total lighting energy = Hourly current converted to kW, Sum kW per week (kWh) * 52
Model Instructions
The yellow cells are the input cells.
Data should only be input in the Raw Data Input tab (step 1)
Calculations are shown in Runtime Calculations and Annual Energy Calc
Determine if the panelboard load is balanced or unbalanced.
If unbalanced measure RMS Voltage, True RMS kW and power factor of each phase line
When measuring circuit(s) take note of what phase that circuit is attributed to
If measuring groups of circuits with a single sensor ensure all circuits are attributed to the same phase
Helpful links
to logger tools
to documentation

## Step 1.1 Raw Data
Datetime | Circuit #1 AC Current (Amps) | Circuit #2 AC Current (Amps) | Circuit #3 AC Current (Amps) | Circuit #4 AC Current (Amps) | 1 | *If the panelboard load is balanced input measured values in the Phase 1 column only
2018-02-01 10:00 | 86.7201 | 86.7018 | 87.0329 | 17.3735
2018-02-01 11:00 | 86.6697 | 86.92 | 87.0665 | 66.1149 |  |  | Voltage (V)
2018-02-01 12:00 | 86.6209 | 86.8498 | 87.0954 | 66.0992 |  | Line 1* | 211
2018-02-01 13:00 | 86.5003 | 86.7323 | 87.0253 | 66.0279 |  | Line 2 | 203.7
2018-02-01 14:00 | 86.54 | 86.6804 | 86.9703 | 65.9873 |  | Line 3 | 212
2018-02-01 15:00 | 86.4958 | 86.7079 | 87.0542 | 66.0296 |  | Line 4 | 210
2018-02-01 16:00 | 86.5171 | 86.7857 | 87.0405 | 66.054 |  | True RMS Power (kW) | 100
2018-02-01 17:00 | 86.3813 | 86.6392 | 87.0085 | 65.9861
2018-02-01 18:00 | 86.537 | 86.6407 | 87.0695 | 66.0099
2018-02-01 19:00 | 86.6224 | 86.8544 | 87.1382 | 66.1172 | 2 | How many holiday days affect the normal operating schedule?
2018-02-01 20:00 | 86.537 | 86.7628 | 87.1458 | 66.0853 |  | 0
2018-02-01 21:00 | 86.5171 | 86.746 | 86.981 | 66.0163
2018-02-01 22:00 | 86.5278 | 86.7292 | 86.9444 | 65.996
2018-02-01 23:00 | 86.5461 | 86.8818 | 87.1351 | 66.1264
2018-02-02 | 0 | 86.7842 | 87.1504 | 66.0951
2018-02-02 01:00 | 0 | 86.8605 | 87.0115 | 66.0714
2018-02-02 02:00 | 0 | 86.8482 | 87.1885 | 66.1339
2018-02-02 03:00 | 0 | 86.8681 | 87.1641 | 66.1322
2018-02-02 04:00 | 0 | 86.7994 | 87.1229 | 66.0905
2018-02-02 05:00 | 0 | 86.8055 | 87.1916 | 66.1189
2018-02-02 06:00 | 0 | 86.8086 | 87.1778 | 66.1148
2018-02-02 07:00 | 0 | 86.865 | 87.2572 | 66.1664
2018-02-02 08:00 | 0 | 86.7994 | 87.1473 | 66.0997
2018-02-02 09:00 | 0 | 86.8925 | 87.1641 | 66.1415
2018-02-02 10:00 | 0 | 86.8956 | 87.2297 | 66.1676
2018-02-02 11:00 | 0 | 86.7704 | 87.1031 | 66.0719
2018-02-02 12:00 | 0 | 86.8101 | 87.0329 | 66.0603
2018-02-02 13:00 | 0 | 86.8727 | 87.1366 | 66.1235
2018-02-02 14:00 | 0 | 86.7964 | 87.0344 | 66.0557
2018-02-02 15:00 | 0 | 86.6041 | 87.0344 | 65.9826
2018-02-02 16:00 | 0 | 86.8391 | 87.1321 | 66.1091
2018-02-02 17:00 | 0 | 86.804 | 86.9657 | 66.0325
2018-02-02 18:00 | 0 | 86.9017 | 87.187 | 66.1537
2018-02-02 19:00 | 0 | 86.4302 | 86.6423 | 65.7675
2018-02-02 20:00 | 0 | 86.6499 | 86.8513 | 65.9305
2018-02-02 21:00 | 0 | 86.6438 | 86.9703 | 65.9734
2018-02-02 22:00 | 0 | 86.6453 | 86.978 | 65.9769
2018-02-02 23:00 | 0 | 86.5202 | 86.9078 | 65.9026
2018-02-03 | 86.0121 | 0 | 86.5507 | 32.8893
2018-02-03 01:00 | 85.919 | 0 | 86.5324 | 32.8823
2018-02-03 02:00 | 86.0533 | 0 | 86.6453 | 32.9252
2018-02-03 03:00 | 86.1677 | 0 | 86.7002 | 32.9461
2018-02-03 04:00 | 86.3081 | 0 | 86.8513 | 33.0035
2018-02-03 05:00 | 86.2562 | 0 | 86.8605 | 33.007
2018-02-03 06:00 | 86.1234 | 0 | 86.6682 | 32.9339
2018-02-03 07:00 | 86.1906 | 0 | 86.7247 | 32.9554
2018-02-03 08:00 | 86.36 | 0 | 86.952 | 33.0418
2018-02-03 09:00 | 86.4912 | 0 | 87.0588 | 33.0823
2018-02-03 10:00 | 86.1982 | 0 | 86.6392 | 32.9229
2018-02-03 11:00 | 86.1707 | 0 | 86.8849 | 33.0163
2018-02-03 12:00 | 86.5019 | 0 | 87.1504 | 33.1172
2018-02-03 13:00 | 86.6148 | 0 | 87.3167 | 33.1803
2018-02-03 14:00 | 86.4439 | 0 | 87.0832 | 33.0916
2018-02-03 15:00 | 86.5522 | 0 | 87.2938 | 33.1716
2018-02-03 16:00 | 86.5644 | 0 | 87.3579 | 33.196
2018-02-03 17:00 | 86.7445 | 0 | 87.57 | 33.2766
2018-02-03 18:00 | 86.4668 | 0 | 87.3014 | 33.1745
2018-02-03 19:00 | 86.3661 | 0 | 87.0954 | 33.0963
2018-02-03 20:00 | 86.1173 | 0 | 86.891 | 33.0186
2018-02-03 21:00 | 86.1555 | 0 | 86.9245 | 33.0313
2018-02-03 22:00 | 86.2211 | 0 | 87.0054 | 33.0621
2018-02-03 23:00 | 86.2226 | 0 | 87.0787 | 33.0899
2018-02-04 | 86.2364 | 86.7994 | 0 | 32.9838
2018-02-04 01:00 | 86.3188 | 86.952 | 0 | 33.0418
2018-02-04 02:00 | 86.2119 | 86.8177 | 0 | 32.9907
2018-02-04 03:00 | 86.1845 | 86.7857 | 0 | 32.9786
2018-02-04 04:00 | 86.2455 | 86.833 | 0 | 32.9965
2018-02-04 05:00 | 86.2333 | 86.833 | 0 | 32.9965
2018-02-04 06:00 | 86.2776 | 86.8528 | 0 | 33.0041
2018-02-04 07:00 | 86.2867 | 86.8452 | 0 | 33.0012
2018-02-04 08:00 | 86.2989 | 86.9032 | 0 | 33.0232
2018-02-04 09:00 | 86.2867 | 86.8162 | 0 | 32.9902
2018-02-04 10:00 | 86.2882 | 86.8528 | 0 | 33.0041
2018-02-04 11:00 | 86.1845 | 86.743 | 0 | 32.9623
2018-02-04 12:00 | 86.1418 | 86.714 | 0 | 32.9513
2018-02-04 13:00 | 86.1479 | 86.7659 | 0 | 32.971
2018-02-04 14:00 | 86.1112 | 86.7018 | 0 | 32.9467
2018-02-04 15:00 | 86.2455 | 86.8482 | 0 | 33.0023
2018-02-04 16:00 | 86.3447 | 86.9398 | 0 | 33.0371
2018-02-04 17:00 | 86.4805 | 86.9856 | 0 | 33.0545
2018-02-04 18:00 | 86.4332 | 86.92 | 0 | 33.0296
2018-02-04 19:00 | 85.6794 | 85.9266 | 0 | 32.6521
2018-02-04 20:00 | 86.3294 | 86.5888 | 0 | 32.9037
2018-02-04 21:00 | 86.3569 | 86.6728 | 0 | 32.9357
2018-02-04 22:00 | 86.4881 | 86.8086 | 0 | 32.9873
2018-02-04 23:00 | 86.4332 | 86.7353 | 0 | 32.9594
2018-02-05 | 86.4088 | 86.7002 | 86.9352 | 65.9815
2018-02-05 01:00 | 86.0426 | 86.3127 | 86.5278 | 65.6794
2018-02-05 02:00 | 86.392 | 86.6392 | 86.8421 | 65.9229
2018-02-05 03:00 | 86.2776 | 86.5766 | 86.7536 | 65.8655
2018-02-05 04:00 | 86.5034 | 86.8849 | 87.0283 | 66.087
2018-02-05 05:00 | 86.3661 | 86.772 | 87.0054 | 66.0354
2018-02-05 06:00 | 86.2898 | 86.6499 | 86.8147 | 65.9165
2018-02-05 07:00 | 86.2043 | 86.5278 | 86.7079 | 65.8296
2018-02-05 08:00 | 86.3355 | 86.5461 | 86.8025 | 65.8725
2018-02-05 09:00 | 86.3798 | 86.7262 | 86.8711 | 65.967
2018-02-05 10:00 | 86.2272 | 86.5156 | 86.714 | 65.8272
2018-02-05 11:00 | 86.2119 | 86.5141 | 86.7201 | 65.829
2018-02-05 12:00 | 86.389 | 86.6835 | 86.8574 | 65.9455
2018-02-05 13:00 | 86.4027 | 86.6224 | 86.7475 | 65.8806
2018-02-05 14:00 | 86.3783 | 86.6606 | 86.7903 | 65.9113
2018-02-05 15:00 | 86.3355 | 86.5248 | 86.7384 | 65.84
2018-02-05 16:00 | 86.3493 | 86.4912 | 86.685 | 65.807
2018-02-05 17:00 | 86.244 | 86.4683 | 86.6743 | 65.7942
2018-02-05 18:00 | 86.3142 | 86.4378 | 86.5934 | 65.7519
2018-02-05 19:00 | 86.2089 | 86.3508 | 86.5583 | 65.7055
2018-02-05 20:00 | 86.2181 | 86.4836 | 86.6896 | 65.8058
2018-02-05 21:00 | 86.1494 | 86.4759 | 86.63 | 65.7802
2018-02-05 22:00 | 86.2593 | 86.5522 | 86.6468 | 65.8156
2018-02-05 23:00 | 86.4424 | 86.8055 | 86.8864 | 66.0029
2018-02-06 | 86.4637 | 0 | 0 | 0
2018-02-06 01:00 | 86.5629 | 0 | 0 | 0
2018-02-06 02:00 | 86.3706 | 0 | 0 | 0
2018-02-06 03:00 | 86.3523 | 0 | 0 | 0
2018-02-06 04:00 | 86.3676 | 0 | 0 | 0
2018-02-06 05:00 | 86.4027 | 0 | 0 | 0
2018-02-06 06:00 | 86.4652 | 0 | 0 | 0
2018-02-06 07:00 | 86.4012 | 0 | 0 | 0
2018-02-06 08:00 | 86.4515 | 0 | 0 | 0
2018-02-06 09:00 | 86.2028 | 0 | 0 | 0
2018-02-06 10:00 | 86.2715 | 0 | 0 | 0
2018-02-06 11:00 | 86.7567 | 0 | 0 | 0
2018-02-06 12:00 | 86.6194 | 0 | 0 | 0
2018-02-06 13:00 | 86.6377 | 0 | 0 | 0
2018-02-06 14:00 | 86.8757 | 0 | 0 | 0
2018-02-06 15:00 | 86.7994 | 0 | 0 | 0
2018-02-06 16:00 | 86.7674 | 0 | 0 | 0
2018-02-06 17:00 | 86.7384 | 0 | 0 | 0
2018-02-06 18:00 | 86.7124 | 0 | 0 | 0
2018-02-06 19:00 | 86.8376 | 0 | 0 | 0
2018-02-06 20:00 | 86.627 | 0 | 0 | 0
2018-02-06 21:00 | 86.6239 | 0 | 0 | 0
2018-02-06 22:00 | 86.714 | 0 | 0 | 0
2018-02-06 23:00 | 86.8971 | 0 | 0 | 0
2018-02-07 | 0 | 0 | 86.6712 | 32.9351
2018-02-07 01:00 | 0 | 0 | 86.511 | 32.8742
2018-02-07 02:00 | 0 | 0 | 86.7628 | 32.9699
2018-02-07 03:00 | 0 | 0 | 86.7384 | 32.9606
2018-02-07 04:00 | 0 | 0 | 86.8376 | 32.9983
2018-02-07 05:00 | 0 | 0 | 87.0222 | 33.0684
2018-02-07 06:00 | 0 | 0 | 86.9627 | 33.0458
2018-02-07 07:00 | 0 | 0 | 87.1321 | 33.1102
2018-02-07 08:00 | 0 | 0 | 87.1931 | 33.1334
2018-02-07 09:00 | 0 | 0 | 86.7155 | 32.9519
2018-02-07 10:00 | 0 | 0 | 86.6743 | 32.9362
2018-02-07 11:00 | 0 | 0 | 86.8956 | 33.0203
2018-02-07 12:00 | 0 | 0 | 86.9276 | 33.0325
2018-02-07 13:00 | 0 | 0 | 87.2541 | 33.1566
2018-02-07 14:00 | 0 | 0 | 87.4037 | 33.2134
2018-02-07 15:00 | 0 | 0 | 87.2129 | 33.1409
2018-02-07 16:00 | 0 | 0 | 86.9718 | 33.0493
2018-02-07 17:00 | 0 | 0 | 87.1397 | 33.1131
2018-02-07 18:00 | 0 | 0 | 87.2435 | 33.1525
2018-02-07 19:00 | 0 | 0 | 86.8894 | 33.018
2018-02-07 20:00 | 0 | 0 | 87.1839 | 33.1299
2018-02-07 21:00 | 0 | 0 | 87.2419 | 33.1519
2018-02-07 22:00 | 0 | 0 | 87.1733 | 33.1259
2018-02-07 23:00 | 0 | 0 | 87.2557 | 33.1572
2018-02-08 | 86.5492 | 0 | 0 | 0
2018-02-08 01:00 | 86.7201 | 0 | 0 | 0
2018-02-08 02:00 | 86.5095 | 0 | 0 | 0
2018-02-08 03:00 | 86.4576 | 0 | 0 | 0
2018-02-08 04:00 | 86.6316 | 0 | 0 | 0
2018-02-08 05:00 | 86.569 | 0 | 0 | 0
2018-02-08 06:00 | 86.6468 | 0 | 0 | 0
2018-02-08 07:00 | 86.6361 | 0 | 0 | 0
2018-02-08 08:00 | 86.6819 | 0 | 0 | 0
2018-02-08 09:00 | 86.7094 | 0 | 0 | 0
2018-02-08 10:00 | 86.7933 | 0 | 0 | 0
2018-02-08 11:00 | 86.8009 | 0 | 0 | 0
2018-02-08 12:00 | 86.6728 | 0 | 0 | 0
2018-02-08 13:00 | 86.6316 | 0 | 0 | 0
2018-02-08 14:00 | 86.6316 | 0 | 0 | 0
2018-02-08 15:00 | 86.6636 | 0 | 0 | 0
2018-02-08 16:00 | 86.5568 | 0 | 0 | 0
2018-02-08 17:00 | 86.6865 | 0 | 0 | 0
2018-02-08 18:00 | 86.7262 | 0 | 0 | 0
2018-02-08 19:00 | 86.5187 | 0 | 0 | 0
2018-02-08 20:00 | 86.5766 | 0 | 0 | 0
2018-02-08 21:00 | 86.6194 | 0 | 0 | 0
2018-02-08 22:00 | 86.6743 | 0 | 0 | 0
2018-02-08 23:00 | 86.5644 | 0 | 0 | 0
2018-02-09 | 86.2226 | 86.688 | 0 | 32.9414
2018-02-09 01:00 | 86.1128 | 86.5232 | 0 | 32.8788
2018-02-09 02:00 | 86.2791 | 86.6896 | 0 | 32.942
2018-02-09 03:00 | 86.0014 | 86.4485 | 0 | 32.8504
2018-02-09 04:00 | 86.0533 | 86.4347 | 0 | 32.8452
2018-02-09 05:00 | 86.2257 | 86.6117 | 0 | 32.9124
2018-02-09 06:00 | 86.4332 | 86.9352 | 0 | 33.0354
2018-02-09 07:00 | 86.5873 | 87.0619 | 0 | 33.0835
2018-02-09 08:00 | 86.3691 | 86.7811 | 0 | 32.9768
2018-02-09 09:00 | 86.334 | 86.7399 | 0 | 32.9612
2018-02-09 10:00 | 86.5126 | 86.862 | 0 | 33.0076
2018-02-09 11:00 | 86.5003 | 86.9306 | 0 | 33.0336
2018-02-09 12:00 | 86.7002 | 87.1412 | 0 | 33.1137
2018-02-09 13:00 | 86.363 | 86.8009 | 0 | 32.9843
2018-02-09 14:00 | 86.4408 | 86.8635 | 0 | 33.0081
2018-02-09 15:00 | 86.2943 | 86.6743 | 0 | 32.9362
2018-02-09 16:00 | 86.3706 | 86.7491 | 0 | 32.9647
2018-02-09 17:00 | 86.2882 | 86.7445 | 0 | 32.9629
2018-02-09 18:00 | 86.1875 | 86.6667 | 0 | 32.9333
2018-02-09 19:00 | 86.099 | 86.5431 | 0 | 32.8864
2018-02-09 20:00 | 86.1997 | 86.5187 | 0 | 32.8771
2018-02-09 21:00 | 86.3767 | 86.7247 | 0 | 32.9554
2018-02-09 22:00 | 86.3691 | 86.7659 | 0 | 32.971
2018-02-09 23:00 | 86.4012 | 86.7918 | 0 | 32.9809
2018-02-10 | 86.0121 | 0 | 86.5507 | 32.8893
2018-02-10 01:00 | 85.919 | 0 | 86.5324 | 32.8823
2018-02-10 02:00 | 86.0533 | 0 | 86.6453 | 32.9252
2018-02-10 03:00 | 86.1677 | 0 | 86.7002 | 32.9461
2018-02-10 04:00 | 86.3081 | 0 | 86.8513 | 33.0035
2018-02-10 05:00 | 86.2562 | 0 | 86.8605 | 33.007
2018-02-10 06:00 | 86.1234 | 0 | 86.6682 | 32.9339
2018-02-10 07:00 | 86.1906 | 0 | 86.7247 | 32.9554
2018-02-10 08:00 | 86.36 | 0 | 86.952 | 33.0418
2018-02-10 09:00 | 86.4912 | 0 | 87.0588 | 33.0823
2018-02-10 10:00 | 86.1982 | 0 | 86.6392 | 32.9229
2018-02-10 11:00 | 86.1707 | 0 | 86.8849 | 33.0163
2018-02-10 12:00 | 86.5019 | 0 | 87.1504 | 33.1172
2018-02-10 13:00 | 86.6148 | 0 | 87.3167 | 33.1803
2018-02-10 14:00 | 86.4439 | 0 | 87.0832 | 33.0916
2018-02-10 15:00 | 86.5522 | 0 | 87.2938 | 33.1716
2018-02-10 16:00 | 86.5644 | 0 | 87.3579 | 33.196
2018-02-10 17:00 | 86.7445 | 0 | 87.57 | 33.2766
2018-02-10 18:00 | 86.4668 | 0 | 87.3014 | 33.1745
2018-02-10 19:00 | 86.3661 | 0 | 87.0954 | 33.0963
2018-02-10 20:00 | 86.1173 | 0 | 86.891 | 33.0186
2018-02-10 21:00 | 86.1555 | 0 | 86.9245 | 33.0313
2018-02-10 22:00 | 86.2211 | 0 | 87.0054 | 33.0621
2018-02-10 23:00 | 86.2226 | 0 | 87.0787 | 33.0899
2018-02-11 | 86.2364 | 86.7994 | 0 | 32.9838
2018-02-11 01:00 | 86.3188 | 86.952 | 0 | 33.0418
2018-02-11 02:00 | 86.2119 | 86.8177 | 0 | 32.9907
2018-02-11 03:00 | 86.1845 | 86.7857 | 0 | 32.9786
2018-02-11 04:00 | 86.2455 | 86.833 | 0 | 32.9965
2018-02-11 05:00 | 86.2333 | 86.833 | 0 | 32.9965
2018-02-11 06:00 | 86.2776 | 86.8528 | 0 | 33.0041
2018-02-11 07:00 | 86.2867 | 86.8452 | 0 | 33.0012
2018-02-11 08:00 | 86.2989 | 86.9032 | 0 | 33.0232
2018-02-11 09:00 | 86.2867 | 86.8162 | 0 | 32.9902
2018-02-11 10:00 | 86.2882 | 86.8528 | 0 | 33.0041
2018-02-11 11:00 | 86.1845 | 86.743 | 0 | 32.9623
2018-02-11 12:00 | 86.1418 | 86.714 | 0 | 32.9513
2018-02-11 13:00 | 86.1479 | 86.7659 | 0 | 32.971
2018-02-11 14:00 | 86.1112 | 86.7018 | 0 | 32.9467
2018-02-11 15:00 | 86.2455 | 86.8482 | 0 | 33.0023
2018-02-11 16:00 | 86.3447 | 86.9398 | 0 | 33.0371
2018-02-11 17:00 | 86.4805 | 86.9856 | 0 | 33.0545
2018-02-11 18:00 | 86.4332 | 86.92 | 0 | 33.0296
2018-02-11 19:00 | 85.6794 | 85.9266 | 0 | 32.6521
2018-02-11 20:00 | 86.3294 | 86.5888 | 0 | 32.9037
2018-02-11 21:00 | 86.3569 | 86.6728 | 0 | 32.9357
2018-02-11 22:00 | 86.4881 | 86.8086 | 0 | 32.9873
2018-02-11 23:00 | 86.4332 | 86.7353 | 0 | 32.9594
2018-02-12 | 86.4088 | 86.7002 | 86.9352 | 65.9815
2018-02-12 01:00 | 86.0426 | 86.3127 | 86.5278 | 65.6794
2018-02-12 02:00 | 86.392 | 86.6392 | 86.8421 | 65.9229
2018-02-12 03:00 | 86.2776 | 86.5766 | 86.7536 | 65.8655
2018-02-12 04:00 | 86.5034 | 86.8849 | 87.0283 | 66.087
2018-02-12 05:00 | 86.3661 | 86.772 | 87.0054 | 66.0354
2018-02-12 06:00 | 86.2898 | 86.6499 | 86.8147 | 65.9165
2018-02-12 07:00 | 86.2043 | 86.5278 | 86.7079 | 65.8296
2018-02-12 08:00 | 86.3355 | 86.5461 | 86.8025 | 65.8725
2018-02-12 09:00 | 86.3798 | 86.7262 | 86.8711 | 65.967
2018-02-12 10:00 | 86.2272 | 86.5156 | 86.714 | 65.8272
2018-02-12 11:00 | 86.2119 | 86.5141 | 86.7201 | 65.829
2018-02-12 12:00 | 86.389 | 86.6835 | 86.8574 | 65.9455
2018-02-12 13:00 | 86.4027 | 86.6224 | 86.7475 | 65.8806
2018-02-12 14:00 | 86.3783 | 86.6606 | 86.7903 | 65.9113
2018-02-12 15:00 | 86.3355 | 86.5248 | 86.7384 | 65.84
2018-02-12 16:00 | 86.3493 | 86.4912 | 86.685 | 65.807
2018-02-12 17:00 | 86.244 | 86.4683 | 86.6743 | 65.7942
2018-02-12 18:00 | 86.3142 | 86.4378 | 86.5934 | 65.7519
2018-02-12 19:00 | 86.2089 | 86.3508 | 86.5583 | 65.7055
2018-02-12 20:00 | 86.2181 | 86.4836 | 86.6896 | 65.8058
2018-02-12 21:00 | 86.1494 | 86.4759 | 86.63 | 65.7802
2018-02-12 22:00 | 86.2593 | 86.5522 | 86.6468 | 65.8156
2018-02-12 23:00 | 86.4424 | 86.8055 | 86.8864 | 66.0029
2018-02-13 | 86.4637 | 0 | 0 | 0
2018-02-13 01:00 | 86.5629 | 0 | 0 | 0
2018-02-13 02:00 | 86.3706 | 0 | 0 | 0
2018-02-13 03:00 | 86.3523 | 0 | 0 | 0
2018-02-13 04:00 | 86.3676 | 0 | 0 | 0
2018-02-13 05:00 | 86.4027 | 0 | 0 | 0
2018-02-13 06:00 | 86.4652 | 0 | 0 | 0
2018-02-13 07:00 | 86.4012 | 0 | 0 | 0
2018-02-13 08:00 | 86.4515 | 0 | 0 | 0
2018-02-13 09:00 | 86.2028 | 0 | 0 | 0
2018-02-13 10:00 | 86.2715 | 0 | 0 | 0
2018-02-13 11:00 | 86.7567 | 0 | 0 | 0
2018-02-13 12:00 | 86.6194 | 0 | 0 | 0
2018-02-13 13:00 | 86.6377 | 0 | 0 | 0
2018-02-13 14:00 | 86.8757 | 0 | 0 | 0
2018-02-13 15:00 | 86.7994 | 0 | 0 | 0
2018-02-13 16:00 | 86.7674 | 0 | 0 | 0
2018-02-13 17:00 | 86.7384 | 0 | 0 | 0
2018-02-13 18:00 | 86.7124 | 0 | 0 | 0
2018-02-13 19:00 | 86.8376 | 0 | 0 | 0
2018-02-13 20:00 | 86.627 | 0 | 0 | 0
2018-02-13 21:00 | 86.6239 | 0 | 0 | 0
2018-02-13 22:00 | 86.714 | 0 | 0 | 0
2018-02-13 23:00 | 86.8971 | 0 | 0 | 0
2018-02-14 | 0 | 0 | 86.6712 | 32.9351
2018-02-14 01:00 | 0 | 0 | 86.511 | 32.8742
2018-02-14 02:00 | 0 | 0 | 86.7628 | 32.9699
2018-02-14 03:00 | 0 | 0 | 86.7384 | 32.9606
2018-02-14 04:00 | 0 | 0 | 86.8376 | 32.9983
2018-02-14 05:00 | 0 | 0 | 87.0222 | 33.0684
2018-02-14 06:00 | 0 | 0 | 86.9627 | 33.0458
2018-02-14 07:00 | 0 | 0 | 87.1321 | 33.1102
2018-02-14 08:00 | 0 | 0 | 87.1931 | 33.1334
2018-02-14 09:00 | 0 | 0 | 86.7155 | 32.9519
2018-02-14 10:00 | 0 | 0 | 86.6743 | 32.9362
2018-02-14 11:00 | 0 | 0 | 86.8956 | 33.0203
2018-02-14 12:00 | 0 | 0 | 86.9276 | 33.0325
2018-02-14 13:00 | 0 | 0 | 87.2541 | 33.1566
2018-02-14 14:00 | 0 | 0 | 87.4037 | 33.2134
2018-02-14 15:00 | 0 | 0 | 87.2129 | 33.1409
2018-02-14 16:00 | 0 | 0 | 86.9718 | 33.0493
2018-02-14 17:00 | 0 | 0 | 87.1397 | 33.1131
2018-02-14 18:00 | 0 | 0 | 87.2435 | 33.1525
2018-02-14 19:00 | 0 | 0 | 86.8894 | 33.018
2018-02-14 20:00 | 0 | 0 | 87.1839 | 33.1299
2018-02-14 21:00 | 0 | 0 | 87.2419 | 33.1519
2018-02-14 22:00 | 0 | 0 | 87.1733 | 33.1259
2018-02-14 23:00 | 0 | 0 | 87.2557 | 33.1572
2018-02-15 | 86.5492 | 0 | 0 | 0
2018-02-15 01:00 | 86.7201 | 0 | 0 | 0
2018-02-15 02:00 | 86.5095 | 0 | 0 | 0
2018-02-15 03:00 | 86.4576 | 0 | 0 | 0
2018-02-15 04:00 | 86.6316 | 0 | 0 | 0
2018-02-15 05:00 | 86.569 | 0 | 0 | 0
2018-02-15 06:00 | 86.6468 | 0 | 0 | 0
2018-02-15 07:00 | 86.6361 | 0 | 0 | 0
2018-02-15 08:00 | 86.6819 | 0 | 0 | 0
2018-02-15 09:00 | 86.7094 | 0 | 0 | 0
2018-02-15 10:00 | 86.7933 | 0 | 0 | 0
2018-02-15 11:00 | 86.8009 | 0 | 0 | 0
2018-02-15 12:00 | 86.6728 | 0 | 0 | 0
2018-02-15 13:00 | 86.6316 | 0 | 0 | 0
2018-02-15 14:00 | 86.6316 | 0 | 0 | 0
2018-02-15 15:00 | 86.6636 | 0 | 0 | 0
2018-02-15 16:00 | 86.5568 | 0 | 0 | 0
2018-02-15 17:00 | 86.6865 | 0 | 0 | 0
2018-02-15 18:00 | 86.7262 | 0 | 0 | 0
2018-02-15 19:00 | 86.5187 | 0 | 0 | 0
2018-02-15 20:00 | 86.5766 | 0 | 0 | 0
2018-02-15 21:00 | 86.6194 | 0 | 0 | 0
2018-02-15 22:00 | 86.6743 | 0 | 0 | 0
2018-02-15 23:00 | 86.5644 | 0 | 0 | 0
2018-02-16 | 86.2226 | 86.688 | 0 | 32.9414
2018-02-16 01:00 | 86.1128 | 86.5232 | 0 | 32.8788
2018-02-16 02:00 | 86.2791 | 86.6896 | 0 | 32.942
2018-02-16 03:00 | 86.0014 | 86.4485 | 0 | 32.8504
2018-02-16 04:00 | 86.0533 | 86.4347 | 0 | 32.8452
2018-02-16 05:00 | 86.2257 | 86.6117 | 0 | 32.9124
2018-02-16 06:00 | 86.4332 | 86.9352 | 0 | 33.0354
2018-02-16 07:00 | 86.5873 | 87.0619 | 0 | 33.0835
2018-02-16 08:00 | 86.3691 | 86.7811 | 0 | 32.9768
2018-02-16 09:00 | 86.334 | 86.7399 | 0 | 32.9612
2018-02-16 10:00 | 86.5126 | 86.862 | 0 | 33.0076
2018-02-16 11:00 | 86.5003 | 86.9306 | 0 | 33.0336
2018-02-16 12:00 | 86.7002 | 87.1412 | 0 | 33.1137
2018-02-16 13:00 | 86.363 | 86.8009 | 0 | 32.9843
2018-02-16 14:00 | 86.4408 | 86.8635 | 0 | 33.0081
2018-02-16 15:00 | 86.2943 | 86.6743 | 0 | 32.9362
2018-02-16 16:00 | 86.3706 | 86.7491 | 0 | 32.9647
2018-02-16 17:00 | 86.2882 | 86.7445 | 0 | 32.9629
2018-02-16 18:00 | 86.1875 | 86.6667 | 0 | 32.9333
2018-02-16 19:00 | 86.099 | 86.5431 | 0 | 32.8864
2018-02-16 20:00 | 86.1997 | 86.5187 | 0 | 32.8771
2018-02-16 21:00 | 86.3767 | 86.7247 | 0 | 32.9554
2018-02-16 22:00 | 86.3691 | 86.7659 | 0 | 32.971
2018-02-16 23:00 | 86.4012 | 86.7918 | 0 | 32.9809
2018-02-17 | 86.0121 | 0 | 86.5507 | 32.8893
2018-02-17 01:00 | 85.919 | 0 | 86.5324 | 32.8823
2018-02-17 02:00 | 86.0533 | 0 | 86.6453 | 32.9252
2018-02-17 03:00 | 86.1677 | 0 | 86.7002 | 32.9461
2018-02-17 04:00 | 86.3081 | 0 | 86.8513 | 33.0035
2018-02-17 05:00 | 86.2562 | 0 | 86.8605 | 33.007
2018-02-17 06:00 | 86.1234 | 0 | 86.6682 | 32.9339
2018-02-17 07:00 | 86.1906 | 0 | 86.7247 | 32.9554
2018-02-17 08:00 | 86.36 | 0 | 86.952 | 33.0418
2018-02-17 09:00 | 86.4912 | 0 | 87.0588 | 33.0823
2018-02-17 10:00 | 86.1982 | 0 | 86.6392 | 32.9229
2018-02-17 11:00 | 86.1707 | 0 | 86.8849 | 33.0163
2018-02-17 12:00 | 86.5019 | 0 | 87.1504 | 33.1172
2018-02-17 13:00 | 86.6148 | 0 | 87.3167 | 33.1803
2018-02-17 14:00 | 86.4439 | 0 | 87.0832 | 33.0916
2018-02-17 15:00 | 86.5522 | 0 | 87.2938 | 33.1716
2018-02-17 16:00 | 86.5644 | 0 | 87.3579 | 33.196
2018-02-17 17:00 | 86.7445 | 0 | 87.57 | 33.2766
2018-02-17 18:00 | 86.4668 | 0 | 87.3014 | 33.1745
2018-02-17 19:00 | 86.3661 | 0 | 87.0954 | 33.0963
2018-02-17 20:00 | 86.1173 | 0 | 86.891 | 33.0186
2018-02-17 21:00 | 86.1555 | 0 | 86.9245 | 33.0313
2018-02-17 22:00 | 86.2211 | 0 | 87.0054 | 33.0621
2018-02-17 23:00 | 86.2226 | 0 | 87.0787 | 33.0899
2018-02-18 | 86.2364 | 86.7994 | 0 | 32.9838
2018-02-18 01:00 | 86.3188 | 86.952 | 0 | 33.0418
2018-02-18 02:00 | 86.2119 | 86.8177 | 0 | 32.9907
2018-02-18 03:00 | 86.1845 | 86.7857 | 0 | 32.9786
2018-02-18 04:00 | 86.2455 | 86.833 | 0 | 32.9965
2018-02-18 05:00 | 86.2333 | 86.833 | 0 | 32.9965
2018-02-18 06:00 | 86.2776 | 86.8528 | 0 | 33.0041
2018-02-18 07:00 | 86.2867 | 86.8452 | 0 | 33.0012
2018-02-18 08:00 | 86.2989 | 86.9032 | 0 | 33.0232
2018-02-18 09:00 | 86.2867 | 86.8162 | 0 | 32.9902
2018-02-18 10:00 | 86.2882 | 86.8528 | 0 | 33.0041
2018-02-18 11:00 | 86.1845 | 86.743 | 0 | 32.9623
2018-02-18 12:00 | 86.1418 | 86.714 | 0 | 32.9513
2018-02-18 13:00 | 86.1479 | 86.7659 | 0 | 32.971
2018-02-18 14:00 | 86.1112 | 86.7018 | 0 | 32.9467
2018-02-18 15:00 | 86.2455 | 86.8482 | 0 | 33.0023
2018-02-18 16:00 | 86.3447 | 86.9398 | 0 | 33.0371
2018-02-18 17:00 | 86.4805 | 86.9856 | 0 | 33.0545
2018-02-18 18:00 | 86.4332 | 86.92 | 0 | 33.0296
2018-02-18 19:00 | 85.6794 | 85.9266 | 0 | 32.6521
2018-02-18 20:00 | 86.3294 | 86.5888 | 0 | 32.9037
2018-02-18 21:00 | 86.3569 | 86.6728 | 0 | 32.9357
2018-02-18 22:00 | 86.4881 | 86.8086 | 0 | 32.9873
2018-02-18 23:00 | 86.4332 | 86.7353 | 0 | 32.9594
2018-02-19 | 86.4088 | 86.7002 | 86.9352 | 65.9815
2018-02-19 01:00 | 86.0426 | 86.3127 | 86.5278 | 65.6794
2018-02-19 02:00 | 86.392 | 86.6392 | 86.8421 | 65.9229
2018-02-19 03:00 | 86.2776 | 86.5766 | 86.7536 | 65.8655
2018-02-19 04:00 | 86.5034 | 86.8849 | 87.0283 | 66.087
2018-02-19 05:00 | 86.3661 | 86.772 | 87.0054 | 66.0354
2018-02-19 06:00 | 86.2898 | 86.6499 | 86.8147 | 65.9165
2018-02-19 07:00 | 86.2043 | 86.5278 | 86.7079 | 65.8296
2018-02-19 08:00 | 86.3355 | 86.5461 | 86.8025 | 65.8725
2018-02-19 09:00 | 86.3798 | 86.7262 | 86.8711 | 65.967
2018-02-19 10:00 | 86.2272 | 86.5156 | 86.714 | 65.8272
2018-02-19 11:00 | 86.2119 | 86.5141 | 86.7201 | 65.829
2018-02-19 12:00 | 86.389 | 86.6835 | 86.8574 | 65.9455
2018-02-19 13:00 | 86.4027 | 86.6224 | 86.7475 | 65.8806
2018-02-19 14:00 | 86.3783 | 86.6606 | 86.7903 | 65.9113
2018-02-19 15:00 | 86.3355 | 86.5248 | 86.7384 | 65.84
2018-02-19 16:00 | 86.3493 | 86.4912 | 86.685 | 65.807
2018-02-19 17:00 | 86.244 | 86.4683 | 86.6743 | 65.7942
2018-02-19 18:00 | 86.3142 | 86.4378 | 86.5934 | 65.7519
2018-02-19 19:00 | 86.2089 | 86.3508 | 86.5583 | 65.7055
2018-02-19 20:00 | 86.2181 | 86.4836 | 86.6896 | 65.8058
2018-02-19 21:00 | 86.1494 | 86.4759 | 86.63 | 65.7802
2018-02-19 22:00 | 86.2593 | 86.5522 | 86.6468 | 65.8156
2018-02-19 23:00 | 86.4424 | 86.8055 | 86.8864 | 66.0029
2018-02-20 | 86.4637 | 0 | 0 | 0
2018-02-20 01:00 | 86.5629 | 0 | 0 | 0
2018-02-20 02:00 | 86.3706 | 0 | 0 | 0
2018-02-20 03:00 | 86.3523 | 0 | 0 | 0
2018-02-20 04:00 | 86.3676 | 0 | 0 | 0
2018-02-20 05:00 | 86.4027 | 0 | 0 | 0
2018-02-20 06:00 | 86.4652 | 0 | 0 | 0
2018-02-20 07:00 | 86.4012 | 0 | 0 | 0
2018-02-20 08:00 | 86.4515 | 0 | 0 | 0
2018-02-20 09:00 | 86.2028 | 0 | 0 | 0
2018-02-20 10:00 | 86.2715 | 0 | 0 | 0
2018-02-20 11:00 | 86.7567 | 0 | 0 | 0
2018-02-20 12:00 | 86.6194 | 0 | 0 | 0
2018-02-20 13:00 | 86.6377 | 0 | 0 | 0
2018-02-20 14:00 | 86.8757 | 0 | 0 | 0
2018-02-20 15:00 | 86.7994 | 0 | 0 | 0
2018-02-20 16:00 | 86.7674 | 0 | 0 | 0
2018-02-20 17:00 | 86.7384 | 0 | 0 | 0
2018-02-20 18:00 | 86.7124 | 0 | 0 | 0
2018-02-20 19:00 | 86.8376 | 0 | 0 | 0
2018-02-20 20:00 | 86.627 | 0 | 0 | 0
2018-02-20 21:00 | 86.6239 | 0 | 0 | 0
2018-02-20 22:00 | 86.714 | 0 | 0 | 0
2018-02-20 23:00 | 86.8971 | 0 | 0 | 0
2018-02-21 | 0 | 0 | 86.6712 | 32.9351
2018-02-21 01:00 | 0 | 0 | 86.511 | 32.8742
2018-02-21 02:00 | 0 | 0 | 86.7628 | 32.9699
2018-02-21 03:00 | 0 | 0 | 86.7384 | 32.9606
2018-02-21 04:00 | 0 | 0 | 86.8376 | 32.9983
2018-02-21 05:00 | 0 | 0 | 87.0222 | 33.0684
2018-02-21 06:00 | 0 | 0 | 86.9627 | 33.0458
2018-02-21 07:00 | 0 | 0 | 87.1321 | 33.1102
2018-02-21 08:00 | 0 | 0 | 87.1931 | 33.1334
2018-02-21 09:00 | 0 | 0 | 86.7155 | 32.9519
2018-02-21 10:00 | 0 | 0 | 86.6743 | 32.9362
2018-02-21 11:00 | 0 | 0 | 86.8956 | 33.0203
2018-02-21 12:00 | 0 | 0 | 86.9276 | 33.0325
2018-02-21 13:00 | 0 | 0 | 87.2541 | 33.1566
2018-02-21 14:00 | 0 | 0 | 87.4037 | 33.2134
2018-02-21 15:00 | 0 | 0 | 87.2129 | 33.1409
2018-02-21 16:00 | 0 | 0 | 86.9718 | 33.0493
2018-02-21 17:00 | 0 | 0 | 87.1397 | 33.1131
2018-02-21 18:00 | 0 | 0 | 87.2435 | 33.1525
2018-02-21 19:00 | 0 | 0 | 86.8894 | 33.018
2018-02-21 20:00 | 0 | 0 | 87.1839 | 33.1299
2018-02-21 21:00 | 0 | 0 | 87.2419 | 33.1519
2018-02-21 22:00 | 0 | 0 | 87.1733 | 33.1259
2018-02-21 23:00 | 0 | 0 | 87.2557 | 33.1572
2018-02-22 | 86.5492 | 0 | 0 | 0
2018-02-22 01:00 | 86.7201 | 0 | 0 | 0
2018-02-22 02:00 | 86.5095 | 0 | 0 | 0
2018-02-22 03:00 | 86.4576 | 0 | 0 | 0
2018-02-22 04:00 | 86.6316 | 0 | 0 | 0
2018-02-22 05:00 | 86.569 | 0 | 0 | 0
2018-02-22 06:00 | 86.6468 | 0 | 0 | 0
2018-02-22 07:00 | 86.6361 | 0 | 0 | 0
2018-02-22 08:00 | 86.6819 | 0 | 0 | 0
2018-02-22 09:00 | 86.7094 | 0 | 0 | 0
2018-02-22 10:00 | 86.7933 | 0 | 0 | 0
2018-02-22 11:00 | 86.8009 | 0 | 0 | 0
2018-02-22 12:00 | 86.6728 | 0 | 0 | 0
2018-02-22 13:00 | 86.6316 | 0 | 0 | 0
2018-02-22 14:00 | 86.6316 | 0 | 0 | 0
2018-02-22 15:00 | 86.6636 | 0 | 0 | 0
2018-02-22 16:00 | 86.5568 | 0 | 0 | 0
2018-02-22 17:00 | 86.6865 | 0 | 0 | 0
2018-02-22 18:00 | 86.7262 | 0 | 0 | 0
2018-02-22 19:00 | 86.5187 | 0 | 0 | 0
2018-02-22 20:00 | 86.5766 | 0 | 0 | 0
2018-02-22 21:00 | 86.6194 | 0 | 0 | 0
2018-02-22 22:00 | 86.6743 | 0 | 0 | 0
2018-02-22 23:00 | 86.5644 | 0 | 0 | 0
2018-02-23 | 86.2226 | 86.688 | 0 | 32.9414
2018-02-23 01:00 | 86.1128 | 86.5232 | 0 | 32.8788
2018-02-23 02:00 | 86.2791 | 86.6896 | 0 | 32.942
2018-02-23 03:00 | 86.0014 | 86.4485 | 0 | 32.8504
2018-02-23 04:00 | 86.0533 | 86.4347 | 0 | 32.8452
2018-02-23 05:00 | 86.2257 | 86.6117 | 0 | 32.9124
2018-02-23 06:00 | 86.4332 | 86.9352 | 0 | 33.0354
2018-02-23 07:00 | 86.5873 | 87.0619 | 0 | 33.0835
2018-02-23 08:00 | 86.3691 | 86.7811 | 0 | 32.9768
2018-02-23 09:00 | 86.334 | 86.7399 | 0 | 32.9612
2018-02-23 10:00 | 86.5126 | 86.862 | 0 | 33.0076
2018-02-23 11:00 | 86.5003 | 86.9306 | 0 | 33.0336
2018-02-23 12:00 | 86.7002 | 87.1412 | 0 | 33.1137
2018-02-23 13:00 | 86.363 | 86.8009 | 0 | 32.9843
2018-02-23 14:00 | 86.4408 | 86.8635 | 0 | 33.0081
2018-02-23 15:00 | 86.2943 | 86.6743 | 0 | 32.9362
2018-02-23 16:00 | 86.3706 | 86.7491 | 0 | 32.9647
2018-02-23 17:00 | 86.2882 | 86.7445 | 0 | 32.9629
2018-02-23 18:00 | 86.1875 | 86.6667 | 0 | 32.9333
2018-02-23 19:00 | 86.099 | 86.5431 | 0 | 32.8864
2018-02-23 20:00 | 86.1997 | 86.5187 | 0 | 32.8771
2018-02-23 21:00 | 86.3767 | 86.7247 | 0 | 32.9554
2018-02-23 22:00 | 86.3691 | 86.7659 | 0 | 32.971
2018-02-23 23:00 | 86.4012 | 86.7918 | 0 | 32.9809
2018-02-24 | 86.0121 | 0 | 86.5507 | 32.8893
2018-02-24 01:00 | 85.919 | 0 | 86.5324 | 32.8823
2018-02-24 02:00 | 86.0533 | 0 | 86.6453 | 32.9252
2018-02-24 03:00 | 86.1677 | 0 | 86.7002 | 32.9461
2018-02-24 04:00 | 86.3081 | 0 | 86.8513 | 33.0035
2018-02-24 05:00 | 86.2562 | 0 | 86.8605 | 33.007
2018-02-24 06:00 | 86.1234 | 0 | 86.6682 | 32.9339
2018-02-24 07:00 | 86.1906 | 0 | 86.7247 | 32.9554
2018-02-24 08:00 | 86.36 | 0 | 86.952 | 33.0418
2018-02-24 09:00 | 86.4912 | 0 | 87.0588 | 33.0823
2018-02-24 10:00 | 86.1982 | 0 | 86.6392 | 32.9229
2018-02-24 11:00 | 86.1707 | 0 | 86.8849 | 33.0163
2018-02-24 12:00 | 86.5019 | 0 | 87.1504 | 33.1172
2018-02-24 13:00 | 86.6148 | 0 | 87.3167 | 33.1803
2018-02-24 14:00 | 86.4439 | 0 | 87.0832 | 33.0916
2018-02-24 15:00 | 86.5522 | 0 | 87.2938 | 33.1716
2018-02-24 16:00 | 86.5644 | 0 | 87.3579 | 33.196
2018-02-24 17:00 | 86.7445 | 0 | 87.57 | 33.2766
2018-02-24 18:00 | 86.4668 | 0 | 87.3014 | 33.1745
2018-02-24 19:00 | 86.3661 | 0 | 87.0954 | 33.0963
2018-02-24 20:00 | 86.1173 | 0 | 86.891 | 33.0186
2018-02-24 21:00 | 86.1555 | 0 | 86.9245 | 33.0313
2018-02-24 22:00 | 86.2211 | 0 | 87.0054 | 33.0621
2018-02-24 23:00 | 86.2226 | 0 | 87.0787 | 33.0899
2018-02-25 | 86.2364 | 86.7994 | 0 | 32.9838
2018-02-25 01:00 | 86.3188 | 86.952 | 0 | 33.0418
2018-02-25 02:00 | 86.2119 | 86.8177 | 0 | 32.9907
2018-02-25 03:00 | 86.1845 | 86.7857 | 0 | 32.9786
2018-02-25 04:00 | 86.2455 | 86.833 | 0 | 32.9965
2018-02-25 05:00 | 86.2333 | 86.833 | 0 | 32.9965
2018-02-25 06:00 | 86.2776 | 86.8528 | 0 | 33.0041
2018-02-25 07:00 | 86.2867 | 86.8452 | 0 | 33.0012
2018-02-25 08:00 | 86.2989 | 86.9032 | 0 | 33.0232
2018-02-25 09:00 | 86.2867 | 86.8162 | 0 | 32.9902
2018-02-25 10:00 | 86.2882 | 86.8528 | 0 | 33.0041
2018-02-25 11:00 | 86.1845 | 86.743 | 0 | 32.9623
2018-02-25 12:00 | 86.1418 | 86.714 | 0 | 32.9513
2018-02-25 13:00 | 86.1479 | 86.7659 | 0 | 32.971
2018-02-25 14:00 | 86.1112 | 86.7018 | 0 | 32.9467
2018-02-25 15:00 | 86.2455 | 86.8482 | 0 | 33.0023
2018-02-25 16:00 | 86.3447 | 86.9398 | 0 | 33.0371
2018-02-25 17:00 | 86.4805 | 86.9856 | 0 | 33.0545
2018-02-25 18:00 | 86.4332 | 86.92 | 0 | 33.0296
2018-02-25 19:00 | 85.6794 | 85.9266 | 0 | 32.6521
2018-02-25 20:00 | 86.3294 | 86.5888 | 0 | 32.9037
2018-02-25 21:00 | 86.3569 | 86.6728 | 0 | 32.9357
2018-02-25 22:00 | 86.4881 | 86.8086 | 0 | 32.9873
2018-02-25 23:00 | 86.4332 | 86.7353 | 0 | 32.9594
2018-02-26 | 86.4088 | 86.7002 | 86.9352 | 65.9815
2018-02-26 01:00 | 86.0426 | 86.3127 | 86.5278 | 65.6794
2018-02-26 02:00 | 86.392 | 86.6392 | 86.8421 | 65.9229
2018-02-26 03:00 | 86.2776 | 86.5766 | 86.7536 | 65.8655
2018-02-26 04:00 | 86.5034 | 86.8849 | 87.0283 | 66.087
2018-02-26 05:00 | 86.3661 | 86.772 | 87.0054 | 66.0354
2018-02-26 06:00 | 86.2898 | 86.6499 | 86.8147 | 65.9165
2018-02-26 07:00 | 86.2043 | 86.5278 | 86.7079 | 65.8296
2018-02-26 08:00 | 86.3355 | 86.5461 | 86.8025 | 65.8725
2018-02-26 09:00 | 86.3798 | 86.7262 | 86.8711 | 65.967
2018-02-26 10:00 | 86.2272 | 86.5156 | 86.714 | 65.8272
2018-02-26 11:00 | 86.2119 | 86.5141 | 86.7201 | 65.829
2018-02-26 12:00 | 86.389 | 86.6835 | 86.8574 | 65.9455
2018-02-26 13:00 | 86.4027 | 86.6224 | 86.7475 | 65.8806
2018-02-26 14:00 | 86.3783 | 86.6606 | 86.7903 | 65.9113
2018-02-26 15:00 | 86.3355 | 86.5248 | 86.7384 | 65.84
2018-02-26 16:00 | 86.3493 | 86.4912 | 86.685 | 65.807
2018-02-26 17:00 | 86.244 | 86.4683 | 86.6743 | 65.7942
2018-02-26 18:00 | 86.3142 | 86.4378 | 86.5934 | 65.7519
2018-02-26 19:00 | 86.2089 | 86.3508 | 86.5583 | 65.7055
2018-02-26 20:00 | 86.2181 | 86.4836 | 86.6896 | 65.8058
2018-02-26 21:00 | 86.1494 | 86.4759 | 86.63 | 65.7802
2018-02-26 22:00 | 86.2593 | 86.5522 | 86.6468 | 65.8156
2018-02-26 23:00 | 86.4424 | 86.8055 | 86.8864 | 66.0029
2018-02-27 | 86.4637 | 0 | 0 | 0
2018-02-27 01:00 | 86.5629 | 0 | 0 | 0
2018-02-27 02:00 | 86.3706 | 0 | 0 | 0
2018-02-27 03:00 | 86.3523 | 0 | 0 | 0
2018-02-27 04:00 | 86.3676 | 0 | 0 | 0
2018-02-27 05:00 | 86.4027 | 0 | 0 | 0
2018-02-27 06:00 | 86.4652 | 0 | 0 | 0
2018-02-27 07:00 | 86.4012 | 0 | 0 | 0
2018-02-27 08:00 | 86.4515 | 0 | 0 | 0
2018-02-27 09:00 | 86.2028 | 0 | 0 | 0
2018-02-27 10:00 | 86.2715 | 0 | 0 | 0
2018-02-27 11:00 | 86.7567 | 0 | 0 | 0
2018-02-27 12:00 | 86.6194 | 0 | 0 | 0
2018-02-27 13:00 | 86.6377 | 0 | 0 | 0
2018-02-27 14:00 | 86.8757 | 0 | 0 | 0
2018-02-27 15:00 | 86.7994 | 0 | 0 | 0
2018-02-27 16:00 | 86.7674 | 0 | 0 | 0
2018-02-27 17:00 | 86.7384 | 0 | 0 | 0
2018-02-27 18:00 | 86.7124 | 0 | 0 | 0
2018-02-27 19:00 | 86.8376 | 0 | 0 | 0
2018-02-27 20:00 | 86.627 | 0 | 0 | 0
2018-02-27 21:00 | 86.6239 | 0 | 0 | 0
2018-02-27 22:00 | 86.714 | 0 | 0 | 0
2018-02-27 23:00 | 86.8971 | 0 | 0 | 0
2018-02-28 | 0 | 0 | 86.6712 | 32.9351
2018-02-28 01:00 | 0 | 0 | 86.511 | 32.8742
2018-02-28 02:00 | 0 | 0 | 86.7628 | 32.9699
2018-02-28 03:00 | 0 | 0 | 86.7384 | 32.9606
2018-02-28 04:00 | 0 | 0 | 86.8376 | 32.9983
2018-02-28 05:00 | 0 | 0 | 87.0222 | 33.0684
2018-02-28 06:00 | 0 | 0 | 86.9627 | 33.0458
2018-02-28 07:00 | 0 | 0 | 87.1321 | 33.1102
2018-02-28 08:00 | 0 | 0 | 87.1931 | 33.1334
2018-02-28 09:00 | 0 | 0 | 86.7155 | 32.9519
2018-02-28 10:00 | 0 | 0 | 86.6743 | 32.9362
2018-02-28 11:00 | 0 | 0 | 86.8956 | 33.0203
2018-02-28 12:00 | 0 | 0 | 86.9276 | 33.0325
2018-02-28 13:00 | 0 | 0 | 87.2541 | 33.1566
2018-02-28 14:00 | 0 | 0 | 87.4037 | 33.2134
2018-02-28 15:00 | 0 | 0 | 87.2129 | 33.1409
2018-02-28 16:00 | 0 | 0 | 86.9718 | 33.0493
2018-02-28 17:00 | 0 | 0 | 87.1397 | 33.1131
2018-02-28 18:00 | 0 | 0 | 87.2435 | 33.1525
2018-02-28 19:00 | 0 | 0 | 86.8894 | 33.018
2018-02-28 20:00 | 0 | 0 | 87.1839 | 33.1299
2018-02-28 21:00 | 0 | 0 | 87.2419 | 33.1519
2018-02-28 22:00 | 0 | 0 | 87.1733 | 33.1259
2018-02-28 23:00 | 0 | 0 | 87.2557 | 33.1572
2018-03-01 | 86.5492 | 0 | 0 | 0
2018-03-01 01:00 | 86.7201 | 0 | 0 | 0
2018-03-01 02:00 | 86.5095 | 0 | 0 | 0
2018-03-01 03:00 | 86.4576 | 0 | 0 | 0
2018-03-01 04:00 | 86.6316 | 0 | 0 | 0
2018-03-01 05:00 | 86.569 | 0 | 0 | 0
2018-03-01 06:00 | 86.6468 | 0 | 0 | 0
2018-03-01 07:00 | 86.6361 | 0 | 0 | 0
2018-03-01 08:00 | 86.6819 | 0 | 0 | 0
2018-03-01 09:00 | 86.7094 | 0 | 0 | 0
2018-03-01 10:00 | 86.7933 | 0 | 0 | 0
2018-03-01 11:00 | 86.8009 | 0 | 0 | 0
2018-03-01 12:00 | 86.6728 | 0 | 0 | 0
2018-03-01 13:00 | 86.6316 | 0 | 0 | 0
2018-03-01 14:00 | 86.6316 | 0 | 0 | 0
2018-03-01 15:00 | 86.6636 | 0 | 0 | 0
2018-03-01 16:00 | 86.5568 | 0 | 0 | 0
2018-03-01 17:00 | 86.6865 | 0 | 0 | 0
2018-03-01 18:00 | 86.7262 | 0 | 0 | 0
2018-03-01 19:00 | 86.5187 | 0 | 0 | 0
2018-03-01 20:00 | 86.5766 | 0 | 0 | 0
2018-03-01 21:00 | 86.6194 | 0 | 0 | 0
2018-03-01 22:00 | 86.6743 | 0 | 0 | 0
2018-03-01 23:00 | 86.5644 | 0 | 0 | 0
2018-03-02 | 86.2226 | 86.688 | 0 | 32.9414
2018-03-02 01:00 | 86.1128 | 86.5232 | 0 | 32.8788
2018-03-02 02:00 | 86.2791 | 86.6896 | 0 | 32.942
2018-03-02 03:00 | 86.0014 | 86.4485 | 0 | 32.8504
2018-03-02 04:00 | 86.0533 | 86.4347 | 0 | 32.8452
2018-03-02 05:00 | 86.2257 | 86.6117 | 0 | 32.9124
2018-03-02 06:00 | 86.4332 | 86.9352 | 0 | 33.0354
2018-03-02 07:00 | 86.5873 | 87.0619 | 0 | 33.0835
2018-03-02 08:00 | 86.3691 | 86.7811 | 0 | 32.9768
2018-03-02 09:00 | 86.334 | 86.7399 | 0 | 32.9612
2018-03-02 10:00 | 86.5126 | 86.862 | 0 | 33.0076
2018-03-02 11:00 | 86.5003 | 86.9306 | 0 | 33.0336
2018-03-02 12:00 | 86.7002 | 87.1412 | 0 | 33.1137
2018-03-02 13:00 | 86.363 | 86.8009 | 0 | 32.9843
2018-03-02 14:00 | 86.4408 | 86.8635 | 0 | 33.0081
2018-03-02 15:00 | 86.2943 | 86.6743 | 0 | 32.9362
2018-03-02 16:00 | 86.3706 | 86.7491 | 0 | 32.9647
2018-03-02 17:00 | 86.2882 | 86.7445 | 0 | 32.9629
2018-03-02 18:00 | 86.1875 | 86.6667 | 0 | 32.9333
2018-03-02 19:00 | 86.099 | 86.5431 | 0 | 32.8864
2018-03-02 20:00 | 86.1997 | 86.5187 | 0 | 32.8771
2018-03-02 21:00 | 86.3767 | 86.7247 | 0 | 32.9554
2018-03-02 22:00 | 86.3691 | 86.7659 | 0 | 32.971
2018-03-02 23:00 | 86.4012 | 86.7918 | 0 | 32.9809
2018-03-03 | 86.0121 | 0 | 86.5507 | 32.8893
2018-03-03 01:00 | 85.919 | 0 | 86.5324 | 32.8823
2018-03-03 02:00 | 86.0533 | 0 | 86.6453 | 32.9252
2018-03-03 03:00 | 86.1677 | 0 | 86.7002 | 32.9461
2018-03-03 04:00 | 86.3081 | 0 | 86.8513 | 33.0035
2018-03-03 05:00 | 86.2562 | 0 | 86.8605 | 33.007
2018-03-03 06:00 | 86.1234 | 0 | 86.6682 | 32.9339
2018-03-03 07:00 | 86.1906 | 0 | 86.7247 | 32.9554
2018-03-03 08:00 | 86.36 | 0 | 86.952 | 33.0418
2018-03-03 09:00 | 86.4912 | 0 | 87.0588 | 33.0823
2018-03-03 10:00 | 86.1982 | 0 | 86.6392 | 32.9229
2018-03-03 11:00 | 86.1707 | 0 | 86.8849 | 33.0163
2018-03-03 12:00 | 86.5019 | 0 | 87.1504 | 33.1172
2018-03-03 13:00 | 86.6148 | 0 | 87.3167 | 33.1803
2018-03-03 14:00 | 86.4439 | 0 | 87.0832 | 33.0916
2018-03-03 15:00 | 86.5522 | 0 | 87.2938 | 33.1716
2018-03-03 16:00 | 86.5644 | 0 | 87.3579 | 33.196
2018-03-03 17:00 | 86.7445 | 0 | 87.57 | 33.2766
2018-03-03 18:00 | 86.4668 | 0 | 87.3014 | 33.1745
2018-03-03 19:00 | 86.3661 | 0 | 87.0954 | 33.0963
2018-03-03 20:00 | 86.1173 | 0 | 86.891 | 33.0186
2018-03-03 21:00 | 86.1555 | 0 | 86.9245 | 33.0313
2018-03-03 22:00 | 86.2211 | 0 | 87.0054 | 33.0621
2018-03-03 23:00 | 86.2226 | 0 | 87.0787 | 33.0899
2018-03-04 | 86.2364 | 86.7994 | 0 | 32.9838
2018-03-04 01:00 | 86.3188 | 86.952 | 0 | 33.0418
2018-03-04 02:00 | 86.2119 | 86.8177 | 0 | 32.9907
2018-03-04 03:00 | 86.1845 | 86.7857 | 0 | 32.9786
2018-03-04 04:00 | 86.2455 | 86.833 | 0 | 32.9965
2018-03-04 05:00 | 86.2333 | 86.833 | 0 | 32.9965
2018-03-04 06:00 | 86.2776 | 86.8528 | 0 | 33.0041
2018-03-04 07:00 | 86.2867 | 86.8452 | 0 | 33.0012
2018-03-04 08:00 | 86.2989 | 86.9032 | 0 | 33.0232
2018-03-04 09:00 | 86.2867 | 86.8162 | 0 | 32.9902
2018-03-04 10:00 | 86.2882 | 86.8528 | 0 | 33.0041
2018-03-04 11:00 | 86.1845 | 86.743 | 0 | 32.9623
2018-03-04 12:00 | 86.1418 | 86.714 | 0 | 32.9513
2018-03-04 13:00 | 86.1479 | 86.7659 | 0 | 32.971
2018-03-04 14:00 | 86.1112 | 86.7018 | 0 | 32.9467
2018-03-04 15:00 | 86.2455 | 86.8482 | 0 | 33.0023
2018-03-04 16:00 | 86.3447 | 86.9398 | 0 | 33.0371
2018-03-04 17:00 | 86.4805 | 86.9856 | 0 | 33.0545
2018-03-04 18:00 | 86.4332 | 86.92 | 0 | 33.0296
2018-03-04 19:00 | 85.6794 | 85.9266 | 0 | 32.6521
2018-03-04 20:00 | 86.3294 | 86.5888 | 0 | 32.9037
2018-03-04 21:00 | 86.3569 | 86.6728 | 0 | 32.9357
2018-03-04 22:00 | 86.4881 | 86.8086 | 0 | 32.9873
2018-03-04 23:00 | 86.4332 | 86.7353 | 0 | 32.9594
2018-03-05 | 86.4088 | 86.7002 | 86.9352 | 65.9815
2018-03-05 01:00 | 86.0426 | 86.3127 | 86.5278 | 65.6794
2018-03-05 02:00 | 86.392 | 86.6392 | 86.8421 | 65.9229
2018-03-05 03:00 | 86.2776 | 86.5766 | 86.7536 | 65.8655
2018-03-05 04:00 | 86.5034 | 86.8849 | 87.0283 | 66.087
2018-03-05 05:00 | 86.3661 | 86.772 | 87.0054 | 66.0354
2018-03-05 06:00 | 86.2898 | 86.6499 | 86.8147 | 65.9165
2018-03-05 07:00 | 86.2043 | 86.5278 | 86.7079 | 65.8296
2018-03-05 08:00 | 86.3355 | 86.5461 | 86.8025 | 65.8725
2018-03-05 09:00 | 86.3798 | 86.7262 | 86.8711 | 65.967
2018-03-05 10:00 | 86.2272 | 86.5156 | 86.714 | 65.8272
2018-03-05 11:00 | 86.2119 | 86.5141 | 86.7201 | 65.829
2018-03-05 12:00 | 86.389 | 86.6835 | 86.8574 | 65.9455
2018-03-05 13:00 | 86.4027 | 86.6224 | 86.7475 | 65.8806
2018-03-05 14:00 | 86.3783 | 86.6606 | 86.7903 | 65.9113
2018-03-05 15:00 | 86.3355 | 86.5248 | 86.7384 | 65.84
2018-03-05 16:00 | 86.3493 | 86.4912 | 86.685 | 65.807
2018-03-05 17:00 | 86.244 | 86.4683 | 86.6743 | 65.7942
2018-03-05 18:00 | 86.3142 | 86.4378 | 86.5934 | 65.7519
2018-03-05 19:00 | 86.2089 | 86.3508 | 86.5583 | 65.7055
2018-03-05 20:00 | 86.2181 | 86.4836 | 86.6896 | 65.8058
2018-03-05 21:00 | 86.1494 | 86.4759 | 86.63 | 65.7802
2018-03-05 22:00 | 86.2593 | 86.5522 | 86.6468 | 65.8156
2018-03-05 23:00 | 86.4424 | 86.8055 | 86.8864 | 66.0029
2018-03-06 | 86.4637 | 0 | 0 | 0
2018-03-06 01:00 | 86.5629 | 0 | 0 | 0
2018-03-06 02:00 | 86.3706 | 0 | 0 | 0
2018-03-06 03:00 | 86.3523 | 0 | 0 | 0
2018-03-06 04:00 | 86.3676 | 0 | 0 | 0
2018-03-06 05:00 | 86.4027 | 0 | 0 | 0
2018-03-06 06:00 | 86.4652 | 0 | 0 | 0
2018-03-06 07:00 | 86.4012 | 0 | 0 | 0
2018-03-06 08:00 | 86.4515 | 0 | 0 | 0
2018-03-06 09:00 | 86.2028 | 0 | 0 | 0
2018-03-06 10:00 | 86.2715 | 0 | 0 | 0
2018-03-06 11:00 | 86.7567 | 0 | 0 | 0
2018-03-06 12:00 | 86.6194 | 0 | 0 | 0
2018-03-06 13:00 | 86.6377 | 0 | 0 | 0
2018-03-06 14:00 | 86.8757 | 0 | 0 | 0
2018-03-06 15:00 | 86.7994 | 0 | 0 | 0
2018-03-06 16:00 | 86.7674 | 0 | 0 | 0
2018-03-06 17:00 | 86.7384 | 0 | 0 | 0
2018-03-06 18:00 | 86.7124 | 0 | 0 | 0
2018-03-06 19:00 | 86.8376 | 0 | 0 | 0
2018-03-06 20:00 | 86.627 | 0 | 0 | 0
2018-03-06 21:00 | 86.6239 | 0 | 0 | 0
2018-03-06 22:00 | 86.714 | 0 | 0 | 0
2018-03-06 23:00 | 86.8971 | 0 | 0 | 0
2018-03-07 | 0 | 0 | 86.6712 | 32.9351
2018-03-07 01:00 | 0 | 0 | 86.511 | 32.8742
2018-03-07 02:00 | 0 | 0 | 86.7628 | 32.9699
2018-03-07 03:00 | 0 | 0 | 86.7384 | 32.9606
2018-03-07 04:00 | 0 | 0 | 86.8376 | 32.9983
2018-03-07 05:00 | 0 | 0 | 87.0222 | 33.0684
2018-03-07 06:00 | 0 | 0 | 86.9627 | 33.0458
2018-03-07 07:00 | 0 | 0 | 87.1321 | 33.1102
2018-03-07 08:00 | 0 | 0 | 87.1931 | 33.1334
2018-03-07 09:00 | 0 | 0 | 86.7155 | 32.9519
2018-03-07 10:00 | 0 | 0 | 86.6743 | 32.9362
2018-03-07 11:00 | 0 | 0 | 86.8956 | 33.0203
2018-03-07 12:00 | 0 | 0 | 86.9276 | 33.0325
2018-03-07 13:00 | 0 | 0 | 87.2541 | 33.1566
2018-03-07 14:00 | 0 | 0 | 87.4037 | 33.2134
2018-03-07 15:00 | 0 | 0 | 87.2129 | 33.1409
2018-03-07 16:00 | 0 | 0 | 86.9718 | 33.0493
2018-03-07 17:00 | 0 | 0 | 87.1397 | 33.1131
2018-03-07 18:00 | 0 | 0 | 87.2435 | 33.1525
2018-03-07 19:00 | 0 | 0 | 86.8894 | 33.018
2018-03-07 20:00 | 0 | 0 | 87.1839 | 33.1299
2018-03-07 21:00 | 0 | 0 | 87.2419 | 33.1519
2018-03-07 22:00 | 0 | 0 | 87.1733 | 33.1259
2018-03-07 23:00 | 0 | 0 | 87.2557 | 33.1572
2018-03-08 | 86.5492 | 0 | 0 | 0
2018-03-08 01:00 | 86.7201 | 0 | 0 | 0
2018-03-08 02:00 | 86.5095 | 0 | 0 | 0
2018-03-08 03:00 | 86.4576 | 0 | 0 | 0
2018-03-08 04:00 | 86.6316 | 0 | 0 | 0
2018-03-08 05:00 | 86.569 | 0 | 0 | 0
2018-03-08 06:00 | 86.6468 | 0 | 0 | 0
2018-03-08 07:00 | 86.6361 | 0 | 0 | 0
2018-03-08 08:00 | 86.6819 | 0 | 0 | 0
2018-03-08 09:00 | 86.7094 | 0 | 0 | 0
2018-03-08 10:00 | 86.7933 | 0 | 0 | 0
2018-03-08 11:00 | 86.8009 | 0 | 0 | 0
2018-03-08 12:00 | 86.6728 | 0 | 0 | 0
2018-03-08 13:00 | 86.6316 | 0 | 0 | 0
2018-03-08 14:00 | 86.6316 | 0 | 0 | 0
2018-03-08 15:00 | 86.6636 | 0 | 0 | 0
2018-03-08 16:00 | 86.5568 | 0 | 0 | 0
2018-03-08 17:00 | 86.6865 | 0 | 0 | 0
2018-03-08 18:00 | 86.7262 | 0 | 0 | 0
2018-03-08 19:00 | 86.5187 | 0 | 0 | 0
2018-03-08 20:00 | 86.5766 | 0 | 0 | 0
2018-03-08 21:00 | 86.6194 | 0 | 0 | 0
2018-03-08 22:00 | 86.6743 | 0 | 0 | 0
2018-03-08 23:00 | 86.5644 | 0 | 0 | 0
2018-03-09 | 86.2226 | 86.688 | 0 | 32.9414
2018-03-09 01:00 | 86.1128 | 86.5232 | 0 | 32.8788
2018-03-09 02:00 | 86.2791 | 86.6896 | 0 | 32.942
2018-03-09 03:00 | 86.0014 | 86.4485 | 0 | 32.8504
2018-03-09 04:00 | 86.0533 | 86.4347 | 0 | 32.8452
2018-03-09 05:00 | 86.2257 | 86.6117 | 0 | 32.9124
2018-03-09 06:00 | 86.4332 | 86.9352 | 0 | 33.0354
2018-03-09 07:00 | 86.5873 | 87.0619 | 0 | 33.0835
2018-03-09 08:00 | 86.3691 | 86.7811 | 0 | 32.9768
2018-03-09 09:00 | 86.334 | 86.7399 | 0 | 32.9612
2018-03-09 10:00 | 86.5126 | 86.862 | 0 | 33.0076
2018-03-09 11:00 | 86.5003 | 86.9306 | 0 | 33.0336
2018-03-09 12:00 | 86.7002 | 87.1412 | 0 | 33.1137
2018-03-09 13:00 | 86.363 | 86.8009 | 0 | 32.9843
2018-03-09 14:00 | 86.4408 | 86.8635 | 0 | 33.0081
2018-03-09 15:00 | 86.2943 | 86.6743 | 0 | 32.9362
2018-03-09 16:00 | 86.3706 | 86.7491 | 0 | 32.9647
2018-03-09 17:00 | 86.2882 | 86.7445 | 0 | 32.9629
2018-03-09 18:00 | 86.1875 | 86.6667 | 0 | 32.9333
2018-03-09 19:00 | 86.099 | 86.5431 | 0 | 32.8864
2018-03-09 20:00 | 86.1997 | 86.5187 | 0 | 32.8771
2018-03-09 21:00 | 86.3767 | 86.7247 | 0 | 32.9554
2018-03-09 22:00 | 86.3691 | 86.7659 | 0 | 32.971
2018-03-09 23:00 | 86.4012 | 86.7918 | 0 | 32.9809
2018-03-10 | 86.0121 | 0 | 86.5507 | 32.8893
2018-03-10 01:00 | 85.919 | 0 | 86.5324 | 32.8823
2018-03-10 02:00 | 86.0533 | 0 | 86.6453 | 32.9252
2018-03-10 03:00 | 86.1677 | 0 | 86.7002 | 32.9461
2018-03-10 04:00 | 86.3081 | 0 | 86.8513 | 33.0035
2018-03-10 05:00 | 86.2562 | 0 | 86.8605 | 33.007
2018-03-10 06:00 | 86.1234 | 0 | 86.6682 | 32.9339
2018-03-10 07:00 | 86.1906 | 0 | 86.7247 | 32.9554
2018-03-10 08:00 | 86.36 | 0 | 86.952 | 33.0418
2018-03-10 09:00 | 86.4912 | 0 | 87.0588 | 33.0823
2018-03-10 10:00 | 86.1982 | 0 | 86.6392 | 32.9229
2018-03-10 11:00 | 86.1707 | 0 | 86.8849 | 33.0163
2018-03-10 12:00 | 86.5019 | 0 | 87.1504 | 33.1172
2018-03-10 13:00 | 86.6148 | 0 | 87.3167 | 33.1803
2018-03-10 14:00 | 86.4439 | 0 | 87.0832 | 33.0916
2018-03-10 15:00 | 86.5522 | 0 | 87.2938 | 33.1716
2018-03-10 16:00 | 86.5644 | 0 | 87.3579 | 33.196
2018-03-10 17:00 | 86.7445 | 0 | 87.57 | 33.2766
2018-03-10 18:00 | 86.4668 | 0 | 87.3014 | 33.1745
2018-03-10 19:00 | 86.3661 | 0 | 87.0954 | 33.0963
2018-03-10 20:00 | 86.1173 | 0 | 86.891 | 33.0186
2018-03-10 21:00 | 86.1555 | 0 | 86.9245 | 33.0313
2018-03-10 22:00 | 86.2211 | 0 | 87.0054 | 33.0621
2018-03-10 23:00 | 86.2226 | 0 | 87.0787 | 33.0899
2018-03-11 | 86.2364 | 86.7994 | 0 | 32.9838
2018-03-11 01:00 | 86.3188 | 86.952 | 0 | 33.0418
2018-03-11 02:00 | 86.2119 | 86.8177 | 0 | 32.9907
2018-03-11 03:00 | 86.1845 | 86.7857 | 0 | 32.9786
2018-03-11 04:00 | 86.2455 | 86.833 | 0 | 32.9965
2018-03-11 05:00 | 86.2333 | 86.833 | 0 | 32.9965
2018-03-11 06:00 | 86.2776 | 86.8528 | 0 | 33.0041
2018-03-11 07:00 | 86.2867 | 86.8452 | 0 | 33.0012
2018-03-11 08:00 | 86.2989 | 86.9032 | 0 | 33.0232
2018-03-11 09:00 | 86.2867 | 86.8162 | 0 | 32.9902
2018-03-11 10:00 | 86.2882 | 86.8528 | 0 | 33.0041
2018-03-11 11:00 | 86.1845 | 86.743 | 0 | 32.9623
2018-03-11 12:00 | 86.1418 | 86.714 | 0 | 32.9513
2018-03-11 13:00 | 86.1479 | 86.7659 | 0 | 32.971
2018-03-11 14:00 | 86.1112 | 86.7018 | 0 | 32.9467
2018-03-11 15:00 | 86.2455 | 86.8482 | 0 | 33.0023
2018-03-11 16:00 | 86.3447 | 86.9398 | 0 | 33.0371
2018-03-11 17:00 | 86.4805 | 86.9856 | 0 | 33.0545
2018-03-11 18:00 | 86.4332 | 86.92 | 0 | 33.0296
2018-03-11 19:00 | 85.6794 | 85.9266 | 0 | 32.6521
2018-03-11 20:00 | 86.3294 | 86.5888 | 0 | 32.9037
2018-03-11 21:00 | 86.3569 | 86.6728 | 0 | 32.9357
2018-03-11 22:00 | 86.4881 | 86.8086 | 0 | 32.9873
2018-03-11 23:00 | 86.4332 | 86.7353 | 0 | 32.9594
2018-03-12 | 86.4088 | 86.7002 | 86.9352 | 65.9815
2018-03-12 01:00 | 86.0426 | 86.3127 | 86.5278 | 65.6794
2018-03-12 02:00 | 86.392 | 86.6392 | 86.8421 | 65.9229
2018-03-12 03:00 | 86.2776 | 86.5766 | 86.7536 | 65.8655
2018-03-12 04:00 | 86.5034 | 86.8849 | 87.0283 | 66.087
2018-03-12 05:00 | 86.3661 | 86.772 | 87.0054 | 66.0354
2018-03-12 06:00 | 86.2898 | 86.6499 | 86.8147 | 65.9165
2018-03-12 07:00 | 86.2043 | 86.5278 | 86.7079 | 65.8296
2018-03-12 08:00 | 86.3355 | 86.5461 | 86.8025 | 65.8725
2018-03-12 09:00 | 86.3798 | 86.7262 | 86.8711 | 65.967
2018-03-12 10:00 | 86.2272 | 86.5156 | 86.714 | 65.8272
2018-03-12 11:00 | 86.2119 | 86.5141 | 86.7201 | 65.829
2018-03-12 12:00 | 86.389 | 86.6835 | 86.8574 | 65.9455
2018-03-12 13:00 | 86.4027 | 86.6224 | 86.7475 | 65.8806
2018-03-12 14:00 | 86.3783 | 86.6606 | 86.7903 | 65.9113
2018-03-12 15:00 | 86.3355 | 86.5248 | 86.7384 | 65.84
2018-03-12 16:00 | 86.3493 | 86.4912 | 86.685 | 65.807
2018-03-12 17:00 | 86.244 | 86.4683 | 86.6743 | 65.7942
2018-03-12 18:00 | 86.3142 | 86.4378 | 86.5934 | 65.7519
2018-03-12 19:00 | 86.2089 | 86.3508 | 86.5583 | 65.7055
2018-03-12 20:00 | 86.2181 | 86.4836 | 86.6896 | 65.8058
2018-03-12 21:00 | 86.1494 | 86.4759 | 86.63 | 65.7802
2018-03-12 22:00 | 86.2593 | 86.5522 | 86.6468 | 65.8156
2018-03-12 23:00 | 86.4424 | 86.8055 | 86.8864 | 66.0029
2018-03-13 | 86.4637 | 0 | 0 | 0
2018-03-13 01:00 | 86.5629 | 0 | 0 | 0
2018-03-13 02:00 | 86.3706 | 0 | 0 | 0
2018-03-13 03:00 | 86.3523 | 0 | 0 | 0
2018-03-13 04:00 | 86.3676 | 0 | 0 | 0
2018-03-13 05:00 | 86.4027 | 0 | 0 | 0
2018-03-13 06:00 | 86.4652 | 0 | 0 | 0
2018-03-13 07:00 | 86.4012 | 0 | 0 | 0
2018-03-13 08:00 | 86.4515 | 0 | 0 | 0
2018-03-13 09:00 | 86.2028 | 0 | 0 | 0
2018-03-13 10:00 | 86.2715 | 0 | 0 | 0
2018-03-13 11:00 | 86.7567 | 0 | 0 | 0
2018-03-13 12:00 | 86.6194 | 0 | 0 | 0
2018-03-13 13:00 | 86.6377 | 0 | 0 | 0
2018-03-13 14:00 | 86.8757 | 0 | 0 | 0
2018-03-13 15:00 | 86.7994 | 0 | 0 | 0
2018-03-13 16:00 | 86.7674 | 0 | 0 | 0
2018-03-13 17:00 | 86.7384 | 0 | 0 | 0
2018-03-13 18:00 | 86.7124 | 0 | 0 | 0
2018-03-13 19:00 | 86.8376 | 0 | 0 | 0
2018-03-13 20:00 | 86.627 | 0 | 0 | 0
2018-03-13 21:00 | 86.6239 | 0 | 0 | 0
2018-03-13 22:00 | 86.714 | 0 | 0 | 0
2018-03-13 23:00 | 86.8971 | 0 | 0 | 0
2018-03-14 | 0 | 0 | 86.6712 | 32.9351
2018-03-14 01:00 | 0 | 0 | 86.511 | 32.8742
2018-03-14 02:00 | 0 | 0 | 86.7628 | 32.9699
2018-03-14 03:00 | 0 | 0 | 86.7384 | 32.9606
2018-03-14 04:00 | 0 | 0 | 86.8376 | 32.9983
2018-03-14 05:00 | 0 | 0 | 87.0222 | 33.0684
2018-03-14 06:00 | 0 | 0 | 86.9627 | 33.0458
2018-03-14 07:00 | 0 | 0 | 87.1321 | 33.1102
2018-03-14 08:00 | 0 | 0 | 87.1931 | 33.1334
2018-03-14 09:00 | 0 | 0 | 86.7155 | 32.9519
2018-03-14 10:00 | 0 | 0 | 86.6743 | 32.9362
2018-03-14 11:00 | 0 | 0 | 86.8956 | 33.0203
2018-03-14 12:00 | 0 | 0 | 86.9276 | 33.0325
2018-03-14 13:00 | 0 | 0 | 87.2541 | 33.1566
2018-03-14 14:00 | 0 | 0 | 87.4037 | 33.2134
2018-03-14 15:00 | 0 | 0 | 87.2129 | 33.1409
2018-03-14 16:00 | 0 | 0 | 86.9718 | 33.0493
2018-03-14 17:00 | 0 | 0 | 87.1397 | 33.1131
2018-03-14 18:00 | 0 | 0 | 87.2435 | 33.1525
2018-03-14 19:00 | 0 | 0 | 86.8894 | 33.018
2018-03-14 20:00 | 0 | 0 | 87.1839 | 33.1299
2018-03-14 21:00 | 0 | 0 | 87.2419 | 33.1519
2018-03-14 22:00 | 0 | 0 | 87.1733 | 33.1259
2018-03-14 23:00 | 0 | 0 | 87.2557 | 33.1572
2018-03-15 | 86.5492 | 0 | 0 | 0
2018-03-15 01:00 | 86.7201 | 0 | 0 | 0
2018-03-15 02:00 | 86.5095 | 0 | 0 | 0
2018-03-15 03:00 | 86.4576 | 0 | 0 | 0
2018-03-15 04:00 | 86.6316 | 0 | 0 | 0
2018-03-15 05:00 | 86.569 | 0 | 0 | 0
2018-03-15 06:00 | 86.6468 | 0 | 0 | 0
2018-03-15 07:00 | 86.6361 | 0 | 0 | 0
2018-03-15 08:00 | 86.6819 | 0 | 0 | 0
2018-03-15 09:00 | 86.7094 | 0 | 0 | 0
2018-03-15 10:00 | 86.7933 | 0 | 0 | 0
2018-03-15 11:00 | 86.8009 | 0 | 0 | 0
2018-03-15 12:00 | 86.6728 | 0 | 0 | 0
2018-03-15 13:00 | 86.6316 | 0 | 0 | 0
2018-03-15 14:00 | 86.6316 | 0 | 0 | 0
2018-03-15 15:00 | 86.6636 | 0 | 0 | 0
2018-03-15 16:00 | 86.5568 | 0 | 0 | 0
2018-03-15 17:00 | 86.6865 | 0 | 0 | 0
2018-03-15 18:00 | 86.7262 | 0 | 0 | 0
2018-03-15 19:00 | 86.5187 | 0 | 0 | 0
2018-03-15 20:00 | 86.5766 | 0 | 0 | 0
2018-03-15 21:00 | 86.6194 | 0 | 0 | 0
2018-03-15 22:00 | 86.6743 | 0 | 0 | 0
2018-03-15 23:00 | 86.5644 | 0 | 0 | 0
2018-03-16 | 86.2226 | 86.688 | 0 | 32.9414
2018-03-16 01:00 | 86.1128 | 86.5232 | 0 | 32.8788
2018-03-16 02:00 | 86.2791 | 86.6896 | 0 | 32.942
2018-03-16 03:00 | 86.0014 | 86.4485 | 0 | 32.8504
2018-03-16 04:00 | 86.0533 | 86.4347 | 0 | 32.8452
2018-03-16 05:00 | 86.2257 | 86.6117 | 0 | 32.9124
2018-03-16 06:00 | 86.4332 | 86.9352 | 0 | 33.0354
2018-03-16 07:00 | 86.5873 | 87.0619 | 0 | 33.0835
2018-03-16 08:00 | 86.3691 | 86.7811 | 0 | 32.9768
2018-03-16 09:00 | 86.334 | 86.7399 | 0 | 32.9612
2018-03-16 10:00 | 86.5126 | 86.862 | 0 | 33.0076
2018-03-16 11:00 | 86.5003 | 86.9306 | 0 | 33.0336
2018-03-16 12:00 | 86.7002 | 87.1412 | 0 | 33.1137
2018-03-16 13:00 | 86.363 | 86.8009 | 0 | 32.9843
2018-03-16 14:00 | 86.4408 | 86.8635 | 0 | 33.0081
2018-03-16 15:00 | 86.2943 | 86.6743 | 0 | 32.9362
2018-03-16 16:00 | 86.3706 | 86.7491 | 0 | 32.9647
2018-03-16 17:00 | 86.2882 | 86.7445 | 0 | 32.9629
2018-03-16 18:00 | 86.1875 | 86.6667 | 0 | 32.9333
2018-03-16 19:00 | 86.099 | 86.5431 | 0 | 32.8864
2018-03-16 20:00 | 86.1997 | 86.5187 | 0 | 32.8771
2018-03-16 21:00 | 86.3767 | 86.7247 | 0 | 32.9554
2018-03-16 22:00 | 86.3691 | 86.7659 | 0 | 32.971
2018-03-16 23:00 | 86.4012 | 86.7918 | 0 | 32.9809
2018-03-17 | 86.0121 | 0 | 86.5507 | 32.8893
2018-03-17 01:00 | 85.919 | 0 | 86.5324 | 32.8823
2018-03-17 02:00 | 86.0533 | 0 | 86.6453 | 32.9252
2018-03-17 03:00 | 86.1677 | 0 | 86.7002 | 32.9461
2018-03-17 04:00 | 86.3081 | 0 | 86.8513 | 33.0035
2018-03-17 05:00 | 86.2562 | 0 | 86.8605 | 33.007
2018-03-17 06:00 | 86.1234 | 0 | 86.6682 | 32.9339
2018-03-17 07:00 | 86.1906 | 0 | 86.7247 | 32.9554
2018-03-17 08:00 | 86.36 | 0 | 86.952 | 33.0418
2018-03-17 09:00 | 86.4912 | 0 | 87.0588 | 33.0823
2018-03-17 10:00 | 86.1982 | 0 | 86.6392 | 32.9229
2018-03-17 11:00 | 86.1707 | 0 | 86.8849 | 33.0163
2018-03-17 12:00 | 86.5019 | 0 | 87.1504 | 33.1172
2018-03-17 13:00 | 86.6148 | 0 | 87.3167 | 33.1803
2018-03-17 14:00 | 86.4439 | 0 | 87.0832 | 33.0916
2018-03-17 15:00 | 86.5522 | 0 | 87.2938 | 33.1716
2018-03-17 16:00 | 86.5644 | 0 | 87.3579 | 33.196
2018-03-17 17:00 | 86.7445 | 0 | 87.57 | 33.2766
2018-03-17 18:00 | 86.4668 | 0 | 87.3014 | 33.1745
2018-03-17 19:00 | 86.3661 | 0 | 87.0954 | 33.0963
2018-03-17 20:00 | 86.1173 | 0 | 86.891 | 33.0186
2018-03-17 21:00 | 86.1555 | 0 | 86.9245 | 33.0313
2018-03-17 22:00 | 86.2211 | 0 | 87.0054 | 33.0621
2018-03-17 23:00 | 86.2226 | 0 | 87.0787 | 33.0899
2018-03-18 | 86.2364 | 86.7994 | 0 | 32.9838
2018-03-18 01:00 | 86.3188 | 86.952 | 0 | 33.0418
2018-03-18 02:00 | 86.2119 | 86.8177 | 0 | 32.9907
2018-03-18 03:00 | 86.1845 | 86.7857 | 0 | 32.9786
2018-03-18 04:00 | 86.2455 | 86.833 | 0 | 32.9965
2018-03-18 05:00 | 86.2333 | 86.833 | 0 | 32.9965
2018-03-18 06:00 | 86.2776 | 86.8528 | 0 | 33.0041
2018-03-18 07:00 | 86.2867 | 86.8452 | 0 | 33.0012
2018-03-18 08:00 | 86.2989 | 86.9032 | 0 | 33.0232
2018-03-18 09:00 | 86.2867 | 86.8162 | 0 | 32.9902
2018-03-18 10:00 | 86.2882 | 86.8528 | 0 | 33.0041
2018-03-18 11:00 | 86.1845 | 86.743 | 0 | 32.9623
2018-03-18 12:00 | 86.1418 | 86.714 | 0 | 32.9513
2018-03-18 13:00 | 86.1479 | 86.7659 | 0 | 32.971
2018-03-18 14:00 | 86.1112 | 86.7018 | 0 | 32.9467
2018-03-18 15:00 | 86.2455 | 86.8482 | 0 | 33.0023
2018-03-18 16:00 | 86.3447 | 86.9398 | 0 | 33.0371
2018-03-18 17:00 | 86.4805 | 86.9856 | 0 | 33.0545
2018-03-18 18:00 | 86.4332 | 86.92 | 0 | 33.0296
2018-03-18 19:00 | 85.6794 | 85.9266 | 0 | 32.6521
2018-03-18 20:00 | 86.3294 | 86.5888 | 0 | 32.9037
2018-03-18 21:00 | 86.3569 | 86.6728 | 0 | 32.9357
2018-03-18 22:00 | 86.4881 | 86.8086 | 0 | 32.9873
2018-03-18 23:00 | 86.4332 | 86.7353 | 0 | 32.9594
2018-03-19 | 86.4088 | 86.7002 | 86.9352 | 65.9815
2018-03-19 01:00 | 86.0426 | 86.3127 | 86.5278 | 65.6794
2018-03-19 02:00 | 86.392 | 86.6392 | 86.8421 | 65.9229
2018-03-19 03:00 | 86.2776 | 86.5766 | 86.7536 | 65.8655
2018-03-19 04:00 | 86.5034 | 86.8849 | 87.0283 | 66.087
2018-03-19 05:00 | 86.3661 | 86.772 | 87.0054 | 66.0354
2018-03-19 06:00 | 86.2898 | 86.6499 | 86.8147 | 65.9165
2018-03-19 07:00 | 86.2043 | 86.5278 | 86.7079 | 65.8296
2018-03-19 08:00 | 86.3355 | 86.5461 | 86.8025 | 65.8725
2018-03-19 09:00 | 86.3798 | 86.7262 | 86.8711 | 65.967
2018-03-19 10:00 | 86.2272 | 86.5156 | 86.714 | 65.8272
2018-03-19 11:00 | 86.2119 | 86.5141 | 86.7201 | 65.829
2018-03-19 12:00 | 86.389 | 86.6835 | 86.8574 | 65.9455
2018-03-19 13:00 | 86.4027 | 86.6224 | 86.7475 | 65.8806
2018-03-19 14:00 | 86.3783 | 86.6606 | 86.7903 | 65.9113
2018-03-19 15:00 | 86.3355 | 86.5248 | 86.7384 | 65.84
2018-03-19 16:00 | 86.3493 | 86.4912 | 86.685 | 65.807
2018-03-19 17:00 | 86.244 | 86.4683 | 86.6743 | 65.7942
2018-03-19 18:00 | 86.3142 | 86.4378 | 86.5934 | 65.7519
2018-03-19 19:00 | 86.2089 | 86.3508 | 86.5583 | 65.7055
2018-03-19 20:00 | 86.2181 | 86.4836 | 86.6896 | 65.8058
2018-03-19 21:00 | 86.1494 | 86.4759 | 86.63 | 65.7802
2018-03-19 22:00 | 86.2593 | 86.5522 | 86.6468 | 65.8156
2018-03-19 23:00 | 86.4424 | 86.8055 | 86.8864 | 66.0029
2018-03-20 | 86.4637 | 0 | 0 | 0
2018-03-20 01:00 | 86.5629 | 0 | 0 | 0
2018-03-20 02:00 | 86.3706 | 0 | 0 | 0
2018-03-20 03:00 | 86.3523 | 0 | 0 | 0
2018-03-20 04:00 | 86.3676 | 0 | 0 | 0
2018-03-20 05:00 | 86.4027 | 0 | 0 | 0
2018-03-20 06:00 | 86.4652 | 0 | 0 | 0
2018-03-20 07:00 | 86.4012 | 0 | 0 | 0
2018-03-20 08:00 | 86.4515 | 0 | 0 | 0
2018-03-20 09:00 | 86.2028 | 0 | 0 | 0
2018-03-20 10:00 | 86.2715 | 0 | 0 | 0
2018-03-20 11:00 | 86.7567 | 0 | 0 | 0
2018-03-20 12:00 | 86.6194 | 0 | 0 | 0
2018-03-20 13:00 | 86.6377 | 0 | 0 | 0
2018-03-20 14:00 | 86.8757 | 0 | 0 | 0
2018-03-20 15:00 | 86.7994 | 0 | 0 | 0
2018-03-20 16:00 | 86.7674 | 0 | 0 | 0
2018-03-20 17:00 | 86.7384 | 0 | 0 | 0
2018-03-20 18:00 | 86.7124 | 0 | 0 | 0
2018-03-20 19:00 | 86.8376 | 0 | 0 | 0
2018-03-20 20:00 | 86.627 | 0 | 0 | 0
2018-03-20 21:00 | 86.6239 | 0 | 0 | 0
2018-03-20 22:00 | 86.714 | 0 | 0 | 0
2018-03-20 23:00 | 86.8971 | 0 | 0 | 0
2018-03-21 | 0 | 0 | 86.6712 | 32.9351
2018-03-21 01:00 | 0 | 0 | 86.511 | 32.8742
2018-03-21 02:00 | 0 | 0 | 86.7628 | 32.9699
2018-03-21 03:00 | 0 | 0 | 86.7384 | 32.9606
2018-03-21 04:00 | 0 | 0 | 86.8376 | 32.9983
2018-03-21 05:00 | 0 | 0 | 87.0222 | 33.0684
2018-03-21 06:00 | 0 | 0 | 86.9627 | 33.0458
2018-03-21 07:00 | 0 | 0 | 87.1321 | 33.1102
2018-03-21 08:00 | 0 | 0 | 87.1931 | 33.1334
2018-03-21 09:00 | 0 | 0 | 86.7155 | 32.9519
2018-03-21 10:00 | 0 | 0 | 86.6743 | 32.9362
2018-03-21 11:00 | 0 | 0 | 86.8956 | 33.0203
2018-03-21 12:00 | 0 | 0 | 86.9276 | 33.0325
2018-03-21 13:00 | 0 | 0 | 87.2541 | 33.1566
2018-03-21 14:00 | 0 | 0 | 87.4037 | 33.2134
2018-03-21 15:00 | 0 | 0 | 87.2129 | 33.1409
2018-03-21 16:00 | 0 | 0 | 86.9718 | 33.0493
2018-03-21 17:00 | 0 | 0 | 87.1397 | 33.1131
2018-03-21 18:00 | 0 | 0 | 87.2435 | 33.1525
2018-03-21 19:00 | 0 | 0 | 86.8894 | 33.018
2018-03-21 20:00 | 0 | 0 | 87.1839 | 33.1299
2018-03-21 21:00 | 0 | 0 | 87.2419 | 33.1519
2018-03-21 22:00 | 0 | 0 | 87.1733 | 33.1259
2018-03-21 23:00 | 0 | 0 | 87.2557 | 33.1572
2018-03-22 | 86.5492 | 0 | 0 | 0
2018-03-22 01:00 | 86.7201 | 0 | 0 | 0
2018-03-22 02:00 | 86.5095 | 0 | 0 | 0
2018-03-22 03:00 | 86.4576 | 0 | 0 | 0
2018-03-22 04:00 | 86.6316 | 0 | 0 | 0
2018-03-22 05:00 | 86.569 | 0 | 0 | 0
2018-03-22 06:00 | 86.6468 | 0 | 0 | 0
2018-03-22 07:00 | 86.6361 | 0 | 0 | 0
2018-03-22 08:00 | 86.6819 | 0 | 0 | 0
2018-03-22 09:00 | 86.7094 | 0 | 0 | 0
2018-03-22 10:00 | 86.7933 | 0 | 0 | 0
2018-03-22 11:00 | 86.8009 | 0 | 0 | 0
2018-03-22 12:00 | 86.6728 | 0 | 0 | 0
2018-03-22 13:00 | 86.6316 | 0 | 0 | 0
2018-03-22 14:00 | 86.6316 | 0 | 0 | 0
2018-03-22 15:00 | 86.6636 | 0 | 0 | 0
2018-03-22 16:00 | 86.5568 | 0 | 0 | 0
2018-03-22 17:00 | 86.6865 | 0 | 0 | 0
2018-03-22 18:00 | 86.7262 | 0 | 0 | 0
2018-03-22 19:00 | 86.5187 | 0 | 0 | 0
2018-03-22 20:00 | 86.5766 | 0 | 0 | 0
2018-03-22 21:00 | 86.6194 | 0 | 0 | 0
2018-03-22 22:00 | 86.6743 | 0 | 0 | 0
2018-03-22 23:00 | 86.5644 | 0 | 0 | 0
2018-03-23 | 86.2226 | 86.688 | 0 | 32.9414
2018-03-23 01:00 | 86.1128 | 86.5232 | 0 | 32.8788
2018-03-23 02:00 | 86.2791 | 86.6896 | 0 | 32.942
2018-03-23 03:00 | 86.0014 | 86.4485 | 0 | 32.8504
2018-03-23 04:00 | 86.0533 | 86.4347 | 0 | 32.8452
2018-03-23 05:00 | 86.2257 | 86.6117 | 0 | 32.9124
2018-03-23 06:00 | 86.4332 | 86.9352 | 0 | 33.0354
2018-03-23 07:00 | 86.5873 | 87.0619 | 0 | 33.0835
2018-03-23 08:00 | 86.3691 | 86.7811 | 0 | 32.9768
2018-03-23 09:00 | 86.334 | 86.7399 | 0 | 32.9612
2018-03-23 10:00 | 86.5126 | 86.862 | 0 | 33.0076
2018-03-23 11:00 | 86.5003 | 86.9306 | 0 | 33.0336
2018-03-23 12:00 | 86.7002 | 87.1412 | 0 | 33.1137
2018-03-23 13:00 | 86.363 | 86.8009 | 0 | 32.9843
2018-03-23 14:00 | 86.4408 | 86.8635 | 0 | 33.0081
2018-03-23 15:00 | 86.2943 | 86.6743 | 0 | 32.9362
2018-03-23 16:00 | 86.3706 | 86.7491 | 0 | 32.9647
2018-03-23 17:00 | 86.2882 | 86.7445 | 0 | 32.9629
2018-03-23 18:00 | 86.1875 | 86.6667 | 0 | 32.9333
2018-03-23 19:00 | 86.099 | 86.5431 | 0 | 32.8864
2018-03-23 20:00 | 86.1997 | 86.5187 | 0 | 32.8771
2018-03-23 21:00 | 86.3767 | 86.7247 | 0 | 32.9554
2018-03-23 22:00 | 86.3691 | 86.7659 | 0 | 32.971
2018-03-23 23:00 | 86.4012 | 86.7918 | 0 | 32.9809
2018-03-24 | 86.0121 | 0 | 86.5507 | 32.8893
2018-03-24 01:00 | 85.919 | 0 | 86.5324 | 32.8823
2018-03-24 02:00 | 86.0533 | 0 | 86.6453 | 32.9252
2018-03-24 03:00 | 86.1677 | 0 | 86.7002 | 32.9461
2018-03-24 04:00 | 86.3081 | 0 | 86.8513 | 33.0035
2018-03-24 05:00 | 86.2562 | 0 | 86.8605 | 33.007
2018-03-24 06:00 | 86.1234 | 0 | 86.6682 | 32.9339
2018-03-24 07:00 | 86.1906 | 0 | 86.7247 | 32.9554
2018-03-24 08:00 | 86.36 | 0 | 86.952 | 33.0418
2018-03-24 09:00 | 86.4912 | 0 | 87.0588 | 33.0823
2018-03-24 10:00 | 86.1982 | 0 | 86.6392 | 32.9229
2018-03-24 11:00 | 86.1707 | 0 | 86.8849 | 33.0163
2018-03-24 12:00 | 86.5019 | 0 | 87.1504 | 33.1172
2018-03-24 13:00 | 86.6148 | 0 | 87.3167 | 33.1803
2018-03-24 14:00 | 86.4439 | 0 | 87.0832 | 33.0916
2018-03-24 15:00 | 86.5522 | 0 | 87.2938 | 33.1716
2018-03-24 16:00 | 86.5644 | 0 | 87.3579 | 33.196
2018-03-24 17:00 | 86.7445 | 0 | 87.57 | 33.2766
2018-03-24 18:00 | 86.4668 | 0 | 87.3014 | 33.1745
2018-03-24 19:00 | 86.3661 | 0 | 87.0954 | 33.0963
2018-03-24 20:00 | 86.1173 | 0 | 86.891 | 33.0186
2018-03-24 21:00 | 86.1555 | 0 | 86.9245 | 33.0313
2018-03-24 22:00 | 86.2211 | 0 | 87.0054 | 33.0621
2018-03-24 23:00 | 86.2226 | 0 | 87.0787 | 33.0899
2018-03-25 | 86.2364 | 86.7994 | 0 | 32.9838
2018-03-25 01:00 | 86.3188 | 86.952 | 0 | 33.0418
2018-03-25 02:00 | 86.2119 | 86.8177 | 0 | 32.9907
2018-03-25 03:00 | 86.1845 | 86.7857 | 0 | 32.9786
2018-03-25 04:00 | 86.2455 | 86.833 | 0 | 32.9965
2018-03-25 05:00 | 86.2333 | 86.833 | 0 | 32.9965
2018-03-25 06:00 | 86.2776 | 86.8528 | 0 | 33.0041
2018-03-25 07:00 | 86.2867 | 86.8452 | 0 | 33.0012
2018-03-25 08:00 | 86.2989 | 86.9032 | 0 | 33.0232
2018-03-25 09:00 | 86.2867 | 86.8162 | 0 | 32.9902
2018-03-25 10:00 | 86.2882 | 86.8528 | 0 | 33.0041
2018-03-25 11:00 | 86.1845 | 86.743 | 0 | 32.9623
2018-03-25 12:00 | 86.1418 | 86.714 | 0 | 32.9513
2018-03-25 13:00 | 86.1479 | 86.7659 | 0 | 32.971
2018-03-25 14:00 | 86.1112 | 86.7018 | 0 | 32.9467
2018-03-25 15:00 | 86.2455 | 86.8482 | 0 | 33.0023
2018-03-25 16:00 | 86.3447 | 86.9398 | 0 | 33.0371
2018-03-25 17:00 | 86.4805 | 86.9856 | 0 | 33.0545
2018-03-25 18:00 | 86.4332 | 86.92 | 0 | 33.0296
2018-03-25 19:00 | 85.6794 | 85.9266 | 0 | 32.6521
2018-03-25 20:00 | 86.3294 | 86.5888 | 0 | 32.9037
2018-03-25 21:00 | 86.3569 | 86.6728 | 0 | 32.9357
2018-03-25 22:00 | 86.4881 | 86.8086 | 0 | 32.9873
2018-03-25 23:00 | 86.4332 | 86.7353 | 0 | 32.9594
2018-03-26 | 86.4088 | 86.7002 | 86.9352 | 65.9815
2018-03-26 01:00 | 86.0426 | 86.3127 | 86.5278 | 65.6794
2018-03-26 02:00 | 86.392 | 86.6392 | 86.8421 | 65.9229
2018-03-26 03:00 | 86.2776 | 86.5766 | 86.7536 | 65.8655
2018-03-26 04:00 | 86.5034 | 86.8849 | 87.0283 | 66.087
2018-03-26 05:00 | 86.3661 | 86.772 | 87.0054 | 66.0354
2018-03-26 06:00 | 86.2898 | 86.6499 | 86.8147 | 65.9165
2018-03-26 07:00 | 86.2043 | 86.5278 | 86.7079 | 65.8296
2018-03-26 08:00 | 86.3355 | 86.5461 | 86.8025 | 65.8725
2018-03-26 09:00 | 86.3798 | 86.7262 | 86.8711 | 65.967
2018-03-26 10:00 | 86.2272 | 86.5156 | 86.714 | 65.8272
2018-03-26 11:00 | 86.2119 | 86.5141 | 86.7201 | 65.829
2018-03-26 12:00 | 86.389 | 86.6835 | 86.8574 | 65.9455
2018-03-26 13:00 | 86.4027 | 86.6224 | 86.7475 | 65.8806
2018-03-26 14:00 | 86.3783 | 86.6606 | 86.7903 | 65.9113
2018-03-26 15:00 | 86.3355 | 86.5248 | 86.7384 | 65.84
2018-03-26 16:00 | 86.3493 | 86.4912 | 86.685 | 65.807
2018-03-26 17:00 | 86.244 | 86.4683 | 86.6743 | 65.7942
2018-03-26 18:00 | 86.3142 | 86.4378 | 86.5934 | 65.7519
2018-03-26 19:00 | 86.2089 | 86.3508 | 86.5583 | 65.7055
2018-03-26 20:00 | 86.2181 | 86.4836 | 86.6896 | 65.8058
2018-03-26 21:00 | 86.1494 | 86.4759 | 86.63 | 65.7802
2018-03-26 22:00 | 86.2593 | 86.5522 | 86.6468 | 65.8156
2018-03-26 23:00 | 86.4424 | 86.8055 | 86.8864 | 66.0029
2018-03-27 | 86.4637 | 0 | 0 | 0
2018-03-27 01:00 | 86.5629 | 0 | 0 | 0
2018-03-27 02:00 | 86.3706 | 0 | 0 | 0
2018-03-27 03:00 | 86.3523 | 0 | 0 | 0
2018-03-27 04:00 | 86.3676 | 0 | 0 | 0
2018-03-27 05:00 | 86.4027 | 0 | 0 | 0
2018-03-27 06:00 | 86.4652 | 0 | 0 | 0
2018-03-27 07:00 | 86.4012 | 0 | 0 | 0
2018-03-27 08:00 | 86.4515 | 0 | 0 | 0
2018-03-27 09:00 | 86.2028 | 0 | 0 | 0
2018-03-27 10:00 | 86.2715 | 0 | 0 | 0
2018-03-27 11:00 | 86.7567 | 0 | 0 | 0
2018-03-27 12:00 | 86.6194 | 0 | 0 | 0
2018-03-27 13:00 | 86.6377 | 0 | 0 | 0
2018-03-27 14:00 | 86.8757 | 0 | 0 | 0
2018-03-27 15:00 | 86.7994 | 0 | 0 | 0
2018-03-27 16:00 | 86.7674 | 0 | 0 | 0
2018-03-27 17:00 | 86.7384 | 0 | 0 | 0
2018-03-27 18:00 | 86.7124 | 0 | 0 | 0
2018-03-27 19:00 | 86.8376 | 0 | 0 | 0
2018-03-27 20:00 | 86.627 | 0 | 0 | 0
2018-03-27 21:00 | 86.6239 | 0 | 0 | 0
2018-03-27 22:00 | 86.714 | 0 | 0 | 0
2018-03-27 23:00 | 86.8971 | 0 | 0 | 0
2018-03-28 | 0 | 0 | 86.6712 | 32.9351
2018-03-28 01:00 | 0 | 0 | 86.511 | 32.8742
2018-03-28 02:00 | 0 | 0 | 86.7628 | 32.9699
2018-03-28 03:00 | 0 | 0 | 86.7384 | 32.9606
2018-03-28 04:00 | 0 | 0 | 86.8376 | 32.9983
2018-03-28 05:00 | 0 | 0 | 87.0222 | 33.0684
2018-03-28 06:00 | 0 | 0 | 86.9627 | 33.0458
2018-03-28 07:00 | 0 | 0 | 87.1321 | 33.1102
2018-03-28 08:00 | 0 | 0 | 87.1931 | 33.1334
2018-03-28 09:00 | 0 | 0 | 86.7155 | 32.9519
2018-03-28 10:00 | 0 | 0 | 86.6743 | 32.9362
2018-03-28 11:00 | 0 | 0 | 86.8956 | 33.0203
2018-03-28 12:00 | 0 | 0 | 86.9276 | 33.0325
2018-03-28 13:00 | 0 | 0 | 87.2541 | 33.1566
2018-03-28 14:00 | 0 | 0 | 87.4037 | 33.2134
2018-03-28 15:00 | 0 | 0 | 87.2129 | 33.1409
2018-03-28 16:00 | 0 | 0 | 86.9718 | 33.0493
2018-03-28 17:00 | 0 | 0 | 87.1397 | 33.1131
2018-03-28 18:00 | 0 | 0 | 87.2435 | 33.1525
2018-03-28 19:00 | 0 | 0 | 86.8894 | 33.018
2018-03-28 20:00 | 0 | 0 | 87.1839 | 33.1299
2018-03-28 21:00 | 0 | 0 | 87.2419 | 33.1519
2018-03-28 22:00 | 0 | 0 | 87.1733 | 33.1259
2018-03-28 23:00 | 0 | 0 | 87.2557 | 33.1572
2018-03-29 | 86.5492 | 0 | 0 | 0
2018-03-29 01:00 | 86.7201 | 0 | 0 | 0
2018-03-29 02:00 | 86.5095 | 0 | 0 | 0
2018-03-29 03:00 | 86.4576 | 0 | 0 | 0
2018-03-29 04:00 | 86.6316 | 0 | 0 | 0
2018-03-29 05:00 | 86.569 | 0 | 0 | 0
2018-03-29 06:00 | 86.6468 | 0 | 0 | 0
2018-03-29 07:00 | 86.6361 | 0 | 0 | 0
2018-03-29 08:00 | 86.6819 | 0 | 0 | 0
2018-03-29 09:00 | 86.7094 | 0 | 0 | 0
2018-03-29 10:00 | 86.7933 | 0 | 0 | 0
2018-03-29 11:00 | 86.8009 | 0 | 0 | 0
2018-03-29 12:00 | 86.6728 | 0 | 0 | 0
2018-03-29 13:00 | 86.6316 | 0 | 0 | 0
2018-03-29 14:00 | 86.6316 | 0 | 0 | 0
2018-03-29 15:00 | 86.6636 | 0 | 0 | 0
2018-03-29 16:00 | 86.5568 | 0 | 0 | 0
2018-03-29 17:00 | 86.6865 | 0 | 0 | 0
2018-03-29 18:00 | 86.7262 | 0 | 0 | 0
2018-03-29 19:00 | 86.5187 | 0 | 0 | 0
2018-03-29 20:00 | 86.5766 | 0 | 0 | 0
2018-03-29 21:00 | 86.6194 | 0 | 0 | 0
2018-03-29 22:00 | 86.6743 | 0 | 0 | 0
2018-03-29 23:00 | 86.5644 | 0 | 0 | 0
2018-03-30 | 86.2226 | 86.688 | 0 | 32.9414
2018-03-30 01:00 | 86.1128 | 86.5232 | 0 | 32.8788
2018-03-30 02:00 | 86.2791 | 86.6896 | 0 | 32.942
2018-03-30 03:00 | 86.0014 | 86.4485 | 0 | 32.8504
2018-03-30 04:00 | 86.0533 | 86.4347 | 0 | 32.8452
2018-03-30 05:00 | 86.2257 | 86.6117 | 0 | 32.9124
2018-03-30 06:00 | 86.4332 | 86.9352 | 0 | 33.0354
2018-03-30 07:00 | 86.5873 | 87.0619 | 0 | 33.0835
2018-03-30 08:00 | 86.3691 | 86.7811 | 0 | 32.9768
2018-03-30 09:00 | 86.334 | 86.7399 | 0 | 32.9612
2018-03-30 10:00 | 86.5126 | 86.862 | 0 | 33.0076
2018-03-30 11:00 | 86.5003 | 86.9306 | 0 | 33.0336
2018-03-30 12:00 | 86.7002 | 87.1412 | 0 | 33.1137
2018-03-30 13:00 | 86.363 | 86.8009 | 0 | 32.9843
2018-03-30 14:00 | 86.4408 | 86.8635 | 0 | 33.0081
2018-03-30 15:00 | 86.2943 | 86.6743 | 0 | 32.9362
2018-03-30 16:00 | 86.3706 | 86.7491 | 0 | 32.9647
2018-03-30 17:00 | 86.2882 | 86.7445 | 0 | 32.9629
2018-03-30 18:00 | 86.1875 | 86.6667 | 0 | 32.9333
2018-03-30 19:00 | 86.099 | 86.5431 | 0 | 32.8864
2018-03-30 20:00 | 86.1997 | 86.5187 | 0 | 32.8771
2018-03-30 21:00 | 86.3767 | 86.7247 | 0 | 32.9554
2018-03-30 22:00 | 86.3691 | 86.7659 | 0 | 32.971
2018-03-30 23:00 | 86.4012 | 86.7918 | 0 | 32.9809
2018-03-31 | 86.0121 | 0 | 86.5507 | 32.8893
2018-03-31 01:00 | 85.919 | 0 | 86.5324 | 32.8823
2018-03-31 02:00 | 86.0533 | 0 | 86.6453 | 32.9252
2018-03-31 03:00 | 86.1677 | 0 | 86.7002 | 32.9461
2018-03-31 04:00 | 86.3081 | 0 | 86.8513 | 33.0035
2018-03-31 05:00 | 86.2562 | 0 | 86.8605 | 33.007
2018-03-31 06:00 | 86.1234 | 0 | 86.6682 | 32.9339
2018-03-31 07:00 | 86.1906 | 0 | 86.7247 | 32.9554
2018-03-31 08:00 | 86.36 | 0 | 86.952 | 33.0418
2018-03-31 09:00 | 86.4912 | 0 | 87.0588 | 33.0823
2018-03-31 10:00 | 86.1982 | 0 | 86.6392 | 32.9229
2018-03-31 11:00 | 86.1707 | 0 | 86.8849 | 33.0163
2018-03-31 12:00 | 86.5019 | 0 | 87.1504 | 33.1172
2018-03-31 13:00 | 86.6148 | 0 | 87.3167 | 33.1803
2018-03-31 14:00 | 86.4439 | 0 | 87.0832 | 33.0916
2018-03-31 15:00 | 86.5522 | 0 | 87.2938 | 33.1716
2018-03-31 16:00 | 86.5644 | 0 | 87.3579 | 33.196
2018-03-31 17:00 | 86.7445 | 0 | 87.57 | 33.2766
2018-03-31 18:00 | 86.4668 | 0 | 87.3014 | 33.1745
2018-03-31 19:00 | 86.3661 | 0 | 87.0954 | 33.0963
2018-03-31 20:00 | 86.1173 | 0 | 86.891 | 33.0186
2018-03-31 21:00 | 86.1555 | 0 | 86.9245 | 33.0313
2018-03-31 22:00 | 86.2211 | 0 | 87.0054 | 33.0621
2018-03-31 23:00 | 86.2226 | 0 | 87.0787 | 33.0899
2018-04-01 | 86.2364 | 86.7994 | 0 | 32.9838
2018-04-01 01:00 | 86.3188 | 86.952 | 0 | 33.0418
2018-04-01 02:00 | 86.2119 | 86.8177 | 0 | 32.9907
2018-04-01 03:00 | 86.1845 | 86.7857 | 0 | 32.9786
2018-04-01 04:00 | 86.2455 | 86.833 | 0 | 32.9965
2018-04-01 05:00 | 86.2333 | 86.833 | 0 | 32.9965
2018-04-01 06:00 | 86.2776 | 86.8528 | 0 | 33.0041
2018-04-01 07:00 | 86.2867 | 86.8452 | 0 | 33.0012
2018-04-01 08:00 | 86.2989 | 86.9032 | 0 | 33.0232
2018-04-01 09:00 | 86.2867 | 86.8162 | 0 | 32.9902
2018-04-01 10:00 | 86.2882 | 86.8528 | 0 | 33.0041
2018-04-01 11:00 | 86.1845 | 86.743 | 0 | 32.9623
2018-04-01 12:00 | 86.1418 | 86.714 | 0 | 32.9513
2018-04-01 13:00 | 86.1479 | 86.7659 | 0 | 32.971
2018-04-01 14:00 | 86.1112 | 86.7018 | 0 | 32.9467
2018-04-01 15:00 | 86.2455 | 86.8482 | 0 | 33.0023
2018-04-01 16:00 | 86.3447 | 86.9398 | 0 | 33.0371
2018-04-01 17:00 | 86.4805 | 86.9856 | 0 | 33.0545
2018-04-01 18:00 | 86.4332 | 86.92 | 0 | 33.0296
2018-04-01 19:00 | 85.6794 | 85.9266 | 0 | 32.6521
2018-04-01 20:00 | 86.3294 | 86.5888 | 0 | 32.9037
2018-04-01 21:00 | 86.3569 | 86.6728 | 0 | 32.9357
2018-04-01 22:00 | 86.4881 | 86.8086 | 0 | 32.9873
2018-04-01 23:00 | 86.4332 | 86.7353 | 0 | 32.9594
2018-04-02 | 86.4088 | 86.7002 | 86.9352 | 65.9815
2018-04-02 01:00 | 86.0426 | 86.3127 | 86.5278 | 65.6794
2018-04-02 02:00 | 86.392 | 86.6392 | 86.8421 | 65.9229
2018-04-02 03:00 | 86.2776 | 86.5766 | 86.7536 | 65.8655
2018-04-02 04:00 | 86.5034 | 86.8849 | 87.0283 | 66.087
2018-04-02 05:00 | 86.3661 | 86.772 | 87.0054 | 66.0354
2018-04-02 06:00 | 86.2898 | 86.6499 | 86.8147 | 65.9165
2018-04-02 07:00 | 86.2043 | 86.5278 | 86.7079 | 65.8296
2018-04-02 08:00 | 86.3355 | 86.5461 | 86.8025 | 65.8725
2018-04-02 09:00 | 86.3798 | 86.7262 | 86.8711 | 65.967
2018-04-02 10:00 | 86.2272 | 86.5156 | 86.714 | 65.8272
2018-04-02 11:00 | 86.2119 | 86.5141 | 86.7201 | 65.829
2018-04-02 12:00 | 86.389 | 86.6835 | 86.8574 | 65.9455
2018-04-02 13:00 | 86.4027 | 86.6224 | 86.7475 | 65.8806
2018-04-02 14:00 | 86.3783 | 86.6606 | 86.7903 | 65.9113
2018-04-02 15:00 | 86.3355 | 86.5248 | 86.7384 | 65.84
2018-04-02 16:00 | 86.3493 | 86.4912 | 86.685 | 65.807
2018-04-02 17:00 | 86.244 | 86.4683 | 86.6743 | 65.7942
2018-04-02 18:00 | 86.3142 | 86.4378 | 86.5934 | 65.7519
2018-04-02 19:00 | 86.2089 | 86.3508 | 86.5583 | 65.7055
2018-04-02 20:00 | 86.2181 | 86.4836 | 86.6896 | 65.8058
2018-04-02 21:00 | 86.1494 | 86.4759 | 86.63 | 65.7802
2018-04-02 22:00 | 86.2593 | 86.5522 | 86.6468 | 65.8156
2018-04-02 23:00 | 86.4424 | 86.8055 | 86.8864 | 66.0029
2018-04-03 | 86.4637 | 0 | 0 | 0
2018-04-03 01:00 | 86.5629 | 0 | 0 | 0
2018-04-03 02:00 | 86.3706 | 0 | 0 | 0
2018-04-03 03:00 | 86.3523 | 0 | 0 | 0
2018-04-03 04:00 | 86.3676 | 0 | 0 | 0
2018-04-03 05:00 | 86.4027 | 0 | 0 | 0
2018-04-03 06:00 | 86.4652 | 0 | 0 | 0
2018-04-03 07:00 | 86.4012 | 0 | 0 | 0
2018-04-03 08:00 | 86.4515 | 0 | 0 | 0
2018-04-03 09:00 | 86.2028 | 0 | 0 | 0
2018-04-03 10:00 | 86.2715 | 0 | 0 | 0
2018-04-03 11:00 | 86.7567 | 0 | 0 | 0
2018-04-03 12:00 | 86.6194 | 0 | 0 | 0
2018-04-03 13:00 | 86.6377 | 0 | 0 | 0
2018-04-03 14:00 | 86.8757 | 0 | 0 | 0
2018-04-03 15:00 | 86.7994 | 0 | 0 | 0
2018-04-03 16:00 | 86.7674 | 0 | 0 | 0
2018-04-03 17:00 | 86.7384 | 0 | 0 | 0
2018-04-03 18:00 | 86.7124 | 0 | 0 | 0
2018-04-03 19:00 | 86.8376 | 0 | 0 | 0
2018-04-03 20:00 | 86.627 | 0 | 0 | 0
2018-04-03 21:00 | 86.6239 | 0 | 0 | 0
2018-04-03 22:00 | 86.714 | 0 | 0 | 0
2018-04-03 23:00 | 86.8971 | 0 | 0 | 0
2018-04-04 | 0 | 0 | 86.6712 | 32.9351
2018-04-04 01:00 | 0 | 0 | 86.511 | 32.8742
2018-04-04 02:00 | 0 | 0 | 86.7628 | 32.9699
2018-04-04 03:00 | 0 | 0 | 86.7384 | 32.9606
2018-04-04 04:00 | 0 | 0 | 86.8376 | 32.9983
2018-04-04 05:00 | 0 | 0 | 87.0222 | 33.0684
2018-04-04 06:00 | 0 | 0 | 86.9627 | 33.0458
2018-04-04 07:00 | 0 | 0 | 87.1321 | 33.1102
2018-04-04 08:00 | 0 | 0 | 87.1931 | 33.1334
2018-04-04 09:00 | 0 | 0 | 86.7155 | 32.9519
2018-04-04 10:00 | 0 | 0 | 86.6743 | 32.9362
2018-04-04 11:00 | 0 | 0 | 86.8956 | 33.0203
2018-04-04 12:00 | 0 | 0 | 86.9276 | 33.0325
2018-04-04 13:00 | 0 | 0 | 87.2541 | 33.1566
2018-04-04 14:00 | 0 | 0 | 87.4037 | 33.2134
2018-04-04 15:00 | 0 | 0 | 87.2129 | 33.1409
2018-04-04 16:00 | 0 | 0 | 86.9718 | 33.0493
2018-04-04 17:00 | 0 | 0 | 87.1397 | 33.1131
2018-04-04 18:00 | 0 | 0 | 87.2435 | 33.1525
2018-04-04 19:00 | 0 | 0 | 86.8894 | 33.018
2018-04-04 20:00 | 0 | 0 | 87.1839 | 33.1299
2018-04-04 21:00 | 0 | 0 | 87.2419 | 33.1519
2018-04-04 22:00 | 0 | 0 | 87.1733 | 33.1259
2018-04-04 23:00 | 0 | 0 | 87.2557 | 33.1572
2018-04-05 | 86.5492 | 0 | 0 | 0
2018-04-05 01:00 | 86.7201 | 0 | 0 | 0
2018-04-05 02:00 | 86.5095 | 0 | 0 | 0
2018-04-05 03:00 | 86.4576 | 0 | 0 | 0
2018-04-05 04:00 | 86.6316 | 0 | 0 | 0
2018-04-05 05:00 | 86.569 | 0 | 0 | 0
2018-04-05 06:00 | 86.6468 | 0 | 0 | 0
2018-04-05 07:00 | 86.6361 | 0 | 0 | 0
2018-04-05 08:00 | 86.6819 | 0 | 0 | 0
2018-04-05 09:00 | 86.7094 | 0 | 0 | 0
2018-04-05 10:00 | 86.7933 | 0 | 0 | 0
2018-04-05 11:00 | 86.8009 | 0 | 0 | 0
2018-04-05 12:00 | 86.6728 | 0 | 0 | 0
2018-04-05 13:00 | 86.6316 | 0 | 0 | 0
2018-04-05 14:00 | 86.6316 | 0 | 0 | 0
2018-04-05 15:00 | 86.6636 | 0 | 0 | 0
2018-04-05 16:00 | 86.5568 | 0 | 0 | 0
2018-04-05 17:00 | 86.6865 | 0 | 0 | 0
2018-04-05 18:00 | 86.7262 | 0 | 0 | 0
2018-04-05 19:00 | 86.5187 | 0 | 0 | 0
2018-04-05 20:00 | 86.5766 | 0 | 0 | 0
2018-04-05 21:00 | 86.6194 | 0 | 0 | 0
2018-04-05 22:00 | 86.6743 | 0 | 0 | 0
2018-04-05 23:00 | 86.5644 | 0 | 0 | 0
2018-04-06 | 86.2226 | 86.688 | 0 | 32.9414
2018-04-06 01:00 | 86.1128 | 86.5232 | 0 | 32.8788
2018-04-06 02:00 | 86.2791 | 86.6896 | 0 | 32.942
2018-04-06 03:00 | 86.0014 | 86.4485 | 0 | 32.8504
2018-04-06 04:00 | 86.0533 | 86.4347 | 0 | 32.8452
2018-04-06 05:00 | 86.2257 | 86.6117 | 0 | 32.9124
2018-04-06 06:00 | 86.4332 | 86.9352 | 0 | 33.0354
2018-04-06 07:00 | 86.5873 | 87.0619 | 0 | 33.0835
2018-04-06 08:00 | 86.3691 | 86.7811 | 0 | 32.9768
2018-04-06 09:00 | 86.334 | 86.7399 | 0 | 32.9612
2018-04-06 10:00 | 86.5126 | 86.862 | 0 | 33.0076
2018-04-06 11:00 | 86.5003 | 86.9306 | 0 | 33.0336
2018-04-06 12:00 | 86.7002 | 87.1412 | 0 | 33.1137
2018-04-06 13:00 | 86.363 | 86.8009 | 0 | 32.9843
2018-04-06 14:00 | 86.4408 | 86.8635 | 0 | 33.0081
2018-04-06 15:00 | 86.2943 | 86.6743 | 0 | 32.9362
2018-04-06 16:00 | 86.3706 | 86.7491 | 0 | 32.9647
2018-04-06 17:00 | 86.2882 | 86.7445 | 0 | 32.9629
2018-04-06 18:00 | 86.1875 | 86.6667 | 0 | 32.9333
2018-04-06 19:00 | 86.099 | 86.5431 | 0 | 32.8864
2018-04-06 20:00 | 86.1997 | 86.5187 | 0 | 32.8771
2018-04-06 21:00 | 86.3767 | 86.7247 | 0 | 32.9554
2018-04-06 22:00 | 86.3691 | 86.7659 | 0 | 32.971
2018-04-06 23:00 | 86.4012 | 86.7918 | 0 | 32.9809
2018-04-07 | 86.0121 | 0 | 86.5507 | 32.8893
2018-04-07 01:00 | 85.919 | 0 | 86.5324 | 32.8823
2018-04-07 02:00 | 86.0533 | 0 | 86.6453 | 32.9252
2018-04-07 03:00 | 86.1677 | 0 | 86.7002 | 32.9461
2018-04-07 04:00 | 86.3081 | 0 | 86.8513 | 33.0035
2018-04-07 05:00 | 86.2562 | 0 | 86.8605 | 33.007
2018-04-07 06:00 | 86.1234 | 0 | 86.6682 | 32.9339
2018-04-07 07:00 | 86.1906 | 0 | 86.7247 | 32.9554
2018-04-07 08:00 | 86.36 | 0 | 86.952 | 33.0418
2018-04-07 09:00 | 86.4912 | 0 | 87.0588 | 33.0823
2018-04-07 10:00 | 86.1982 | 0 | 86.6392 | 32.9229
2018-04-07 11:00 | 86.1707 | 0 | 86.8849 | 33.0163
2018-04-07 12:00 | 86.5019 | 0 | 87.1504 | 33.1172
2018-04-07 13:00 | 86.6148 | 0 | 87.3167 | 33.1803
2018-04-07 14:00 | 86.4439 | 0 | 87.0832 | 33.0916
2018-04-07 15:00 | 86.5522 | 0 | 87.2938 | 33.1716
2018-04-07 16:00 | 86.5644 | 0 | 87.3579 | 33.196
2018-04-07 17:00 | 86.7445 | 0 | 87.57 | 33.2766
2018-04-07 18:00 | 86.4668 | 0 | 87.3014 | 33.1745
2018-04-07 19:00 | 86.3661 | 0 | 87.0954 | 33.0963
2018-04-07 20:00 | 86.1173 | 0 | 86.891 | 33.0186
2018-04-07 21:00 | 86.1555 | 0 | 86.9245 | 33.0313
2018-04-07 22:00 | 86.2211 | 0 | 87.0054 | 33.0621
2018-04-07 23:00 | 86.2226 | 0 | 87.0787 | 33.0899
2018-04-08 | 86.2364 | 86.7994 | 0 | 32.9838
2018-04-08 01:00 | 86.3188 | 86.952 | 0 | 33.0418
2018-04-08 02:00 | 86.2119 | 86.8177 | 0 | 32.9907
2018-04-08 03:00 | 86.1845 | 86.7857 | 0 | 32.9786
2018-04-08 04:00 | 86.2455 | 86.833 | 0 | 32.9965
2018-04-08 05:00 | 86.2333 | 86.833 | 0 | 32.9965
2018-04-08 06:00 | 86.2776 | 86.8528 | 0 | 33.0041
2018-04-08 07:00 | 86.2867 | 86.8452 | 0 | 33.0012
2018-04-08 08:00 | 86.2989 | 86.9032 | 0 | 33.0232
2018-04-08 09:00 | 86.2867 | 86.8162 | 0 | 32.9902
2018-04-08 10:00 | 86.2882 | 86.8528 | 0 | 33.0041
2018-04-08 11:00 | 86.1845 | 86.743 | 0 | 32.9623
2018-04-08 12:00 | 86.1418 | 86.714 | 0 | 32.9513
2018-04-08 13:00 | 86.1479 | 86.7659 | 0 | 32.971
2018-04-08 14:00 | 86.1112 | 86.7018 | 0 | 32.9467
2018-04-08 15:00 | 86.2455 | 86.8482 | 0 | 33.0023
2018-04-08 16:00 | 86.3447 | 86.9398 | 0 | 33.0371
2018-04-08 17:00 | 86.4805 | 86.9856 | 0 | 33.0545
2018-04-08 18:00 | 86.4332 | 86.92 | 0 | 33.0296
2018-04-08 19:00 | 85.6794 | 85.9266 | 0 | 32.6521
2018-04-08 20:00 | 86.3294 | 86.5888 | 0 | 32.9037
2018-04-08 21:00 | 86.3569 | 86.6728 | 0 | 32.9357
2018-04-08 22:00 | 86.4881 | 86.8086 | 0 | 32.9873
2018-04-08 23:00 | 86.4332 | 86.7353 | 0 | 32.9594
2018-04-09 | 86.4088 | 86.7002 | 86.9352 | 65.9815
2018-04-09 01:00 | 86.0426 | 86.3127 | 86.5278 | 65.6794
2018-04-09 02:00 | 86.392 | 86.6392 | 86.8421 | 65.9229
2018-04-09 03:00 | 86.2776 | 86.5766 | 86.7536 | 65.8655
2018-04-09 04:00 | 86.5034 | 86.8849 | 87.0283 | 66.087
2018-04-09 05:00 | 86.3661 | 86.772 | 87.0054 | 66.0354
2018-04-09 06:00 | 86.2898 | 86.6499 | 86.8147 | 65.9165
2018-04-09 07:00 | 86.2043 | 86.5278 | 86.7079 | 65.8296
2018-04-09 08:00 | 86.3355 | 86.5461 | 86.8025 | 65.8725
2018-04-09 09:00 | 86.3798 | 86.7262 | 86.8711 | 65.967
2018-04-09 10:00 | 86.2272 | 86.5156 | 86.714 | 65.8272
2018-04-09 11:00 | 86.2119 | 86.5141 | 86.7201 | 65.829
2018-04-09 12:00 | 86.389 | 86.6835 | 86.8574 | 65.9455
2018-04-09 13:00 | 86.4027 | 86.6224 | 86.7475 | 65.8806
2018-04-09 14:00 | 86.3783 | 86.6606 | 86.7903 | 65.9113
2018-04-09 15:00 | 86.3355 | 86.5248 | 86.7384 | 65.84
2018-04-09 16:00 | 86.3493 | 86.4912 | 86.685 | 65.807
2018-04-09 17:00 | 86.244 | 86.4683 | 86.6743 | 65.7942
2018-04-09 18:00 | 86.3142 | 86.4378 | 86.5934 | 65.7519
2018-04-09 19:00 | 86.2089 | 86.3508 | 86.5583 | 65.7055
2018-04-09 20:00 | 86.2181 | 86.4836 | 86.6896 | 65.8058
2018-04-09 21:00 | 86.1494 | 86.4759 | 86.63 | 65.7802
2018-04-09 22:00 | 86.2593 | 86.5522 | 86.6468 | 65.8156
2018-04-09 23:00 | 86.4424 | 86.8055 | 86.8864 | 66.0029
2018-04-10 | 86.4637 | 0 | 0 | 0
2018-04-10 01:00 | 86.5629 | 0 | 0 | 0
2018-04-10 02:00 | 86.3706 | 0 | 0 | 0
2018-04-10 03:00 | 86.3523 | 0 | 0 | 0
2018-04-10 04:00 | 86.3676 | 0 | 0 | 0
2018-04-10 05:00 | 86.4027 | 0 | 0 | 0
2018-04-10 06:00 | 86.4652 | 0 | 0 | 0
2018-04-10 07:00 | 86.4012 | 0 | 0 | 0
2018-04-10 08:00 | 86.4515 | 0 | 0 | 0
2018-04-10 09:00 | 86.2028 | 0 | 0 | 0
2018-04-10 10:00 | 86.2715 | 0 | 0 | 0
2018-04-10 11:00 | 86.7567 | 0 | 0 | 0
2018-04-10 12:00 | 86.6194 | 0 | 0 | 0
2018-04-10 13:00 | 86.6377 | 0 | 0 | 0
2018-04-10 14:00 | 86.8757 | 0 | 0 | 0
2018-04-10 15:00 | 86.7994 | 0 | 0 | 0
2018-04-10 16:00 | 86.7674 | 0 | 0 | 0
2018-04-10 17:00 | 86.7384 | 0 | 0 | 0
2018-04-10 18:00 | 86.7124 | 0 | 0 | 0
2018-04-10 19:00 | 86.8376 | 0 | 0 | 0
2018-04-10 20:00 | 86.627 | 0 | 0 | 0
2018-04-10 21:00 | 86.6239 | 0 | 0 | 0
2018-04-10 22:00 | 86.714 | 0 | 0 | 0
2018-04-10 23:00 | 86.8971 | 0 | 0 | 0
2018-04-11 | 0 | 0 | 86.6712 | 32.9351
2018-04-11 01:00 | 0 | 0 | 86.511 | 32.8742
2018-04-11 02:00 | 0 | 0 | 86.7628 | 32.9699
2018-04-11 03:00 | 0 | 0 | 86.7384 | 32.9606
2018-04-11 04:00 | 0 | 0 | 86.8376 | 32.9983
2018-04-11 05:00 | 0 | 0 | 87.0222 | 33.0684
2018-04-11 06:00 | 0 | 0 | 86.9627 | 33.0458
2018-04-11 07:00 | 0 | 0 | 87.1321 | 33.1102
2018-04-11 08:00 | 0 | 0 | 87.1931 | 33.1334
2018-04-11 09:00 | 0 | 0 | 86.7155 | 32.9519
2018-04-11 10:00 | 0 | 0 | 86.6743 | 32.9362
2018-04-11 11:00 | 0 | 0 | 86.8956 | 33.0203
2018-04-11 12:00 | 0 | 0 | 86.9276 | 33.0325
2018-04-11 13:00 | 0 | 0 | 87.2541 | 33.1566
2018-04-11 14:00 | 0 | 0 | 87.4037 | 33.2134
2018-04-11 15:00 | 0 | 0 | 87.2129 | 33.1409
2018-04-11 16:00 | 0 | 0 | 86.9718 | 33.0493
2018-04-11 17:00 | 0 | 0 | 87.1397 | 33.1131
2018-04-11 18:00 | 0 | 0 | 87.2435 | 33.1525
2018-04-11 19:00 | 0 | 0 | 86.8894 | 33.018
2018-04-11 20:00 | 0 | 0 | 87.1839 | 33.1299
2018-04-11 21:00 | 0 | 0 | 87.2419 | 33.1519
2018-04-11 22:00 | 0 | 0 | 87.1733 | 33.1259
2018-04-11 23:00 | 0 | 0 | 87.2557 | 33.1572
2018-04-12 | 86.5492 | 0 | 0 | 0
2018-04-12 01:00 | 86.7201 | 0 | 0 | 0
2018-04-12 02:00 | 86.5095 | 0 | 0 | 0
2018-04-12 03:00 | 86.4576 | 0 | 0 | 0
2018-04-12 04:00 | 86.6316 | 0 | 0 | 0
2018-04-12 05:00 | 86.569 | 0 | 0 | 0
2018-04-12 06:00 | 86.6468 | 0 | 0 | 0
2018-04-12 07:00 | 86.6361 | 0 | 0 | 0
2018-04-12 08:00 | 86.6819 | 0 | 0 | 0
2018-04-12 09:00 | 86.7094 | 0 | 0 | 0
2018-04-12 10:00 | 86.7933 | 0 | 0 | 0
2018-04-12 11:00 | 86.8009 | 0 | 0 | 0
2018-04-12 12:00 | 86.6728 | 0 | 0 | 0
2018-04-12 13:00 | 86.6316 | 0 | 0 | 0
2018-04-12 14:00 | 86.6316 | 0 | 0 | 0
2018-04-12 15:00 | 86.6636 | 0 | 0 | 0
2018-04-12 16:00 | 86.5568 | 0 | 0 | 0
2018-04-12 17:00 | 86.6865 | 0 | 0 | 0
2018-04-12 18:00 | 86.7262 | 0 | 0 | 0
2018-04-12 19:00 | 86.5187 | 0 | 0 | 0
2018-04-12 20:00 | 86.5766 | 0 | 0 | 0
2018-04-12 21:00 | 86.6194 | 0 | 0 | 0
2018-04-12 22:00 | 86.6743 | 0 | 0 | 0
2018-04-12 23:00 | 86.5644 | 0 | 0 | 0
2018-04-13 | 86.2226 | 86.688 | 0 | 32.9414
2018-04-13 01:00 | 86.1128 | 86.5232 | 0 | 32.8788
2018-04-13 02:00 | 86.2791 | 86.6896 | 0 | 32.942
2018-04-13 03:00 | 86.0014 | 86.4485 | 0 | 32.8504
2018-04-13 04:00 | 86.0533 | 86.4347 | 0 | 32.8452
2018-04-13 05:00 | 86.2257 | 86.6117 | 0 | 32.9124
2018-04-13 06:00 | 86.4332 | 86.9352 | 0 | 33.0354
2018-04-13 07:00 | 86.5873 | 87.0619 | 0 | 33.0835
2018-04-13 08:00 | 86.3691 | 86.7811 | 0 | 32.9768
2018-04-13 09:00 | 86.334 | 86.7399 | 0 | 32.9612
2018-04-13 10:00 | 86.5126 | 86.862 | 0 | 33.0076
2018-04-13 11:00 | 86.5003 | 86.9306 | 0 | 33.0336
2018-04-13 12:00 | 86.7002 | 87.1412 | 0 | 33.1137
2018-04-13 13:00 | 86.363 | 86.8009 | 0 | 32.9843
2018-04-13 14:00 | 86.4408 | 86.8635 | 0 | 33.0081
2018-04-13 15:00 | 86.2943 | 86.6743 | 0 | 32.9362
2018-04-13 16:00 | 86.3706 | 86.7491 | 0 | 32.9647
2018-04-13 17:00 | 86.2882 | 86.7445 | 0 | 32.9629
2018-04-13 18:00 | 86.1875 | 86.6667 | 0 | 32.9333
2018-04-13 19:00 | 86.099 | 86.5431 | 0 | 32.8864
2018-04-13 20:00 | 86.1997 | 86.5187 | 0 | 32.8771
2018-04-13 21:00 | 86.3767 | 86.7247 | 0 | 32.9554
2018-04-13 22:00 | 86.3691 | 86.7659 | 0 | 32.971
2018-04-13 23:00 | 86.4012 | 86.7918 | 0 | 32.9809
2018-04-14 | 86.0121 | 0 | 86.5507 | 32.8893
2018-04-14 01:00 | 85.919 | 0 | 86.5324 | 32.8823
2018-04-14 02:00 | 86.0533 | 0 | 86.6453 | 32.9252
2018-04-14 03:00 | 86.1677 | 0 | 86.7002 | 32.9461
2018-04-14 04:00 | 86.3081 | 0 | 86.8513 | 33.0035
2018-04-14 05:00 | 86.2562 | 0 | 86.8605 | 33.007
2018-04-14 06:00 | 86.1234 | 0 | 86.6682 | 32.9339
2018-04-14 07:00 | 86.1906 | 0 | 86.7247 | 32.9554
2018-04-14 08:00 | 86.36 | 0 | 86.952 | 33.0418
2018-04-14 09:00 | 86.4912 | 0 | 87.0588 | 33.0823
2018-04-14 10:00 | 86.1982 | 0 | 86.6392 | 32.9229
2018-04-14 11:00 | 86.1707 | 0 | 86.8849 | 33.0163
2018-04-14 12:00 | 86.5019 | 0 | 87.1504 | 33.1172
2018-04-14 13:00 | 86.6148 | 0 | 87.3167 | 33.1803
2018-04-14 14:00 | 86.4439 | 0 | 87.0832 | 33.0916
2018-04-14 15:00 | 86.5522 | 0 | 87.2938 | 33.1716
2018-04-14 16:00 | 86.5644 | 0 | 87.3579 | 33.196
2018-04-14 17:00 | 86.7445 | 0 | 87.57 | 33.2766
2018-04-14 18:00 | 86.4668 | 0 | 87.3014 | 33.1745
2018-04-14 19:00 | 86.3661 | 0 | 87.0954 | 33.0963
2018-04-14 20:00 | 86.1173 | 0 | 86.891 | 33.0186
2018-04-14 21:00 | 86.1555 | 0 | 86.9245 | 33.0313
2018-04-14 22:00 | 86.2211 | 0 | 87.0054 | 33.0621
2018-04-14 23:00 | 86.2226 | 0 | 87.0787 | 33.0899
2018-04-15 | 86.2364 | 86.7994 | 0 | 32.9838
2018-04-15 01:00 | 86.3188 | 86.952 | 0 | 33.0418
2018-04-15 02:00 | 86.2119 | 86.8177 | 0 | 32.9907
2018-04-15 03:00 | 86.1845 | 86.7857 | 0 | 32.9786
2018-04-15 04:00 | 86.2455 | 86.833 | 0 | 32.9965
2018-04-15 05:00 | 86.2333 | 86.833 | 0 | 32.9965
2018-04-15 06:00 | 86.2776 | 86.8528 | 0 | 33.0041
2018-04-15 07:00 | 86.2867 | 86.8452 | 0 | 33.0012
2018-04-15 08:00 | 86.2989 | 86.9032 | 0 | 33.0232
2018-04-15 09:00 | 86.2867 | 86.8162 | 0 | 32.9902
2018-04-15 10:00 | 86.2882 | 86.8528 | 0 | 33.0041
2018-04-15 11:00 | 86.1845 | 86.743 | 0 | 32.9623
2018-04-15 12:00 | 86.1418 | 86.714 | 0 | 32.9513
2018-04-15 13:00 | 86.1479 | 86.7659 | 0 | 32.971
2018-04-15 14:00 | 86.1112 | 86.7018 | 0 | 32.9467
2018-04-15 15:00 | 86.2455 | 86.8482 | 0 | 33.0023
2018-04-15 16:00 | 86.3447 | 86.9398 | 0 | 33.0371
2018-04-15 17:00 | 86.4805 | 86.9856 | 0 | 33.0545
2018-04-15 18:00 | 86.4332 | 86.92 | 0 | 33.0296
2018-04-15 19:00 | 85.6794 | 85.9266 | 0 | 32.6521
2018-04-15 20:00 | 86.3294 | 86.5888 | 0 | 32.9037
2018-04-15 21:00 | 86.3569 | 86.6728 | 0 | 32.9357
2018-04-15 22:00 | 86.4881 | 86.8086 | 0 | 32.9873
2018-04-15 23:00 | 86.4332 | 86.7353 | 0 | 32.9594
2018-04-16 | 86.4088 | 86.7002 | 86.9352 | 65.9815
2018-04-16 01:00 | 86.0426 | 86.3127 | 86.5278 | 65.6794
2018-04-16 02:00 | 86.392 | 86.6392 | 86.8421 | 65.9229
2018-04-16 03:00 | 86.2776 | 86.5766 | 86.7536 | 65.8655
2018-04-16 04:00 | 86.5034 | 86.8849 | 87.0283 | 66.087
2018-04-16 05:00 | 86.3661 | 86.772 | 87.0054 | 66.0354
2018-04-16 06:00 | 86.2898 | 86.6499 | 86.8147 | 65.9165
2018-04-16 07:00 | 86.2043 | 86.5278 | 86.7079 | 65.8296
2018-04-16 08:00 | 86.3355 | 86.5461 | 86.8025 | 65.8725
2018-04-16 09:00 | 86.3798 | 86.7262 | 86.8711 | 65.967
2018-04-16 10:00 | 86.2272 | 86.5156 | 86.714 | 65.8272
2018-04-16 11:00 | 86.2119 | 86.5141 | 86.7201 | 65.829
2018-04-16 12:00 | 86.389 | 86.6835 | 86.8574 | 65.9455
2018-04-16 13:00 | 86.4027 | 86.6224 | 86.7475 | 65.8806
2018-04-16 14:00 | 86.3783 | 86.6606 | 86.7903 | 65.9113
2018-04-16 15:00 | 86.3355 | 86.5248 | 86.7384 | 65.84
2018-04-16 16:00 | 86.3493 | 86.4912 | 86.685 | 65.807
2018-04-16 17:00 | 86.244 | 86.4683 | 86.6743 | 65.7942
2018-04-16 18:00 | 86.3142 | 86.4378 | 86.5934 | 65.7519
2018-04-16 19:00 | 86.2089 | 86.3508 | 86.5583 | 65.7055
2018-04-16 20:00 | 86.2181 | 86.4836 | 86.6896 | 65.8058
2018-04-16 21:00 | 86.1494 | 86.4759 | 86.63 | 65.7802
2018-04-16 22:00 | 86.2593 | 86.5522 | 86.6468 | 65.8156
2018-04-16 23:00 | 86.4424 | 86.8055 | 86.8864 | 66.0029
2018-04-17 | 86.4637 | 0 | 0 | 0
2018-04-17 01:00 | 86.5629 | 0 | 0 | 0
2018-04-17 02:00 | 86.3706 | 0 | 0 | 0
2018-04-17 03:00 | 86.3523 | 0 | 0 | 0
2018-04-17 04:00 | 86.3676 | 0 | 0 | 0
2018-04-17 05:00 | 86.4027 | 0 | 0 | 0
2018-04-17 06:00 | 86.4652 | 0 | 0 | 0
2018-04-17 07:00 | 86.4012 | 0 | 0 | 0
2018-04-17 08:00 | 86.4515 | 0 | 0 | 0
2018-04-17 09:00 | 86.2028 | 0 | 0 | 0
2018-04-17 10:00 | 86.2715 | 0 | 0 | 0
2018-04-17 11:00 | 86.7567 | 0 | 0 | 0
2018-04-17 12:00 | 86.6194 | 0 | 0 | 0
2018-04-17 13:00 | 86.6377 | 0 | 0 | 0
2018-04-17 14:00 | 86.8757 | 0 | 0 | 0
2018-04-17 15:00 | 86.7994 | 0 | 0 | 0
2018-04-17 16:00 | 86.7674 | 0 | 0 | 0
2018-04-17 17:00 | 86.7384 | 0 | 0 | 0
2018-04-17 18:00 | 86.7124 | 0 | 0 | 0
2018-04-17 19:00 | 86.8376 | 0 | 0 | 0
2018-04-17 20:00 | 86.627 | 0 | 0 | 0
2018-04-17 21:00 | 86.6239 | 0 | 0 | 0
2018-04-17 22:00 | 86.714 | 0 | 0 | 0
2018-04-17 23:00 | 86.8971 | 0 | 0 | 0
2018-04-18 | 0 | 0 | 86.6712 | 32.9351
2018-04-18 01:00 | 0 | 0 | 86.511 | 32.8742
2018-04-18 02:00 | 0 | 0 | 86.7628 | 32.9699
2018-04-18 03:00 | 0 | 0 | 86.7384 | 32.9606
2018-04-18 04:00 | 0 | 0 | 86.8376 | 32.9983
2018-04-18 05:00 | 0 | 0 | 87.0222 | 33.0684
2018-04-18 06:00 | 0 | 0 | 86.9627 | 33.0458
2018-04-18 07:00 | 0 | 0 | 87.1321 | 33.1102
2018-04-18 08:00 | 0 | 0 | 87.1931 | 33.1334
2018-04-18 09:00 | 0 | 0 | 86.7155 | 32.9519
2018-04-18 10:00 | 0 | 0 | 86.6743 | 32.9362
2018-04-18 11:00 | 0 | 0 | 86.8956 | 33.0203
2018-04-18 12:00 | 0 | 0 | 86.9276 | 33.0325
2018-04-18 13:00 | 0 | 0 | 87.2541 | 33.1566
2018-04-18 14:00 | 0 | 0 | 87.4037 | 33.2134
2018-04-18 15:00 | 0 | 0 | 87.2129 | 33.1409
2018-04-18 16:00 | 0 | 0 | 86.9718 | 33.0493
2018-04-18 17:00 | 0 | 0 | 87.1397 | 33.1131
2018-04-18 18:00 | 0 | 0 | 87.2435 | 33.1525
2018-04-18 19:00 | 0 | 0 | 86.8894 | 33.018
2018-04-18 20:00 | 0 | 0 | 87.1839 | 33.1299
2018-04-18 21:00 | 0 | 0 | 87.2419 | 33.1519
2018-04-18 22:00 | 0 | 0 | 87.1733 | 33.1259
2018-04-18 23:00 | 0 | 0 | 87.2557 | 33.1572
2018-04-19 | 86.5492 | 0 | 0 | 0
2018-04-19 01:00 | 86.7201 | 0 | 0 | 0
2018-04-19 02:00 | 86.5095 | 0 | 0 | 0
2018-04-19 03:00 | 86.4576 | 0 | 0 | 0
2018-04-19 04:00 | 86.6316 | 0 | 0 | 0
2018-04-19 05:00 | 86.569 | 0 | 0 | 0
2018-04-19 06:00 | 86.6468 | 0 | 0 | 0
2018-04-19 07:00 | 86.6361 | 0 | 0 | 0
2018-04-19 08:00 | 86.6819 | 0 | 0 | 0
2018-04-19 09:00 | 86.7094 | 0 | 0 | 0
2018-04-19 10:00 | 86.7933 | 0 | 0 | 0
2018-04-19 11:00 | 86.8009 | 0 | 0 | 0
2018-04-19 12:00 | 86.6728 | 0 | 0 | 0
2018-04-19 13:00 | 86.6316 | 0 | 0 | 0
2018-04-19 14:00 | 86.6316 | 0 | 0 | 0
2018-04-19 15:00 | 86.6636 | 0 | 0 | 0
2018-04-19 16:00 | 86.5568 | 0 | 0 | 0
2018-04-19 17:00 | 86.6865 | 0 | 0 | 0
2018-04-19 18:00 | 86.7262 | 0 | 0 | 0
2018-04-19 19:00 | 86.5187 | 0 | 0 | 0
2018-04-19 20:00 | 86.5766 | 0 | 0 | 0
2018-04-19 21:00 | 86.6194 | 0 | 0 | 0
2018-04-19 22:00 | 86.6743 | 0 | 0 | 0
2018-04-19 23:00 | 86.5644 | 0 | 0 | 0
2018-04-20 | 86.2226 | 86.688 | 0 | 32.9414
2018-04-20 01:00 | 86.1128 | 86.5232 | 0 | 32.8788
2018-04-20 02:00 | 86.2791 | 86.6896 | 0 | 32.942
2018-04-20 03:00 | 86.0014 | 86.4485 | 0 | 32.8504
2018-04-20 04:00 | 86.0533 | 86.4347 | 0 | 32.8452
2018-04-20 05:00 | 86.2257 | 86.6117 | 0 | 32.9124
2018-04-20 06:00 | 86.4332 | 86.9352 | 0 | 33.0354
2018-04-20 07:00 | 86.5873 | 87.0619 | 0 | 33.0835
2018-04-20 08:00 | 86.3691 | 86.7811 | 0 | 32.9768
2018-04-20 09:00 | 86.334 | 86.7399 | 0 | 32.9612
2018-04-20 10:00 | 86.5126 | 86.862 | 0 | 33.0076
2018-04-20 11:00 | 86.5003 | 86.9306 | 0 | 33.0336
2018-04-20 12:00 | 86.7002 | 87.1412 | 0 | 33.1137
2018-04-20 13:00 | 86.363 | 86.8009 | 0 | 32.9843
2018-04-20 14:00 | 86.4408 | 86.8635 | 0 | 33.0081
2018-04-20 15:00 | 86.2943 | 86.6743 | 0 | 32.9362
2018-04-20 16:00 | 86.3706 | 86.7491 | 0 | 32.9647
2018-04-20 17:00 | 86.2882 | 86.7445 | 0 | 32.9629
2018-04-20 18:00 | 86.1875 | 86.6667 | 0 | 32.9333
2018-04-20 19:00 | 86.099 | 86.5431 | 0 | 32.8864
2018-04-20 20:00 | 86.1997 | 86.5187 | 0 | 32.8771
2018-04-20 21:00 | 86.3767 | 86.7247 | 0 | 32.9554
2018-04-20 22:00 | 86.3691 | 86.7659 | 0 | 32.971
2018-04-20 23:00 | 86.4012 | 86.7918 | 0 | 32.9809
2018-04-21 | 86.0121 | 0 | 86.5507 | 32.8893
2018-04-21 01:00 | 85.919 | 0 | 86.5324 | 32.8823
2018-04-21 02:00 | 86.0533 | 0 | 86.6453 | 32.9252
2018-04-21 03:00 | 86.1677 | 0 | 86.7002 | 32.9461
2018-04-21 04:00 | 86.3081 | 0 | 86.8513 | 33.0035
2018-04-21 05:00 | 86.2562 | 0 | 86.8605 | 33.007
2018-04-21 06:00 | 86.1234 | 0 | 86.6682 | 32.9339
2018-04-21 07:00 | 86.1906 | 0 | 86.7247 | 32.9554
2018-04-21 08:00 | 86.36 | 0 | 86.952 | 33.0418
2018-04-21 09:00 | 86.4912 | 0 | 87.0588 | 33.0823
2018-04-21 10:00 | 86.1982 | 0 | 86.6392 | 32.9229
2018-04-21 11:00 | 86.1707 | 0 | 86.8849 | 33.0163
2018-04-21 12:00 | 86.5019 | 0 | 87.1504 | 33.1172
2018-04-21 13:00 | 86.6148 | 0 | 87.3167 | 33.1803
2018-04-21 14:00 | 86.4439 | 0 | 87.0832 | 33.0916
2018-04-21 15:00 | 86.5522 | 0 | 87.2938 | 33.1716
2018-04-21 16:00 | 86.5644 | 0 | 87.3579 | 33.196
2018-04-21 17:00 | 86.7445 | 0 | 87.57 | 33.2766
2018-04-21 18:00 | 86.4668 | 0 | 87.3014 | 33.1745
2018-04-21 19:00 | 86.3661 | 0 | 87.0954 | 33.0963
2018-04-21 20:00 | 86.1173 | 0 | 86.891 | 33.0186
2018-04-21 21:00 | 86.1555 | 0 | 86.9245 | 33.0313
2018-04-21 22:00 | 86.2211 | 0 | 87.0054 | 33.0621
2018-04-21 23:00 | 86.2226 | 0 | 87.0787 | 33.0899
2018-04-22 | 86.2364 | 86.7994 | 0 | 32.9838
2018-04-22 01:00 | 86.3188 | 86.952 | 0 | 33.0418
2018-04-22 02:00 | 86.2119 | 86.8177 | 0 | 32.9907
2018-04-22 03:00 | 86.1845 | 86.7857 | 0 | 32.9786
2018-04-22 04:00 | 86.2455 | 86.833 | 0 | 32.9965
2018-04-22 05:00 | 86.2333 | 86.833 | 0 | 32.9965
2018-04-22 06:00 | 86.2776 | 86.8528 | 0 | 33.0041
2018-04-22 07:00 | 86.2867 | 86.8452 | 0 | 33.0012
2018-04-22 08:00 | 86.2989 | 86.9032 | 0 | 33.0232
2018-04-22 09:00 | 86.2867 | 86.8162 | 0 | 32.9902
2018-04-22 10:00 | 86.2882 | 86.8528 | 0 | 33.0041
2018-04-22 11:00 | 86.1845 | 86.743 | 0 | 32.9623
2018-04-22 12:00 | 86.1418 | 86.714 | 0 | 32.9513
2018-04-22 13:00 | 86.1479 | 86.7659 | 0 | 32.971
2018-04-22 14:00 | 86.1112 | 86.7018 | 0 | 32.9467
2018-04-22 15:00 | 86.2455 | 86.8482 | 0 | 33.0023
2018-04-22 16:00 | 86.3447 | 86.9398 | 0 | 33.0371
2018-04-22 17:00 | 86.4805 | 86.9856 | 0 | 33.0545
2018-04-22 18:00 | 86.4332 | 86.92 | 0 | 33.0296
2018-04-22 19:00 | 85.6794 | 85.9266 | 0 | 32.6521
2018-04-22 20:00 | 86.3294 | 86.5888 | 0 | 32.9037
2018-04-22 21:00 | 86.3569 | 86.6728 | 0 | 32.9357
2018-04-22 22:00 | 86.4881 | 86.8086 | 0 | 32.9873
2018-04-22 23:00 | 86.4332 | 86.7353 | 0 | 32.9594
2018-04-23 | 86.4088 | 86.7002 | 86.9352 | 65.9815
2018-04-23 01:00 | 86.0426 | 86.3127 | 86.5278 | 65.6794
2018-04-23 02:00 | 86.392 | 86.6392 | 86.8421 | 65.9229
2018-04-23 03:00 | 86.2776 | 86.5766 | 86.7536 | 65.8655
2018-04-23 04:00 | 86.5034 | 86.8849 | 87.0283 | 66.087
2018-04-23 05:00 | 86.3661 | 86.772 | 87.0054 | 66.0354
2018-04-23 06:00 | 86.2898 | 86.6499 | 86.8147 | 65.9165
2018-04-23 07:00 | 86.2043 | 86.5278 | 86.7079 | 65.8296
2018-04-23 08:00 | 86.3355 | 86.5461 | 86.8025 | 65.8725
2018-04-23 09:00 | 86.3798 | 86.7262 | 86.8711 | 65.967
2018-04-23 10:00 | 86.2272 | 86.5156 | 86.714 | 65.8272
2018-04-23 11:00 | 86.2119 | 86.5141 | 86.7201 | 65.829
2018-04-23 12:00 | 86.389 | 86.6835 | 86.8574 | 65.9455
2018-04-23 13:00 | 86.4027 | 86.6224 | 86.7475 | 65.8806
2018-04-23 14:00 | 86.3783 | 86.6606 | 86.7903 | 65.9113
2018-04-23 15:00 | 86.3355 | 86.5248 | 86.7384 | 65.84
2018-04-23 16:00 | 86.3493 | 86.4912 | 86.685 | 65.807
2018-04-23 17:00 | 86.244 | 86.4683 | 86.6743 | 65.7942
2018-04-23 18:00 | 86.3142 | 86.4378 | 86.5934 | 65.7519
2018-04-23 19:00 | 86.2089 | 86.3508 | 86.5583 | 65.7055
2018-04-23 20:00 | 86.2181 | 86.4836 | 86.6896 | 65.8058
2018-04-23 21:00 | 86.1494 | 86.4759 | 86.63 | 65.7802
2018-04-23 22:00 | 86.2593 | 86.5522 | 86.6468 | 65.8156
2018-04-23 23:00 | 86.4424 | 86.8055 | 86.8864 | 66.0029
2018-04-24 | 86.4637 | 0 | 0 | 0
2018-04-24 01:00 | 86.5629 | 0 | 0 | 0
2018-04-24 02:00 | 86.3706 | 0 | 0 | 0
2018-04-24 03:00 | 86.3523 | 0 | 0 | 0
2018-04-24 04:00 | 86.3676 | 0 | 0 | 0
2018-04-24 05:00 | 86.4027 | 0 | 0 | 0
2018-04-24 06:00 | 86.4652 | 0 | 0 | 0
2018-04-24 07:00 | 86.4012 | 0 | 0 | 0
2018-04-24 08:00 | 86.4515 | 0 | 0 | 0
2018-04-24 09:00 | 86.2028 | 0 | 0 | 0
2018-04-24 10:00 | 86.2715 | 0 | 0 | 0
2018-04-24 11:00 | 86.7567 | 0 | 0 | 0
2018-04-24 12:00 | 86.6194 | 0 | 0 | 0
2018-04-24 13:00 | 86.6377 | 0 | 0 | 0
2018-04-24 14:00 | 86.8757 | 0 | 0 | 0
2018-04-24 15:00 | 86.7994 | 0 | 0 | 0
2018-04-24 16:00 | 86.7674 | 0 | 0 | 0
2018-04-24 17:00 | 86.7384 | 0 | 0 | 0
2018-04-24 18:00 | 86.7124 | 0 | 0 | 0
2018-04-24 19:00 | 86.8376 | 0 | 0 | 0
2018-04-24 20:00 | 86.627 | 0 | 0 | 0
2018-04-24 21:00 | 86.6239 | 0 | 0 | 0
2018-04-24 22:00 | 86.714 | 0 | 0 | 0
2018-04-24 23:00 | 86.8971 | 0 | 0 | 0
2018-04-25 | 0 | 0 | 86.6712 | 32.9351
2018-04-25 01:00 | 0 | 0 | 86.511 | 32.8742
2018-04-25 02:00 | 0 | 0 | 86.7628 | 32.9699
2018-04-25 03:00 | 0 | 0 | 86.7384 | 32.9606
2018-04-25 04:00 | 0 | 0 | 86.8376 | 32.9983
2018-04-25 05:00 | 0 | 0 | 87.0222 | 33.0684
2018-04-25 06:00 | 0 | 0 | 86.9627 | 33.0458
2018-04-25 07:00 | 0 | 0 | 87.1321 | 33.1102
2018-04-25 08:00 | 0 | 0 | 87.1931 | 33.1334
2018-04-25 09:00 | 0 | 0 | 86.7155 | 32.9519
2018-04-25 10:00 | 0 | 0 | 86.6743 | 32.9362
2018-04-25 11:00 | 0 | 0 | 86.8956 | 33.0203
2018-04-25 12:00 | 0 | 0 | 86.9276 | 33.0325
2018-04-25 13:00 | 0 | 0 | 87.2541 | 33.1566
2018-04-25 14:00 | 0 | 0 | 87.4037 | 33.2134
2018-04-25 15:00 | 0 | 0 | 87.2129 | 33.1409
2018-04-25 16:00 | 0 | 0 | 86.9718 | 33.0493
2018-04-25 17:00 | 0 | 0 | 87.1397 | 33.1131
2018-04-25 18:00 | 0 | 0 | 87.2435 | 33.1525
2018-04-25 19:00 | 0 | 0 | 86.8894 | 33.018
2018-04-25 20:00 | 0 | 0 | 87.1839 | 33.1299
2018-04-25 21:00 | 0 | 0 | 87.2419 | 33.1519
2018-04-25 22:00 | 0 | 0 | 87.1733 | 33.1259
2018-04-25 23:00 | 0 | 0 | 87.2557 | 33.1572
2018-04-26 | 86.5492 | 0 | 0 | 0
2018-04-26 01:00 | 86.7201 | 0 | 0 | 0
2018-04-26 02:00 | 86.5095 | 0 | 0 | 0
2018-04-26 03:00 | 86.4576 | 0 | 0 | 0
2018-04-26 04:00 | 86.6316 | 0 | 0 | 0
2018-04-26 05:00 | 86.569 | 0 | 0 | 0
2018-04-26 06:00 | 86.6468 | 0 | 0 | 0
2018-04-26 07:00 | 86.6361 | 0 | 0 | 0
2018-04-26 08:00 | 86.6819 | 0 | 0 | 0
2018-04-26 09:00 | 86.7094 | 0 | 0 | 0
2018-04-26 10:00 | 86.7933 | 0 | 0 | 0
2018-04-26 11:00 | 86.8009 | 0 | 0 | 0
2018-04-26 12:00 | 86.6728 | 0 | 0 | 0
2018-04-26 13:00 | 86.6316 | 0 | 0 | 0
2018-04-26 14:00 | 86.6316 | 0 | 0 | 0
2018-04-26 15:00 | 86.6636 | 0 | 0 | 0
2018-04-26 16:00 | 86.5568 | 0 | 0 | 0
2018-04-26 17:00 | 86.6865 | 0 | 0 | 0
2018-04-26 18:00 | 86.7262 | 0 | 0 | 0
2018-04-26 19:00 | 86.5187 | 0 | 0 | 0
2018-04-26 20:00 | 86.5766 | 0 | 0 | 0
2018-04-26 21:00 | 86.6194 | 0 | 0 | 0
2018-04-26 22:00 | 86.6743 | 0 | 0 | 0
2018-04-26 23:00 | 86.5644 | 0 | 0 | 0
2018-04-27 | 86.2226 | 86.688 | 0 | 32.9414
2018-04-27 01:00 | 86.1128 | 86.5232 | 0 | 32.8788
2018-04-27 02:00 | 86.2791 | 86.6896 | 0 | 32.942
2018-04-27 03:00 | 86.0014 | 86.4485 | 0 | 32.8504
2018-04-27 04:00 | 86.0533 | 86.4347 | 0 | 32.8452
2018-04-27 05:00 | 86.2257 | 86.6117 | 0 | 32.9124
2018-04-27 06:00 | 86.4332 | 86.9352 | 0 | 33.0354
2018-04-27 07:00 | 86.5873 | 87.0619 | 0 | 33.0835
2018-04-27 08:00 | 86.3691 | 86.7811 | 0 | 32.9768
2018-04-27 09:00 | 86.334 | 86.7399 | 0 | 32.9612
2018-04-27 10:00 | 86.5126 | 86.862 | 0 | 33.0076
2018-04-27 11:00 | 86.5003 | 86.9306 | 0 | 33.0336
2018-04-27 12:00 | 86.7002 | 87.1412 | 0 | 33.1137
2018-04-27 13:00 | 86.363 | 86.8009 | 0 | 32.9843
2018-04-27 14:00 | 86.4408 | 86.8635 | 0 | 33.0081
2018-04-27 15:00 | 86.2943 | 86.6743 | 0 | 32.9362
2018-04-27 16:00 | 86.3706 | 86.7491 | 0 | 32.9647
2018-04-27 17:00 | 86.2882 | 86.7445 | 0 | 32.9629
2018-04-27 18:00 | 86.1875 | 86.6667 | 0 | 32.9333
2018-04-27 19:00 | 86.099 | 86.5431 | 0 | 32.8864
2018-04-27 20:00 | 86.1997 | 86.5187 | 0 | 32.8771
2018-04-27 21:00 | 86.3767 | 86.7247 | 0 | 32.9554
2018-04-27 22:00 | 86.3691 | 86.7659 | 0 | 32.971
2018-04-27 23:00 | 86.4012 | 86.7918 | 0 | 32.9809
2018-04-28 | 86.0121 | 0 | 86.5507 | 32.8893
2018-04-28 01:00 | 85.919 | 0 | 86.5324 | 32.8823
2018-04-28 02:00 | 86.0533 | 0 | 86.6453 | 32.9252
2018-04-28 03:00 | 86.1677 | 0 | 86.7002 | 32.9461
2018-04-28 04:00 | 86.3081 | 0 | 86.8513 | 33.0035
2018-04-28 05:00 | 86.2562 | 0 | 86.8605 | 33.007
2018-04-28 06:00 | 86.1234 | 0 | 86.6682 | 32.9339
2018-04-28 07:00 | 86.1906 | 0 | 86.7247 | 32.9554
2018-04-28 08:00 | 86.36 | 0 | 86.952 | 33.0418
2018-04-28 09:00 | 86.4912 | 0 | 87.0588 | 33.0823
2018-04-28 10:00 | 86.1982 | 0 | 86.6392 | 32.9229
2018-04-28 11:00 | 86.1707 | 0 | 86.8849 | 33.0163
2018-04-28 12:00 | 86.5019 | 0 | 87.1504 | 33.1172
2018-04-28 13:00 | 86.6148 | 0 | 87.3167 | 33.1803
2018-04-28 14:00 | 86.4439 | 0 | 87.0832 | 33.0916
2018-04-28 15:00 | 86.5522 | 0 | 87.2938 | 33.1716
2018-04-28 16:00 | 86.5644 | 0 | 87.3579 | 33.196
2018-04-28 17:00 | 86.7445 | 0 | 87.57 | 33.2766
2018-04-28 18:00 | 86.4668 | 0 | 87.3014 | 33.1745
2018-04-28 19:00 | 86.3661 | 0 | 87.0954 | 33.0963
2018-04-28 20:00 | 86.1173 | 0 | 86.891 | 33.0186
2018-04-28 21:00 | 86.1555 | 0 | 86.9245 | 33.0313
2018-04-28 22:00 | 86.2211 | 0 | 87.0054 | 33.0621
2018-04-28 23:00 | 86.2226 | 0 | 87.0787 | 33.0899
2018-04-29 | 86.2364 | 86.7994 | 0 | 32.9838
2018-04-29 01:00 | 86.3188 | 86.952 | 0 | 33.0418
2018-04-29 02:00 | 86.2119 | 86.8177 | 0 | 32.9907
2018-04-29 03:00 | 86.1845 | 86.7857 | 0 | 32.9786
2018-04-29 04:00 | 86.2455 | 86.833 | 0 | 32.9965
2018-04-29 05:00 | 86.2333 | 86.833 | 0 | 32.9965
2018-04-29 06:00 | 86.2776 | 86.8528 | 0 | 33.0041
2018-04-29 07:00 | 86.2867 | 86.8452 | 0 | 33.0012
2018-04-29 08:00 | 86.2989 | 86.9032 | 0 | 33.0232
2018-04-29 09:00 | 86.2867 | 86.8162 | 0 | 32.9902
2018-04-29 10:00 | 86.2882 | 86.8528 | 0 | 33.0041
2018-04-29 11:00 | 86.1845 | 86.743 | 0 | 32.9623
2018-04-29 12:00 | 86.1418 | 86.714 | 0 | 32.9513
2018-04-29 13:00 | 86.1479 | 86.7659 | 0 | 32.971
2018-04-29 14:00 | 86.1112 | 86.7018 | 0 | 32.9467
2018-04-29 15:00 | 86.2455 | 86.8482 | 0 | 33.0023
2018-04-29 16:00 | 86.3447 | 86.9398 | 0 | 33.0371
2018-04-29 17:00 | 86.4805 | 86.9856 | 0 | 33.0545
2018-04-29 18:00 | 86.4332 | 86.92 | 0 | 33.0296
2018-04-29 19:00 | 85.6794 | 85.9266 | 0 | 32.6521
2018-04-29 20:00 | 86.3294 | 86.5888 | 0 | 32.9037
2018-04-29 21:00 | 86.3569 | 86.6728 | 0 | 32.9357
2018-04-29 22:00 | 86.4881 | 86.8086 | 0 | 32.9873
2018-04-29 23:00 | 86.4332 | 86.7353 | 0 | 32.9594
2018-04-30 | 86.4088 | 86.7002 | 86.9352 | 65.9815
2018-04-30 01:00 | 86.0426 | 86.3127 | 86.5278 | 65.6794
2018-04-30 02:00 | 86.392 | 86.6392 | 86.8421 | 65.9229
2018-04-30 03:00 | 86.2776 | 86.5766 | 86.7536 | 65.8655
2018-04-30 04:00 | 86.5034 | 86.8849 | 87.0283 | 66.087
2018-04-30 05:00 | 86.3661 | 86.772 | 87.0054 | 66.0354
2018-04-30 06:00 | 86.2898 | 86.6499 | 86.8147 | 65.9165
2018-04-30 07:00 | 86.2043 | 86.5278 | 86.7079 | 65.8296
2018-04-30 08:00 | 86.3355 | 86.5461 | 86.8025 | 65.8725
2018-04-30 09:00 | 86.3798 | 86.7262 | 86.8711 | 65.967
2018-04-30 10:00 | 86.2272 | 86.5156 | 86.714 | 65.8272
2018-04-30 11:00 | 86.2119 | 86.5141 | 86.7201 | 65.829
2018-04-30 12:00 | 86.389 | 86.6835 | 86.8574 | 65.9455
2018-04-30 13:00 | 86.4027 | 86.6224 | 86.7475 | 65.8806
2018-04-30 14:00 | 86.3783 | 86.6606 | 86.7903 | 65.9113
2018-04-30 15:00 | 86.3355 | 86.5248 | 86.7384 | 65.84
2018-04-30 16:00 | 86.3493 | 86.4912 | 86.685 | 65.807
2018-04-30 17:00 | 86.244 | 86.4683 | 86.6743 | 65.7942
2018-04-30 18:00 | 86.3142 | 86.4378 | 86.5934 | 65.7519
2018-04-30 19:00 | 86.2089 | 86.3508 | 86.5583 | 65.7055
2018-04-30 20:00 | 86.2181 | 86.4836 | 86.6896 | 65.8058
2018-04-30 21:00 | 86.1494 | 86.4759 | 86.63 | 65.7802
2018-04-30 22:00 | 86.2593 | 86.5522 | 86.6468 | 65.8156
2018-04-30 23:00 | 86.4424 | 86.8055 | 86.8864 | 66.0029
2018-05-01 | 86.4637 | 0 | 0 | 0
2018-05-01 01:00 | 86.5629 | 0 | 0 | 0
2018-05-01 02:00 | 86.3706 | 0 | 0 | 0
2018-05-01 03:00 | 86.3523 | 0 | 0 | 0
2018-05-01 04:00 | 86.3676 | 0 | 0 | 0
2018-05-01 05:00 | 86.4027 | 0 | 0 | 0
2018-05-01 06:00 | 86.4652 | 0 | 0 | 0
2018-05-01 07:00 | 86.4012 | 0 | 0 | 0
2018-05-01 08:00 | 86.4515 | 0 | 0 | 0
2018-05-01 09:00 | 86.2028 | 0 | 0 | 0
2018-05-01 10:00 | 86.2715 | 0 | 0 | 0
2018-05-01 11:00 | 86.7567 | 0 | 0 | 0
2018-05-01 12:00 | 86.6194 | 0 | 0 | 0
2018-05-01 13:00 | 86.6377 | 0 | 0 | 0
2018-05-01 14:00 | 86.8757 | 0 | 0 | 0
2018-05-01 15:00 | 86.7994 | 0 | 0 | 0
2018-05-01 16:00 | 86.7674 | 0 | 0 | 0
2018-05-01 17:00 | 86.7384 | 0 | 0 | 0
2018-05-01 18:00 | 86.7124 | 0 | 0 | 0
2018-05-01 19:00 | 86.8376 | 0 | 0 | 0
2018-05-01 20:00 | 86.627 | 0 | 0 | 0
2018-05-01 21:00 | 86.6239 | 0 | 0 | 0
2018-05-01 22:00 | 86.714 | 0 | 0 | 0
2018-05-01 23:00 | 86.8971 | 0 | 0 | 0
2018-05-02 | 0 | 0 | 86.6712 | 32.9351
2018-05-02 01:00 | 0 | 0 | 86.511 | 32.8742
2018-05-02 02:00 | 0 | 0 | 86.7628 | 32.9699
2018-05-02 03:00 | 0 | 0 | 86.7384 | 32.9606
2018-05-02 04:00 | 0 | 0 | 86.8376 | 32.9983
2018-05-02 05:00 | 0 | 0 | 87.0222 | 33.0684
2018-05-02 06:00 | 0 | 0 | 86.9627 | 33.0458
2018-05-02 07:00 | 0 | 0 | 87.1321 | 33.1102
2018-05-02 08:00 | 0 | 0 | 87.1931 | 33.1334
2018-05-02 09:00 | 0 | 0 | 86.7155 | 32.9519
2018-05-02 10:00 | 0 | 0 | 86.6743 | 32.9362
2018-05-02 11:00 | 0 | 0 | 86.8956 | 33.0203
2018-05-02 12:00 | 0 | 0 | 86.9276 | 33.0325
2018-05-02 13:00 | 0 | 0 | 87.2541 | 33.1566
2018-05-02 14:00 | 0 | 0 | 87.4037 | 33.2134
2018-05-02 15:00 | 0 | 0 | 87.2129 | 33.1409
2018-05-02 16:00 | 0 | 0 | 86.9718 | 33.0493
2018-05-02 17:00 | 0 | 0 | 87.1397 | 33.1131
2018-05-02 18:00 | 0 | 0 | 87.2435 | 33.1525
2018-05-02 19:00 | 0 | 0 | 86.8894 | 33.018
2018-05-02 20:00 | 0 | 0 | 87.1839 | 33.1299
2018-05-02 21:00 | 0 | 0 | 87.2419 | 33.1519
2018-05-02 22:00 | 0 | 0 | 87.1733 | 33.1259
2018-05-02 23:00 | 0 | 0 | 87.2557 | 33.1572
2018-05-03 | 86.5492 | 0 | 0 | 0
2018-05-03 01:00 | 86.7201 | 0 | 0 | 0
2018-05-03 02:00 | 86.5095 | 0 | 0 | 0
2018-05-03 03:00 | 86.4576 | 0 | 0 | 0
2018-05-03 04:00 | 86.6316 | 0 | 0 | 0
2018-05-03 05:00 | 86.569 | 0 | 0 | 0
2018-05-03 06:00 | 86.6468 | 0 | 0 | 0
2018-05-03 07:00 | 86.6361 | 0 | 0 | 0
2018-05-03 08:00 | 86.6819 | 0 | 0 | 0
2018-05-03 09:00 | 86.7094 | 0 | 0 | 0
2018-05-03 10:00 | 86.7933 | 0 | 0 | 0
2018-05-03 11:00 | 86.8009 | 0 | 0 | 0
2018-05-03 12:00 | 86.6728 | 0 | 0 | 0
2018-05-03 13:00 | 86.6316 | 0 | 0 | 0
2018-05-03 14:00 | 86.6316 | 0 | 0 | 0
2018-05-03 15:00 | 86.6636 | 0 | 0 | 0
2018-05-03 16:00 | 86.5568 | 0 | 0 | 0
2018-05-03 17:00 | 86.6865 | 0 | 0 | 0
2018-05-03 18:00 | 86.7262 | 0 | 0 | 0
2018-05-03 19:00 | 86.5187 | 0 | 0 | 0
2018-05-03 20:00 | 86.5766 | 0 | 0 | 0
2018-05-03 21:00 | 86.6194 | 0 | 0 | 0
2018-05-03 22:00 | 86.6743 | 0 | 0 | 0
2018-05-03 23:00 | 86.5644 | 0 | 0 | 0
2018-05-04 | 86.2226 | 86.688 | 0 | 32.9414
2018-05-04 01:00 | 86.1128 | 86.5232 | 0 | 32.8788
2018-05-04 02:00 | 86.2791 | 86.6896 | 0 | 32.942
2018-05-04 03:00 | 86.0014 | 86.4485 | 0 | 32.8504
2018-05-04 04:00 | 86.0533 | 86.4347 | 0 | 32.8452
2018-05-04 05:00 | 86.2257 | 86.6117 | 0 | 32.9124
2018-05-04 06:00 | 86.4332 | 86.9352 | 0 | 33.0354
2018-05-04 07:00 | 86.5873 | 87.0619 | 0 | 33.0835
2018-05-04 08:00 | 86.3691 | 86.7811 | 0 | 32.9768
2018-05-04 09:00 | 86.334 | 86.7399 | 0 | 32.9612
2018-05-04 10:00 | 86.5126 | 86.862 | 0 | 33.0076
2018-05-04 11:00 | 86.5003 | 86.9306 | 0 | 33.0336
2018-05-04 12:00 | 86.7002 | 87.1412 | 0 | 33.1137
2018-05-04 13:00 | 86.363 | 86.8009 | 0 | 32.9843
2018-05-04 14:00 | 86.4408 | 86.8635 | 0 | 33.0081
2018-05-04 15:00 | 86.2943 | 86.6743 | 0 | 32.9362
2018-05-04 16:00 | 86.3706 | 86.7491 | 0 | 32.9647
2018-05-04 17:00 | 86.2882 | 86.7445 | 0 | 32.9629
2018-05-04 18:00 | 86.1875 | 86.6667 | 0 | 32.9333
2018-05-04 19:00 | 86.099 | 86.5431 | 0 | 32.8864
2018-05-04 20:00 | 86.1997 | 86.5187 | 0 | 32.8771
2018-05-04 21:00 | 86.3767 | 86.7247 | 0 | 32.9554
2018-05-04 22:00 | 86.3691 | 86.7659 | 0 | 32.971
2018-05-04 23:00 | 86.4012 | 86.7918 | 0 | 32.9809
2018-05-05 | 86.0121 | 0 | 86.5507 | 32.8893
2018-05-05 01:00 | 85.919 | 0 | 86.5324 | 32.8823
2018-05-05 02:00 | 86.0533 | 0 | 86.6453 | 32.9252
2018-05-05 03:00 | 86.1677 | 0 | 86.7002 | 32.9461
2018-05-05 04:00 | 86.3081 | 0 | 86.8513 | 33.0035
2018-05-05 05:00 | 86.2562 | 0 | 86.8605 | 33.007
2018-05-05 06:00 | 86.1234 | 0 | 86.6682 | 32.9339
2018-05-05 07:00 | 86.1906 | 0 | 86.7247 | 32.9554
2018-05-05 08:00 | 86.36 | 0 | 86.952 | 33.0418
2018-05-05 09:00 | 86.4912 | 0 | 87.0588 | 33.0823
2018-05-05 10:00 | 86.1982 | 0 | 86.6392 | 32.9229
2018-05-05 11:00 | 86.1707 | 0 | 86.8849 | 33.0163
2018-05-05 12:00 | 86.5019 | 0 | 87.1504 | 33.1172
2018-05-05 13:00 | 86.6148 | 0 | 87.3167 | 33.1803
2018-05-05 14:00 | 86.4439 | 0 | 87.0832 | 33.0916
2018-05-05 15:00 | 86.5522 | 0 | 87.2938 | 33.1716
2018-05-05 16:00 | 86.5644 | 0 | 87.3579 | 33.196
2018-05-05 17:00 | 86.7445 | 0 | 87.57 | 33.2766
2018-05-05 18:00 | 86.4668 | 0 | 87.3014 | 33.1745
2018-05-05 19:00 | 86.3661 | 0 | 87.0954 | 33.0963
2018-05-05 20:00 | 86.1173 | 0 | 86.891 | 33.0186
2018-05-05 21:00 | 86.1555 | 0 | 86.9245 | 33.0313
2018-05-05 22:00 | 86.2211 | 0 | 87.0054 | 33.0621
2018-05-05 23:00 | 86.2226 | 0 | 87.0787 | 33.0899
2018-05-06 | 86.2364 | 86.7994 | 0 | 32.9838
2018-05-06 01:00 | 86.3188 | 86.952 | 0 | 33.0418
2018-05-06 02:00 | 86.2119 | 86.8177 | 0 | 32.9907
2018-05-06 03:00 | 86.1845 | 86.7857 | 0 | 32.9786
2018-05-06 04:00 | 86.2455 | 86.833 | 0 | 32.9965
2018-05-06 05:00 | 86.2333 | 86.833 | 0 | 32.9965
2018-05-06 06:00 | 86.2776 | 86.8528 | 0 | 33.0041
2018-05-06 07:00 | 86.2867 | 86.8452 | 0 | 33.0012
2018-05-06 08:00 | 86.2989 | 86.9032 | 0 | 33.0232
2018-05-06 09:00 | 86.2867 | 86.8162 | 0 | 32.9902
2018-05-06 10:00 | 86.2882 | 86.8528 | 0 | 33.0041
2018-05-06 11:00 | 86.1845 | 86.743 | 0 | 32.9623
2018-05-06 12:00 | 86.1418 | 86.714 | 0 | 32.9513
2018-05-06 13:00 | 86.1479 | 86.7659 | 0 | 32.971
2018-05-06 14:00 | 86.1112 | 86.7018 | 0 | 32.9467
2018-05-06 15:00 | 86.2455 | 86.8482 | 0 | 33.0023
2018-05-06 16:00 | 86.3447 | 86.9398 | 0 | 33.0371
2018-05-06 17:00 | 86.4805 | 86.9856 | 0 | 33.0545
2018-05-06 18:00 | 86.4332 | 86.92 | 0 | 33.0296
2018-05-06 19:00 | 85.6794 | 85.9266 | 0 | 32.6521
2018-05-06 20:00 | 86.3294 | 86.5888 | 0 | 32.9037
2018-05-06 21:00 | 86.3569 | 86.6728 | 0 | 32.9357
2018-05-06 22:00 | 86.4881 | 86.8086 | 0 | 32.9873
2018-05-06 23:00 | 86.4332 | 86.7353 | 0 | 32.9594
2018-05-07 | 86.4088 | 86.7002 | 86.9352 | 65.9815
2018-05-07 01:00 | 86.0426 | 86.3127 | 86.5278 | 65.6794
2018-05-07 02:00 | 86.392 | 86.6392 | 86.8421 | 65.9229
2018-05-07 03:00 | 86.2776 | 86.5766 | 86.7536 | 65.8655
2018-05-07 04:00 | 86.5034 | 86.8849 | 87.0283 | 66.087
2018-05-07 05:00 | 86.3661 | 86.772 | 87.0054 | 66.0354
2018-05-07 06:00 | 86.2898 | 86.6499 | 86.8147 | 65.9165
2018-05-07 07:00 | 86.2043 | 86.5278 | 86.7079 | 65.8296
2018-05-07 08:00 | 86.3355 | 86.5461 | 86.8025 | 65.8725
2018-05-07 09:00 | 86.3798 | 86.7262 | 86.8711 | 65.967
2018-05-07 10:00 | 86.2272 | 86.5156 | 86.714 | 65.8272
2018-05-07 11:00 | 86.2119 | 86.5141 | 86.7201 | 65.829
2018-05-07 12:00 | 86.389 | 86.6835 | 86.8574 | 65.9455
2018-05-07 13:00 | 86.4027 | 86.6224 | 86.7475 | 65.8806
2018-05-07 14:00 | 86.3783 | 86.6606 | 86.7903 | 65.9113
2018-05-07 15:00 | 86.3355 | 86.5248 | 86.7384 | 65.84
2018-05-07 16:00 | 86.3493 | 86.4912 | 86.685 | 65.807
2018-05-07 17:00 | 86.244 | 86.4683 | 86.6743 | 65.7942
2018-05-07 18:00 | 86.3142 | 86.4378 | 86.5934 | 65.7519
2018-05-07 19:00 | 86.2089 | 86.3508 | 86.5583 | 65.7055
2018-05-07 20:00 | 86.2181 | 86.4836 | 86.6896 | 65.8058
2018-05-07 21:00 | 86.1494 | 86.4759 | 86.63 | 65.7802
2018-05-07 22:00 | 86.2593 | 86.5522 | 86.6468 | 65.8156
2018-05-07 23:00 | 86.4424 | 86.8055 | 86.8864 | 66.0029
2018-05-08 | 86.4637 | 0 | 0 | 0
2018-05-08 01:00 | 86.5629 | 0 | 0 | 0
2018-05-08 02:00 | 86.3706 | 0 | 0 | 0
2018-05-08 03:00 | 86.3523 | 0 | 0 | 0
2018-05-08 04:00 | 86.3676 | 0 | 0 | 0
2018-05-08 05:00 | 86.4027 | 0 | 0 | 0
2018-05-08 06:00 | 86.4652 | 0 | 0 | 0
2018-05-08 07:00 | 86.4012 | 0 | 0 | 0
2018-05-08 08:00 | 86.4515 | 0 | 0 | 0
2018-05-08 09:00 | 86.2028 | 0 | 0 | 0
2018-05-08 10:00 | 86.2715 | 0 | 0 | 0
2018-05-08 11:00 | 86.7567 | 0 | 0 | 0
2018-05-08 12:00 | 86.6194 | 0 | 0 | 0
2018-05-08 13:00 | 86.6377 | 0 | 0 | 0
2018-05-08 14:00 | 86.8757 | 0 | 0 | 0
2018-05-08 15:00 | 86.7994 | 0 | 0 | 0
2018-05-08 16:00 | 86.7674 | 0 | 0 | 0
2018-05-08 17:00 | 86.7384 | 0 | 0 | 0
2018-05-08 18:00 | 86.7124 | 0 | 0 | 0
2018-05-08 19:00 | 86.8376 | 0 | 0 | 0
2018-05-08 20:00 | 86.627 | 0 | 0 | 0
2018-05-08 21:00 | 86.6239 | 0 | 0 | 0
2018-05-08 22:00 | 86.714 | 0 | 0 | 0
2018-05-08 23:00 | 86.8971 | 0 | 0 | 0
2018-05-09 | 0 | 0 | 86.6712 | 32.9351
2018-05-09 01:00 | 0 | 0 | 86.511 | 32.8742
2018-05-09 02:00 | 0 | 0 | 86.7628 | 32.9699
2018-05-09 03:00 | 0 | 0 | 86.7384 | 32.9606
2018-05-09 04:00 | 0 | 0 | 86.8376 | 32.9983
2018-05-09 05:00 | 0 | 0 | 87.0222 | 33.0684
2018-05-09 06:00 | 0 | 0 | 86.9627 | 33.0458
2018-05-09 07:00 | 0 | 0 | 87.1321 | 33.1102
2018-05-09 08:00 | 0 | 0 | 87.1931 | 33.1334
2018-05-09 09:00 | 0 | 0 | 86.7155 | 32.9519
2018-05-09 10:00 | 0 | 0 | 86.6743 | 32.9362
2018-05-09 11:00 | 0 | 0 | 86.8956 | 33.0203
2018-05-09 12:00 | 0 | 0 | 86.9276 | 33.0325
2018-05-09 13:00 | 0 | 0 | 87.2541 | 33.1566
2018-05-09 14:00 | 0 | 0 | 87.4037 | 33.2134
2018-05-09 15:00 | 0 | 0 | 87.2129 | 33.1409
2018-05-09 16:00 | 0 | 0 | 86.9718 | 33.0493
2018-05-09 17:00 | 0 | 0 | 87.1397 | 33.1131
2018-05-09 18:00 | 0 | 0 | 87.2435 | 33.1525
2018-05-09 19:00 | 0 | 0 | 86.8894 | 33.018
2018-05-09 20:00 | 0 | 0 | 87.1839 | 33.1299
2018-05-09 21:00 | 0 | 0 | 87.2419 | 33.1519
2018-05-09 22:00 | 0 | 0 | 87.1733 | 33.1259
2018-05-09 23:00 | 0 | 0 | 87.2557 | 33.1572
2018-05-10 | 86.5492 | 0 | 0 | 0
2018-05-10 01:00 | 86.7201 | 0 | 0 | 0
2018-05-10 02:00 | 86.5095 | 0 | 0 | 0
2018-05-10 03:00 | 86.4576 | 0 | 0 | 0
2018-05-10 04:00 | 86.6316 | 0 | 0 | 0
2018-05-10 05:00 | 86.569 | 0 | 0 | 0
2018-05-10 06:00 | 86.6468 | 0 | 0 | 0
2018-05-10 07:00 | 86.6361 | 0 | 0 | 0
2018-05-10 08:00 | 86.6819 | 0 | 0 | 0
2018-05-10 09:00 | 86.7094 | 0 | 0 | 0
2018-05-10 10:00 | 86.7933 | 0 | 0 | 0
2018-05-10 11:00 | 86.8009 | 0 | 0 | 0
2018-05-10 12:00 | 86.6728 | 0 | 0 | 0
2018-05-10 13:00 | 86.6316 | 0 | 0 | 0
2018-05-10 14:00 | 86.6316 | 0 | 0 | 0
2018-05-10 15:00 | 86.6636 | 0 | 0 | 0
2018-05-10 16:00 | 86.5568 | 0 | 0 | 0
2018-05-10 17:00 | 86.6865 | 0 | 0 | 0
2018-05-10 18:00 | 86.7262 | 0 | 0 | 0
2018-05-10 19:00 | 86.5187 | 0 | 0 | 0
2018-05-10 20:00 | 86.5766 | 0 | 0 | 0
2018-05-10 21:00 | 86.6194 | 0 | 0 | 0
2018-05-10 22:00 | 86.6743 | 0 | 0 | 0
2018-05-10 23:00 | 86.5644 | 0 | 0 | 0
2018-05-11 | 86.2226 | 86.688 | 0 | 32.9414
2018-05-11 01:00 | 86.1128 | 86.5232 | 0 | 32.8788
2018-05-11 02:00 | 86.2791 | 86.6896 | 0 | 32.942
2018-05-11 03:00 | 86.0014 | 86.4485 | 0 | 32.8504
2018-05-11 04:00 | 86.0533 | 86.4347 | 0 | 32.8452
2018-05-11 05:00 | 86.2257 | 86.6117 | 0 | 32.9124
2018-05-11 06:00 | 86.4332 | 86.9352 | 0 | 33.0354
2018-05-11 07:00 | 86.5873 | 87.0619 | 0 | 33.0835
2018-05-11 08:00 | 86.3691 | 86.7811 | 0 | 32.9768
2018-05-11 09:00 | 86.334 | 86.7399 | 0 | 32.9612
2018-05-11 10:00 | 86.5126 | 86.862 | 0 | 33.0076
2018-05-11 11:00 | 86.5003 | 86.9306 | 0 | 33.0336
2018-05-11 12:00 | 86.7002 | 87.1412 | 0 | 33.1137
2018-05-11 13:00 | 86.363 | 86.8009 | 0 | 32.9843
2018-05-11 14:00 | 86.4408 | 86.8635 | 0 | 33.0081
2018-05-11 15:00 | 86.2943 | 86.6743 | 0 | 32.9362
2018-05-11 16:00 | 86.3706 | 86.7491 | 0 | 32.9647
2018-05-11 17:00 | 86.2882 | 86.7445 | 0 | 32.9629
2018-05-11 18:00 | 86.1875 | 86.6667 | 0 | 32.9333
2018-05-11 19:00 | 86.099 | 86.5431 | 0 | 32.8864
2018-05-11 20:00 | 86.1997 | 86.5187 | 0 | 32.8771
2018-05-11 21:00 | 86.3767 | 86.7247 | 0 | 32.9554
2018-05-11 22:00 | 86.3691 | 86.7659 | 0 | 32.971
2018-05-11 23:00 | 86.4012 | 86.7918 | 0 | 32.9809
2018-05-12 | 86.0121 | 0 | 86.5507 | 32.8893
2018-05-12 01:00 | 85.919 | 0 | 86.5324 | 32.8823
2018-05-12 02:00 | 86.0533 | 0 | 86.6453 | 32.9252
2018-05-12 03:00 | 86.1677 | 0 | 86.7002 | 32.9461
2018-05-12 04:00 | 86.3081 | 0 | 86.8513 | 33.0035
2018-05-12 05:00 | 86.2562 | 0 | 86.8605 | 33.007
2018-05-12 06:00 | 86.1234 | 0 | 86.6682 | 32.9339
2018-05-12 07:00 | 86.1906 | 0 | 86.7247 | 32.9554
2018-05-12 08:00 | 86.36 | 0 | 86.952 | 33.0418
2018-05-12 09:00 | 86.4912 | 0 | 87.0588 | 33.0823
2018-05-12 10:00 | 86.1982 | 0 | 86.6392 | 32.9229
2018-05-12 11:00 | 86.1707 | 0 | 86.8849 | 33.0163
2018-05-12 12:00 | 86.5019 | 0 | 87.1504 | 33.1172
2018-05-12 13:00 | 86.6148 | 0 | 87.3167 | 33.1803
2018-05-12 14:00 | 86.4439 | 0 | 87.0832 | 33.0916
2018-05-12 15:00 | 86.5522 | 0 | 87.2938 | 33.1716
2018-05-12 16:00 | 86.5644 | 0 | 87.3579 | 33.196
2018-05-12 17:00 | 86.7445 | 0 | 87.57 | 33.2766
2018-05-12 18:00 | 86.4668 | 0 | 87.3014 | 33.1745
2018-05-12 19:00 | 86.3661 | 0 | 87.0954 | 33.0963
2018-05-12 20:00 | 86.1173 | 0 | 86.891 | 33.0186
2018-05-12 21:00 | 86.1555 | 0 | 86.9245 | 33.0313
2018-05-12 22:00 | 86.2211 | 0 | 87.0054 | 33.0621
2018-05-12 23:00 | 86.2226 | 0 | 87.0787 | 33.0899
2018-05-13 | 86.2364 | 86.7994 | 0 | 32.9838
2018-05-13 01:00 | 86.3188 | 86.952 | 0 | 33.0418
2018-05-13 02:00 | 86.2119 | 86.8177 | 0 | 32.9907
2018-05-13 03:00 | 86.1845 | 86.7857 | 0 | 32.9786
2018-05-13 04:00 | 86.2455 | 86.833 | 0 | 32.9965
2018-05-13 05:00 | 86.2333 | 86.833 | 0 | 32.9965
2018-05-13 06:00 | 86.2776 | 86.8528 | 0 | 33.0041
2018-05-13 07:00 | 86.2867 | 86.8452 | 0 | 33.0012
2018-05-13 08:00 | 86.2989 | 86.9032 | 0 | 33.0232
2018-05-13 09:00 | 86.2867 | 86.8162 | 0 | 32.9902
2018-05-13 10:00 | 86.2882 | 86.8528 | 0 | 33.0041
2018-05-13 11:00 | 86.1845 | 86.743 | 0 | 32.9623
2018-05-13 12:00 | 86.1418 | 86.714 | 0 | 32.9513
2018-05-13 13:00 | 86.1479 | 86.7659 | 0 | 32.971
2018-05-13 14:00 | 86.1112 | 86.7018 | 0 | 32.9467
2018-05-13 15:00 | 86.2455 | 86.8482 | 0 | 33.0023
2018-05-13 16:00 | 86.3447 | 86.9398 | 0 | 33.0371
2018-05-13 17:00 | 86.4805 | 86.9856 | 0 | 33.0545
2018-05-13 18:00 | 86.4332 | 86.92 | 0 | 33.0296
2018-05-13 19:00 | 85.6794 | 85.9266 | 0 | 32.6521
2018-05-13 20:00 | 86.3294 | 86.5888 | 0 | 32.9037
2018-05-13 21:00 | 86.3569 | 86.6728 | 0 | 32.9357
2018-05-13 22:00 | 86.4881 | 86.8086 | 0 | 32.9873
2018-05-13 23:00 | 86.4332 | 86.7353 | 0 | 32.9594
2018-05-14 | 86.4088 | 86.7002 | 86.9352 | 65.9815
2018-05-14 01:00 | 86.0426 | 86.3127 | 86.5278 | 65.6794
2018-05-14 02:00 | 86.392 | 86.6392 | 86.8421 | 65.9229
2018-05-14 03:00 | 86.2776 | 86.5766 | 86.7536 | 65.8655
2018-05-14 04:00 | 86.5034 | 86.8849 | 87.0283 | 66.087
2018-05-14 05:00 | 86.3661 | 86.772 | 87.0054 | 66.0354
2018-05-14 06:00 | 86.2898 | 86.6499 | 86.8147 | 65.9165
2018-05-14 07:00 | 86.2043 | 86.5278 | 86.7079 | 65.8296
2018-05-14 08:00 | 86.3355 | 86.5461 | 86.8025 | 65.8725
2018-05-14 09:00 | 86.3798 | 86.7262 | 86.8711 | 65.967
2018-05-14 10:00 | 86.2272 | 86.5156 | 86.714 | 65.8272
2018-05-14 11:00 | 86.2119 | 86.5141 | 86.7201 | 65.829
2018-05-14 12:00 | 86.389 | 86.6835 | 86.8574 | 65.9455
2018-05-14 13:00 | 86.4027 | 86.6224 | 86.7475 | 65.8806
2018-05-14 14:00 | 86.3783 | 86.6606 | 86.7903 | 65.9113
2018-05-14 15:00 | 86.3355 | 86.5248 | 86.7384 | 65.84
2018-05-14 16:00 | 86.3493 | 86.4912 | 86.685 | 65.807
2018-05-14 17:00 | 86.244 | 86.4683 | 86.6743 | 65.7942
2018-05-14 18:00 | 86.3142 | 86.4378 | 86.5934 | 65.7519
2018-05-14 19:00 | 86.2089 | 86.3508 | 86.5583 | 65.7055
2018-05-14 20:00 | 86.2181 | 86.4836 | 86.6896 | 65.8058
2018-05-14 21:00 | 86.1494 | 86.4759 | 86.63 | 65.7802
2018-05-14 22:00 | 86.2593 | 86.5522 | 86.6468 | 65.8156
2018-05-14 23:00 | 86.4424 | 86.8055 | 86.8864 | 66.0029
2018-05-15 | 86.4637 | 0 | 0 | 0
2018-05-15 01:00 | 86.5629 | 0 | 0 | 0
2018-05-15 02:00 | 86.3706 | 0 | 0 | 0
2018-05-15 03:00 | 86.3523 | 0 | 0 | 0
2018-05-15 04:00 | 86.3676 | 0 | 0 | 0
2018-05-15 05:00 | 86.4027 | 0 | 0 | 0
2018-05-15 06:00 | 86.4652 | 0 | 0 | 0
2018-05-15 07:00 | 86.4012 | 0 | 0 | 0
2018-05-15 08:00 | 86.4515 | 0 | 0 | 0
2018-05-15 09:00 | 86.2028 | 0 | 0 | 0
2018-05-15 10:00 | 86.2715 | 0 | 0 | 0
2018-05-15 11:00 | 86.7567 | 0 | 0 | 0
2018-05-15 12:00 | 86.6194 | 0 | 0 | 0
2018-05-15 13:00 | 86.6377 | 0 | 0 | 0
2018-05-15 14:00 | 86.8757 | 0 | 0 | 0
2018-05-15 15:00 | 86.7994 | 0 | 0 | 0
2018-05-15 16:00 | 86.7674 | 0 | 0 | 0
2018-05-15 17:00 | 86.7384 | 0 | 0 | 0
2018-05-15 18:00 | 86.7124 | 0 | 0 | 0
2018-05-15 19:00 | 86.8376 | 0 | 0 | 0
2018-05-15 20:00 | 86.627 | 0 | 0 | 0
2018-05-15 21:00 | 86.6239 | 0 | 0 | 0
2018-05-15 22:00 | 86.714 | 0 | 0 | 0
2018-05-15 23:00 | 86.8971 | 0 | 0 | 0
2018-05-16 | 0 | 0 | 86.6712 | 32.9351
2018-05-16 01:00 | 0 | 0 | 86.511 | 32.8742
2018-05-16 02:00 | 0 | 0 | 86.7628 | 32.9699
2018-05-16 03:00 | 0 | 0 | 86.7384 | 32.9606
2018-05-16 04:00 | 0 | 0 | 86.8376 | 32.9983
2018-05-16 05:00 | 0 | 0 | 87.0222 | 33.0684
2018-05-16 06:00 | 0 | 0 | 86.9627 | 33.0458
2018-05-16 07:00 | 0 | 0 | 87.1321 | 33.1102
2018-05-16 08:00 | 0 | 0 | 87.1931 | 33.1334
2018-05-16 09:00 | 0 | 0 | 86.7155 | 32.9519
2018-05-16 10:00 | 0 | 0 | 86.6743 | 32.9362
2018-05-16 11:00 | 0 | 0 | 86.8956 | 33.0203
2018-05-16 12:00 | 0 | 0 | 86.9276 | 33.0325
2018-05-16 13:00 | 0 | 0 | 87.2541 | 33.1566
2018-05-16 14:00 | 0 | 0 | 87.4037 | 33.2134
2018-05-16 15:00 | 0 | 0 | 87.2129 | 33.1409
2018-05-16 16:00 | 0 | 0 | 86.9718 | 33.0493
2018-05-16 17:00 | 0 | 0 | 87.1397 | 33.1131
2018-05-16 18:00 | 0 | 0 | 87.2435 | 33.1525
2018-05-16 19:00 | 0 | 0 | 86.8894 | 33.018
2018-05-16 20:00 | 0 | 0 | 87.1839 | 33.1299
2018-05-16 21:00 | 0 | 0 | 87.2419 | 33.1519
2018-05-16 22:00 | 0 | 0 | 87.1733 | 33.1259
2018-05-16 23:00 | 0 | 0 | 87.2557 | 33.1572
2018-05-17 | 86.5492 | 0 | 0 | 0
2018-05-17 01:00 | 86.7201 | 0 | 0 | 0
2018-05-17 02:00 | 86.5095 | 0 | 0 | 0
2018-05-17 03:00 | 86.4576 | 0 | 0 | 0
2018-05-17 04:00 | 86.6316 | 0 | 0 | 0
2018-05-17 05:00 | 86.569 | 0 | 0 | 0
2018-05-17 06:00 | 86.6468 | 0 | 0 | 0
2018-05-17 07:00 | 86.6361 | 0 | 0 | 0
2018-05-17 08:00 | 86.6819 | 0 | 0 | 0
2018-05-17 09:00 | 86.7094 | 0 | 0 | 0
2018-05-17 10:00 | 86.7933 | 0 | 0 | 0
2018-05-17 11:00 | 86.8009 | 0 | 0 | 0
2018-05-17 12:00 | 86.6728 | 0 | 0 | 0
2018-05-17 13:00 | 86.6316 | 0 | 0 | 0
2018-05-17 14:00 | 86.6316 | 0 | 0 | 0
2018-05-17 15:00 | 86.6636 | 0 | 0 | 0
2018-05-17 16:00 | 86.5568 | 0 | 0 | 0
2018-05-17 17:00 | 86.6865 | 0 | 0 | 0
2018-05-17 18:00 | 86.7262 | 0 | 0 | 0
2018-05-17 19:00 | 86.5187 | 0 | 0 | 0
2018-05-17 20:00 | 86.5766 | 0 | 0 | 0
2018-05-17 21:00 | 86.6194 | 0 | 0 | 0
2018-05-17 22:00 | 86.6743 | 0 | 0 | 0
2018-05-17 23:00 | 86.5644 | 0 | 0 | 0
2018-05-18 | 86.2226 | 86.688 | 0 | 32.9414
2018-05-18 01:00 | 86.1128 | 86.5232 | 0 | 32.8788
2018-05-18 02:00 | 86.2791 | 86.6896 | 0 | 32.942
2018-05-18 03:00 | 86.0014 | 86.4485 | 0 | 32.8504
2018-05-18 04:00 | 86.0533 | 86.4347 | 0 | 32.8452
2018-05-18 05:00 | 86.2257 | 86.6117 | 0 | 32.9124
2018-05-18 06:00 | 86.4332 | 86.9352 | 0 | 33.0354
2018-05-18 07:00 | 86.5873 | 87.0619 | 0 | 33.0835
2018-05-18 08:00 | 86.3691 | 86.7811 | 0 | 32.9768
2018-05-18 09:00 | 86.334 | 86.7399 | 0 | 32.9612
2018-05-18 10:00 | 86.5126 | 86.862 | 0 | 33.0076
2018-05-18 11:00 | 86.5003 | 86.9306 | 0 | 33.0336
2018-05-18 12:00 | 86.7002 | 87.1412 | 0 | 33.1137
2018-05-18 13:00 | 86.363 | 86.8009 | 0 | 32.9843
2018-05-18 14:00 | 86.4408 | 86.8635 | 0 | 33.0081
2018-05-18 15:00 | 86.2943 | 86.6743 | 0 | 32.9362
2018-05-18 16:00 | 86.3706 | 86.7491 | 0 | 32.9647
2018-05-18 17:00 | 86.2882 | 86.7445 | 0 | 32.9629
2018-05-18 18:00 | 86.1875 | 86.6667 | 0 | 32.9333
2018-05-18 19:00 | 86.099 | 86.5431 | 0 | 32.8864
2018-05-18 20:00 | 86.1997 | 86.5187 | 0 | 32.8771
2018-05-18 21:00 | 86.3767 | 86.7247 | 0 | 32.9554
2018-05-18 22:00 | 86.3691 | 86.7659 | 0 | 32.971
2018-05-18 23:00 | 86.4012 | 86.7918 | 0 | 32.9809
2018-05-19 | 86.0121 | 0 | 86.5507 | 32.8893
2018-05-19 01:00 | 85.919 | 0 | 86.5324 | 32.8823
2018-05-19 02:00 | 86.0533 | 0 | 86.6453 | 32.9252
2018-05-19 03:00 | 86.1677 | 0 | 86.7002 | 32.9461
2018-05-19 04:00 | 86.3081 | 0 | 86.8513 | 33.0035
2018-05-19 05:00 | 86.2562 | 0 | 86.8605 | 33.007
2018-05-19 06:00 | 86.1234 | 0 | 86.6682 | 32.9339
2018-05-19 07:00 | 86.1906 | 0 | 86.7247 | 32.9554
2018-05-19 08:00 | 86.36 | 0 | 86.952 | 33.0418
2018-05-19 09:00 | 86.4912 | 0 | 87.0588 | 33.0823
2018-05-19 10:00 | 86.1982 | 0 | 86.6392 | 32.9229
2018-05-19 11:00 | 86.1707 | 0 | 86.8849 | 33.0163
2018-05-19 12:00 | 86.5019 | 0 | 87.1504 | 33.1172
2018-05-19 13:00 | 86.6148 | 0 | 87.3167 | 33.1803
2018-05-19 14:00 | 86.4439 | 0 | 87.0832 | 33.0916
2018-05-19 15:00 | 86.5522 | 0 | 87.2938 | 33.1716
2018-05-19 16:00 | 86.5644 | 0 | 87.3579 | 33.196
2018-05-19 17:00 | 86.7445 | 0 | 87.57 | 33.2766
2018-05-19 18:00 | 86.4668 | 0 | 87.3014 | 33.1745
2018-05-19 19:00 | 86.3661 | 0 | 87.0954 | 33.0963
2018-05-19 20:00 | 86.1173 | 0 | 86.891 | 33.0186
2018-05-19 21:00 | 86.1555 | 0 | 86.9245 | 33.0313
2018-05-19 22:00 | 86.2211 | 0 | 87.0054 | 33.0621
2018-05-19 23:00 | 86.2226 | 0 | 87.0787 | 33.0899
2018-05-20 | 86.2364 | 86.7994 | 0 | 32.9838
2018-05-20 01:00 | 86.3188 | 86.952 | 0 | 33.0418
2018-05-20 02:00 | 86.2119 | 86.8177 | 0 | 32.9907
2018-05-20 03:00 | 86.1845 | 86.7857 | 0 | 32.9786
2018-05-20 04:00 | 86.2455 | 86.833 | 0 | 32.9965
2018-05-20 05:00 | 86.2333 | 86.833 | 0 | 32.9965
2018-05-20 06:00 | 86.2776 | 86.8528 | 0 | 33.0041
2018-05-20 07:00 | 86.2867 | 86.8452 | 0 | 33.0012
2018-05-20 08:00 | 86.2989 | 86.9032 | 0 | 33.0232
2018-05-20 09:00 | 86.2867 | 86.8162 | 0 | 32.9902
2018-05-20 10:00 | 86.2882 | 86.8528 | 0 | 33.0041
2018-05-20 11:00 | 86.1845 | 86.743 | 0 | 32.9623
2018-05-20 12:00 | 86.1418 | 86.714 | 0 | 32.9513
2018-05-20 13:00 | 86.1479 | 86.7659 | 0 | 32.971
2018-05-20 14:00 | 86.1112 | 86.7018 | 0 | 32.9467
2018-05-20 15:00 | 86.2455 | 86.8482 | 0 | 33.0023
2018-05-20 16:00 | 86.3447 | 86.9398 | 0 | 33.0371
2018-05-20 17:00 | 86.4805 | 86.9856 | 0 | 33.0545
2018-05-20 18:00 | 86.4332 | 86.92 | 0 | 33.0296
2018-05-20 19:00 | 85.6794 | 85.9266 | 0 | 32.6521
2018-05-20 20:00 | 86.3294 | 86.5888 | 0 | 32.9037
2018-05-20 21:00 | 86.3569 | 86.6728 | 0 | 32.9357
2018-05-20 22:00 | 86.4881 | 86.8086 | 0 | 32.9873
2018-05-20 23:00 | 86.4332 | 86.7353 | 0 | 32.9594
2018-05-21 | 86.4088 | 86.7002 | 86.9352 | 65.9815
2018-05-21 01:00 | 86.0426 | 86.3127 | 86.5278 | 65.6794
2018-05-21 02:00 | 86.392 | 86.6392 | 86.8421 | 65.9229
2018-05-21 03:00 | 86.2776 | 86.5766 | 86.7536 | 65.8655
2018-05-21 04:00 | 86.5034 | 86.8849 | 87.0283 | 66.087
2018-05-21 05:00 | 86.3661 | 86.772 | 87.0054 | 66.0354
2018-05-21 06:00 | 86.2898 | 86.6499 | 86.8147 | 65.9165
2018-05-21 07:00 | 86.2043 | 86.5278 | 86.7079 | 65.8296
2018-05-21 08:00 | 86.3355 | 86.5461 | 86.8025 | 65.8725
2018-05-21 09:00 | 86.3798 | 86.7262 | 86.8711 | 65.967
2018-05-21 10:00 | 86.2272 | 86.5156 | 86.714 | 65.8272
2018-05-21 11:00 | 86.2119 | 86.5141 | 86.7201 | 65.829
2018-05-21 12:00 | 86.389 | 86.6835 | 86.8574 | 65.9455
2018-05-21 13:00 | 86.4027 | 86.6224 | 86.7475 | 65.8806
2018-05-21 14:00 | 86.3783 | 86.6606 | 86.7903 | 65.9113
2018-05-21 15:00 | 86.3355 | 86.5248 | 86.7384 | 65.84
2018-05-21 16:00 | 86.3493 | 86.4912 | 86.685 | 65.807
2018-05-21 17:00 | 86.244 | 86.4683 | 86.6743 | 65.7942
2018-05-21 18:00 | 86.3142 | 86.4378 | 86.5934 | 65.7519
2018-05-21 19:00 | 86.2089 | 86.3508 | 86.5583 | 65.7055
2018-05-21 20:00 | 86.2181 | 86.4836 | 86.6896 | 65.8058
2018-05-21 21:00 | 86.1494 | 86.4759 | 86.63 | 65.7802
2018-05-21 22:00 | 86.2593 | 86.5522 | 86.6468 | 65.8156
2018-05-21 23:00 | 86.4424 | 86.8055 | 86.8864 | 66.0029
2018-05-22 | 86.4637 | 0 | 0 | 0
2018-05-22 01:00 | 86.5629 | 0 | 0 | 0
2018-05-22 02:00 | 86.3706 | 0 | 0 | 0
2018-05-22 03:00 | 86.3523 | 0 | 0 | 0
2018-05-22 04:00 | 86.3676 | 0 | 0 | 0
2018-05-22 05:00 | 86.4027 | 0 | 0 | 0
2018-05-22 06:00 | 86.4652 | 0 | 0 | 0
2018-05-22 07:00 | 86.4012 | 0 | 0 | 0
2018-05-22 08:00 | 86.4515 | 0 | 0 | 0
2018-05-22 09:00 | 86.2028 | 0 | 0 | 0
2018-05-22 10:00 | 86.2715 | 0 | 0 | 0
2018-05-22 11:00 | 86.7567 | 0 | 0 | 0
2018-05-22 12:00 | 86.6194 | 0 | 0 | 0
2018-05-22 13:00 | 86.6377 | 0 | 0 | 0
2018-05-22 14:00 | 86.8757 | 0 | 0 | 0
2018-05-22 15:00 | 86.7994 | 0 | 0 | 0
2018-05-22 16:00 | 86.7674 | 0 | 0 | 0
2018-05-22 17:00 | 86.7384 | 0 | 0 | 0
2018-05-22 18:00 | 86.7124 | 0 | 0 | 0
2018-05-22 19:00 | 86.8376 | 0 | 0 | 0
2018-05-22 20:00 | 86.627 | 0 | 0 | 0
2018-05-22 21:00 | 86.6239 | 0 | 0 | 0
2018-05-22 22:00 | 86.714 | 0 | 0 | 0
2018-05-22 23:00 | 86.8971 | 0 | 0 | 0
2018-05-23 | 0 | 0 | 86.6712 | 32.9351
2018-05-23 01:00 | 0 | 0 | 86.511 | 32.8742
2018-05-23 02:00 | 0 | 0 | 86.7628 | 32.9699
2018-05-23 03:00 | 0 | 0 | 86.7384 | 32.9606
2018-05-23 04:00 | 0 | 0 | 86.8376 | 32.9983
2018-05-23 05:00 | 0 | 0 | 87.0222 | 33.0684
2018-05-23 06:00 | 0 | 0 | 86.9627 | 33.0458
2018-05-23 07:00 | 0 | 0 | 87.1321 | 33.1102
2018-05-23 08:00 | 0 | 0 | 87.1931 | 33.1334
2018-05-23 09:00 | 0 | 0 | 86.7155 | 32.9519
2018-05-23 10:00 | 0 | 0 | 86.6743 | 32.9362
2018-05-23 11:00 | 0 | 0 | 86.8956 | 33.0203
2018-05-23 12:00 | 0 | 0 | 86.9276 | 33.0325
2018-05-23 13:00 | 0 | 0 | 87.2541 | 33.1566
2018-05-23 14:00 | 0 | 0 | 87.4037 | 33.2134
2018-05-23 15:00 | 0 | 0 | 87.2129 | 33.1409
2018-05-23 16:00 | 0 | 0 | 86.9718 | 33.0493
2018-05-23 17:00 | 0 | 0 | 87.1397 | 33.1131
2018-05-23 18:00 | 0 | 0 | 87.2435 | 33.1525
2018-05-23 19:00 | 0 | 0 | 86.8894 | 33.018
2018-05-23 20:00 | 0 | 0 | 87.1839 | 33.1299
2018-05-23 21:00 | 0 | 0 | 87.2419 | 33.1519
2018-05-23 22:00 | 0 | 0 | 87.1733 | 33.1259
2018-05-23 23:00 | 0 | 0 | 87.2557 | 33.1572
2018-05-24 | 86.5492 | 0 | 0 | 0
2018-05-24 01:00 | 86.7201 | 0 | 0 | 0
2018-05-24 02:00 | 86.5095 | 0 | 0 | 0
2018-05-24 03:00 | 86.4576 | 0 | 0 | 0
2018-05-24 04:00 | 86.6316 | 0 | 0 | 0
2018-05-24 05:00 | 86.569 | 0 | 0 | 0
2018-05-24 06:00 | 86.6468 | 0 | 0 | 0
2018-05-24 07:00 | 86.6361 | 0 | 0 | 0
2018-05-24 08:00 | 86.6819 | 0 | 0 | 0
2018-05-24 09:00 | 86.7094 | 0 | 0 | 0
2018-05-24 10:00 | 86.7933 | 0 | 0 | 0
2018-05-24 11:00 | 86.8009 | 0 | 0 | 0

## Step 1.2 Fixture Inventory
Lamp Wattage (W) | Lamp Quantity | Ballast Wattage (W) | Ballast Quantity |  | Total Anticipated Load (kW)
100 | 2000 |  |  | 200 | 200 | If lighting panel is mixed, input existing lamp and ballast wattage and quantity
|  |  |  | 0 |  | If ballast wattage is unknown leave ballast wattage and quantity blank, only input lamp wattage and quantity
0
|  |  |  | 0 |  | The Total Anticipated Load will sum the wattage and quantity of up to 100 fixtures
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0

## Step 2. Power Calcs
Circuit #1 Datetime | Hour of Day | Day of Week | Circuit #1 AC Current (Amps) | Circuit #1 Power (kW) - Balanced Load | Circuit #2 Datetime | Hour of Day | Day of Week | Circuit #2 AC Current (Amps) | Circuit #2 Power (kW) - Balanced Load | Circuit #3 Datetime | Hour of Day | Day of Week | Circuit #3 AC Current (Amps) | Circuit #3 Power (kW) - Balanced Load | Circuit #4 Datetime | Hour of Day | Day of Week | Circuit #4 AC Current (Amps) | Circuit #4 Power (kW) - Balanced Load
2018-02-01 10:00 | 10 | 5 | 86.7201 | 18.2979 | 2018-02-01 10:00 | 10 | 5 | 86.7018 | 17.6612 | 2018-02-01 10:00 | 10 | 5 | 87.0329 | 18.451 | 2018-02-01 10:00 | 10 | 5 | 17.3735 | 3.6484
2018-02-01 11:00 | 11 | 5 | 86.6697 | 18.2873 | 2018-02-01 11:00 | 11 | 5 | 86.92 | 17.7056 | 2018-02-01 11:00 | 11 | 5 | 87.0665 | 18.4581 | 2018-02-01 11:00 | 11 | 5 | 66.1149 | 13.8841
2018-02-01 12:00 | 12 | 5 | 86.6209 | 18.277 | 2018-02-01 12:00 | 12 | 5 | 86.8498 | 17.6913 | 2018-02-01 12:00 | 12 | 5 | 87.0954 | 18.4642 | 2018-02-01 12:00 | 12 | 5 | 66.0992 | 13.8808
2018-02-01 13:00 | 13 | 5 | 86.5003 | 18.2516 | 2018-02-01 13:00 | 13 | 5 | 86.7323 | 17.6674 | 2018-02-01 13:00 | 13 | 5 | 87.0253 | 18.4494 | 2018-02-01 13:00 | 13 | 5 | 66.0279 | 13.8659
2018-02-01 14:00 | 14 | 5 | 86.54 | 18.2599 | 2018-02-01 14:00 | 14 | 5 | 86.6804 | 17.6568 | 2018-02-01 14:00 | 14 | 5 | 86.9703 | 18.4377 | 2018-02-01 14:00 | 14 | 5 | 65.9873 | 13.8573
2018-02-01 15:00 | 15 | 5 | 86.4958 | 18.2506 | 2018-02-01 15:00 | 15 | 5 | 86.7079 | 17.6624 | 2018-02-01 15:00 | 15 | 5 | 87.0542 | 18.4555 | 2018-02-01 15:00 | 15 | 5 | 66.0296 | 13.8662
2018-02-01 16:00 | 16 | 5 | 86.5171 | 18.2551 | 2018-02-01 16:00 | 16 | 5 | 86.7857 | 17.6782 | 2018-02-01 16:00 | 16 | 5 | 87.0405 | 18.4526 | 2018-02-01 16:00 | 16 | 5 | 66.054 | 13.8713
2018-02-01 17:00 | 17 | 5 | 86.3813 | 18.2265 | 2018-02-01 17:00 | 17 | 5 | 86.6392 | 17.6484 | 2018-02-01 17:00 | 17 | 5 | 87.0085 | 18.4458 | 2018-02-01 17:00 | 17 | 5 | 65.9861 | 13.8571
2018-02-01 18:00 | 18 | 5 | 86.537 | 18.2593 | 2018-02-01 18:00 | 18 | 5 | 86.6407 | 17.6487 | 2018-02-01 18:00 | 18 | 5 | 87.0695 | 18.4587 | 2018-02-01 18:00 | 18 | 5 | 66.0099 | 13.8621
2018-02-01 19:00 | 19 | 5 | 86.6224 | 18.2773 | 2018-02-01 19:00 | 19 | 5 | 86.8544 | 17.6922 | 2018-02-01 19:00 | 19 | 5 | 87.1382 | 18.4733 | 2018-02-01 19:00 | 19 | 5 | 66.1172 | 13.8846
2018-02-01 20:00 | 20 | 5 | 86.537 | 18.2593 | 2018-02-01 20:00 | 20 | 5 | 86.7628 | 17.6736 | 2018-02-01 20:00 | 20 | 5 | 87.1458 | 18.4749 | 2018-02-01 20:00 | 20 | 5 | 66.0853 | 13.8779
2018-02-01 21:00 | 21 | 5 | 86.5171 | 18.2551 | 2018-02-01 21:00 | 21 | 5 | 86.746 | 17.6702 | 2018-02-01 21:00 | 21 | 5 | 86.981 | 18.44 | 2018-02-01 21:00 | 21 | 5 | 66.0163 | 13.8634
2018-02-01 22:00 | 22 | 5 | 86.5278 | 18.2574 | 2018-02-01 22:00 | 22 | 5 | 86.7292 | 17.6667 | 2018-02-01 22:00 | 22 | 5 | 86.9444 | 18.4322 | 2018-02-01 22:00 | 22 | 5 | 65.996 | 13.8592
2018-02-01 23:00 | 23 | 5 | 86.5461 | 18.2612 | 2018-02-01 23:00 | 23 | 5 | 86.8818 | 17.6978 | 2018-02-01 23:00 | 23 | 5 | 87.1351 | 18.4726 | 2018-02-01 23:00 | 23 | 5 | 66.1264 | 13.8865
2018-02-02 | 0 | 6 | 0 | 0 | 2018-02-02 | 0 | 6 | 86.7842 | 17.6779 | 2018-02-02 | 0 | 6 | 87.1504 | 18.4759 | 2018-02-02 | 0 | 6 | 66.0951 | 13.88
2018-02-02 01:00 | 1 | 6 | 0 | 0 | 2018-02-02 01:00 | 1 | 6 | 86.8605 | 17.6935 | 2018-02-02 01:00 | 1 | 6 | 87.0115 | 18.4464 | 2018-02-02 01:00 | 1 | 6 | 66.0714 | 13.875
2018-02-02 02:00 | 2 | 6 | 0 | 0 | 2018-02-02 02:00 | 2 | 6 | 86.8482 | 17.691 | 2018-02-02 02:00 | 2 | 6 | 87.1885 | 18.484 | 2018-02-02 02:00 | 2 | 6 | 66.1339 | 13.8881
2018-02-02 03:00 | 3 | 6 | 0 | 0 | 2018-02-02 03:00 | 3 | 6 | 86.8681 | 17.695 | 2018-02-02 03:00 | 3 | 6 | 87.1641 | 18.4788 | 2018-02-02 03:00 | 3 | 6 | 66.1322 | 13.8878
2018-02-02 04:00 | 4 | 6 | 0 | 0 | 2018-02-02 04:00 | 4 | 6 | 86.7994 | 17.681 | 2018-02-02 04:00 | 4 | 6 | 87.1229 | 18.4701 | 2018-02-02 04:00 | 4 | 6 | 66.0905 | 13.879
2018-02-02 05:00 | 5 | 6 | 0 | 0 | 2018-02-02 05:00 | 5 | 6 | 86.8055 | 17.6823 | 2018-02-02 05:00 | 5 | 6 | 87.1916 | 18.4846 | 2018-02-02 05:00 | 5 | 6 | 66.1189 | 13.885
2018-02-02 06:00 | 6 | 6 | 0 | 0 | 2018-02-02 06:00 | 6 | 6 | 86.8086 | 17.6829 | 2018-02-02 06:00 | 6 | 6 | 87.1778 | 18.4817 | 2018-02-02 06:00 | 6 | 6 | 66.1148 | 13.8841
2018-02-02 07:00 | 7 | 6 | 0 | 0 | 2018-02-02 07:00 | 7 | 6 | 86.865 | 17.6944 | 2018-02-02 07:00 | 7 | 6 | 87.2572 | 18.4985 | 2018-02-02 07:00 | 7 | 6 | 66.1664 | 13.895
2018-02-02 08:00 | 8 | 6 | 0 | 0 | 2018-02-02 08:00 | 8 | 6 | 86.7994 | 17.681 | 2018-02-02 08:00 | 8 | 6 | 87.1473 | 18.4752 | 2018-02-02 08:00 | 8 | 6 | 66.0997 | 13.8809
2018-02-02 09:00 | 9 | 6 | 0 | 0 | 2018-02-02 09:00 | 9 | 6 | 86.8925 | 17.7 | 2018-02-02 09:00 | 9 | 6 | 87.1641 | 18.4788 | 2018-02-02 09:00 | 9 | 6 | 66.1415 | 13.8897
2018-02-02 10:00 | 10 | 6 | 0 | 0 | 2018-02-02 10:00 | 10 | 6 | 86.8956 | 17.7006 | 2018-02-02 10:00 | 10 | 6 | 87.2297 | 18.4927 | 2018-02-02 10:00 | 10 | 6 | 66.1676 | 13.8952
2018-02-02 11:00 | 11 | 6 | 0 | 0 | 2018-02-02 11:00 | 11 | 6 | 86.7704 | 17.6751 | 2018-02-02 11:00 | 11 | 6 | 87.1031 | 18.4659 | 2018-02-02 11:00 | 11 | 6 | 66.0719 | 13.8751
2018-02-02 12:00 | 12 | 6 | 0 | 0 | 2018-02-02 12:00 | 12 | 6 | 86.8101 | 17.6832 | 2018-02-02 12:00 | 12 | 6 | 87.0329 | 18.451 | 2018-02-02 12:00 | 12 | 6 | 66.0603 | 13.8727
2018-02-02 13:00 | 13 | 6 | 0 | 0 | 2018-02-02 13:00 | 13 | 6 | 86.8727 | 17.696 | 2018-02-02 13:00 | 13 | 6 | 87.1366 | 18.473 | 2018-02-02 13:00 | 13 | 6 | 66.1235 | 13.8859
2018-02-02 14:00 | 14 | 6 | 0 | 0 | 2018-02-02 14:00 | 14 | 6 | 86.7964 | 17.6804 | 2018-02-02 14:00 | 14 | 6 | 87.0344 | 18.4513 | 2018-02-02 14:00 | 14 | 6 | 66.0557 | 13.8717
2018-02-02 15:00 | 15 | 6 | 0 | 0 | 2018-02-02 15:00 | 15 | 6 | 86.6041 | 17.6413 | 2018-02-02 15:00 | 15 | 6 | 87.0344 | 18.4513 | 2018-02-02 15:00 | 15 | 6 | 65.9826 | 13.8564
2018-02-02 16:00 | 16 | 6 | 0 | 0 | 2018-02-02 16:00 | 16 | 6 | 86.8391 | 17.6891 | 2018-02-02 16:00 | 16 | 6 | 87.1321 | 18.472 | 2018-02-02 16:00 | 16 | 6 | 66.1091 | 13.8829
2018-02-02 17:00 | 17 | 6 | 0 | 0 | 2018-02-02 17:00 | 17 | 6 | 86.804 | 17.682 | 2018-02-02 17:00 | 17 | 6 | 86.9657 | 18.4367 | 2018-02-02 17:00 | 17 | 6 | 66.0325 | 13.8668
2018-02-02 18:00 | 18 | 6 | 0 | 0 | 2018-02-02 18:00 | 18 | 6 | 86.9017 | 17.7019 | 2018-02-02 18:00 | 18 | 6 | 87.187 | 18.4836 | 2018-02-02 18:00 | 18 | 6 | 66.1537 | 13.8923
2018-02-02 19:00 | 19 | 6 | 0 | 0 | 2018-02-02 19:00 | 19 | 6 | 86.4302 | 17.6058 | 2018-02-02 19:00 | 19 | 6 | 86.6423 | 18.3682 | 2018-02-02 19:00 | 19 | 6 | 65.7675 | 13.8112
2018-02-02 20:00 | 20 | 6 | 0 | 0 | 2018-02-02 20:00 | 20 | 6 | 86.6499 | 17.6506 | 2018-02-02 20:00 | 20 | 6 | 86.8513 | 18.4125 | 2018-02-02 20:00 | 20 | 6 | 65.9305 | 13.8454
2018-02-02 21:00 | 21 | 6 | 0 | 0 | 2018-02-02 21:00 | 21 | 6 | 86.6438 | 17.6493 | 2018-02-02 21:00 | 21 | 6 | 86.9703 | 18.4377 | 2018-02-02 21:00 | 21 | 6 | 65.9734 | 13.8544
2018-02-02 22:00 | 22 | 6 | 0 | 0 | 2018-02-02 22:00 | 22 | 6 | 86.6453 | 17.6496 | 2018-02-02 22:00 | 22 | 6 | 86.978 | 18.4393 | 2018-02-02 22:00 | 22 | 6 | 65.9769 | 13.8551
2018-02-02 23:00 | 23 | 6 | 0 | 0 | 2018-02-02 23:00 | 23 | 6 | 86.5202 | 17.6242 | 2018-02-02 23:00 | 23 | 6 | 86.9078 | 18.4245 | 2018-02-02 23:00 | 23 | 6 | 65.9026 | 13.8396
2018-02-03 | 0 | 7 | 86.0121 | 18.1486 | 2018-02-03 | 0 | 7 | 0 | 0 | 2018-02-03 | 0 | 7 | 86.5507 | 18.3487 | 2018-02-03 | 0 | 7 | 32.8893 | 6.9067
2018-02-03 01:00 | 1 | 7 | 85.919 | 18.1289 | 2018-02-03 01:00 | 1 | 7 | 0 | 0 | 2018-02-03 01:00 | 1 | 7 | 86.5324 | 18.3449 | 2018-02-03 01:00 | 1 | 7 | 32.8823 | 6.9053
2018-02-03 02:00 | 2 | 7 | 86.0533 | 18.1572 | 2018-02-03 02:00 | 2 | 7 | 0 | 0 | 2018-02-03 02:00 | 2 | 7 | 86.6453 | 18.3688 | 2018-02-03 02:00 | 2 | 7 | 32.9252 | 6.9143
2018-02-03 03:00 | 3 | 7 | 86.1677 | 18.1814 | 2018-02-03 03:00 | 3 | 7 | 0 | 0 | 2018-02-03 03:00 | 3 | 7 | 86.7002 | 18.3804 | 2018-02-03 03:00 | 3 | 7 | 32.9461 | 6.9187
2018-02-03 04:00 | 4 | 7 | 86.3081 | 18.211 | 2018-02-03 04:00 | 4 | 7 | 0 | 0 | 2018-02-03 04:00 | 4 | 7 | 86.8513 | 18.4125 | 2018-02-03 04:00 | 4 | 7 | 33.0035 | 6.9307
2018-02-03 05:00 | 5 | 7 | 86.2562 | 18.2001 | 2018-02-03 05:00 | 5 | 7 | 0 | 0 | 2018-02-03 05:00 | 5 | 7 | 86.8605 | 18.4144 | 2018-02-03 05:00 | 5 | 7 | 33.007 | 6.9315
2018-02-03 06:00 | 6 | 7 | 86.1234 | 18.172 | 2018-02-03 06:00 | 6 | 7 | 0 | 0 | 2018-02-03 06:00 | 6 | 7 | 86.6682 | 18.3737 | 2018-02-03 06:00 | 6 | 7 | 32.9339 | 6.9161
2018-02-03 07:00 | 7 | 7 | 86.1906 | 18.1862 | 2018-02-03 07:00 | 7 | 7 | 0 | 0 | 2018-02-03 07:00 | 7 | 7 | 86.7247 | 18.3856 | 2018-02-03 07:00 | 7 | 7 | 32.9554 | 6.9206
2018-02-03 08:00 | 8 | 7 | 86.36 | 18.222 | 2018-02-03 08:00 | 8 | 7 | 0 | 0 | 2018-02-03 08:00 | 8 | 7 | 86.952 | 18.4338 | 2018-02-03 08:00 | 8 | 7 | 33.0418 | 6.9388
2018-02-03 09:00 | 9 | 7 | 86.4912 | 18.2496 | 2018-02-03 09:00 | 9 | 7 | 0 | 0 | 2018-02-03 09:00 | 9 | 7 | 87.0588 | 18.4565 | 2018-02-03 09:00 | 9 | 7 | 33.0823 | 6.9473
2018-02-03 10:00 | 10 | 7 | 86.1982 | 18.1878 | 2018-02-03 10:00 | 10 | 7 | 0 | 0 | 2018-02-03 10:00 | 10 | 7 | 86.6392 | 18.3675 | 2018-02-03 10:00 | 10 | 7 | 32.9229 | 6.9138
2018-02-03 11:00 | 11 | 7 | 86.1707 | 18.182 | 2018-02-03 11:00 | 11 | 7 | 0 | 0 | 2018-02-03 11:00 | 11 | 7 | 86.8849 | 18.4196 | 2018-02-03 11:00 | 11 | 7 | 33.0163 | 6.9334
2018-02-03 12:00 | 12 | 7 | 86.5019 | 18.2519 | 2018-02-03 12:00 | 12 | 7 | 0 | 0 | 2018-02-03 12:00 | 12 | 7 | 87.1504 | 18.4759 | 2018-02-03 12:00 | 12 | 7 | 33.1172 | 6.9546
2018-02-03 13:00 | 13 | 7 | 86.6148 | 18.2757 | 2018-02-03 13:00 | 13 | 7 | 0 | 0 | 2018-02-03 13:00 | 13 | 7 | 87.3167 | 18.5111 | 2018-02-03 13:00 | 13 | 7 | 33.1803 | 6.9679
2018-02-03 14:00 | 14 | 7 | 86.4439 | 18.2397 | 2018-02-03 14:00 | 14 | 7 | 0 | 0 | 2018-02-03 14:00 | 14 | 7 | 87.0832 | 18.4616 | 2018-02-03 14:00 | 14 | 7 | 33.0916 | 6.9492
2018-02-03 15:00 | 15 | 7 | 86.5522 | 18.2625 | 2018-02-03 15:00 | 15 | 7 | 0 | 0 | 2018-02-03 15:00 | 15 | 7 | 87.2938 | 18.5063 | 2018-02-03 15:00 | 15 | 7 | 33.1716 | 6.966
2018-02-03 16:00 | 16 | 7 | 86.5644 | 18.2651 | 2018-02-03 16:00 | 16 | 7 | 0 | 0 | 2018-02-03 16:00 | 16 | 7 | 87.3579 | 18.5199 | 2018-02-03 16:00 | 16 | 7 | 33.196 | 6.9712
2018-02-03 17:00 | 17 | 7 | 86.7445 | 18.3031 | 2018-02-03 17:00 | 17 | 7 | 0 | 0 | 2018-02-03 17:00 | 17 | 7 | 87.57 | 18.5648 | 2018-02-03 17:00 | 17 | 7 | 33.2766 | 6.9881
2018-02-03 18:00 | 18 | 7 | 86.4668 | 18.2445 | 2018-02-03 18:00 | 18 | 7 | 0 | 0 | 2018-02-03 18:00 | 18 | 7 | 87.3014 | 18.5079 | 2018-02-03 18:00 | 18 | 7 | 33.1745 | 6.9667
2018-02-03 19:00 | 19 | 7 | 86.3661 | 18.2232 | 2018-02-03 19:00 | 19 | 7 | 0 | 0 | 2018-02-03 19:00 | 19 | 7 | 87.0954 | 18.4642 | 2018-02-03 19:00 | 19 | 7 | 33.0963 | 6.9502
2018-02-03 20:00 | 20 | 7 | 86.1173 | 18.1708 | 2018-02-03 20:00 | 20 | 7 | 0 | 0 | 2018-02-03 20:00 | 20 | 7 | 86.891 | 18.4209 | 2018-02-03 20:00 | 20 | 7 | 33.0186 | 6.9339
2018-02-03 21:00 | 21 | 7 | 86.1555 | 18.1788 | 2018-02-03 21:00 | 21 | 7 | 0 | 0 | 2018-02-03 21:00 | 21 | 7 | 86.9245 | 18.428 | 2018-02-03 21:00 | 21 | 7 | 33.0313 | 6.9366
2018-02-03 22:00 | 22 | 7 | 86.2211 | 18.1927 | 2018-02-03 22:00 | 22 | 7 | 0 | 0 | 2018-02-03 22:00 | 22 | 7 | 87.0054 | 18.4451 | 2018-02-03 22:00 | 22 | 7 | 33.0621 | 6.943
2018-02-03 23:00 | 23 | 7 | 86.2226 | 18.193 | 2018-02-03 23:00 | 23 | 7 | 0 | 0 | 2018-02-03 23:00 | 23 | 7 | 87.0787 | 18.4607 | 2018-02-03 23:00 | 23 | 7 | 33.0899 | 6.9489
2018-02-04 | 0 | 1 | 86.2364 | 18.1959 | 2018-02-04 | 0 | 1 | 86.7994 | 17.681 | 2018-02-04 | 0 | 1 | 0 | 0 | 2018-02-04 | 0 | 1 | 32.9838 | 6.9266
2018-02-04 01:00 | 1 | 1 | 86.3188 | 18.2133 | 2018-02-04 01:00 | 1 | 1 | 86.952 | 17.7121 | 2018-02-04 01:00 | 1 | 1 | 0 | 0 | 2018-02-04 01:00 | 1 | 1 | 33.0418 | 6.9388
2018-02-04 02:00 | 2 | 1 | 86.2119 | 18.1907 | 2018-02-04 02:00 | 2 | 1 | 86.8177 | 17.6848 | 2018-02-04 02:00 | 2 | 1 | 0 | 0 | 2018-02-04 02:00 | 2 | 1 | 32.9907 | 6.9281
2018-02-04 03:00 | 3 | 1 | 86.1845 | 18.1849 | 2018-02-04 03:00 | 3 | 1 | 86.7857 | 17.6782 | 2018-02-04 03:00 | 3 | 1 | 0 | 0 | 2018-02-04 03:00 | 3 | 1 | 32.9786 | 6.9255
2018-02-04 04:00 | 4 | 1 | 86.2455 | 18.1978 | 2018-02-04 04:00 | 4 | 1 | 86.833 | 17.6879 | 2018-02-04 04:00 | 4 | 1 | 0 | 0 | 2018-02-04 04:00 | 4 | 1 | 32.9965 | 6.9293
2018-02-04 05:00 | 5 | 1 | 86.2333 | 18.1952 | 2018-02-04 05:00 | 5 | 1 | 86.833 | 17.6879 | 2018-02-04 05:00 | 5 | 1 | 0 | 0 | 2018-02-04 05:00 | 5 | 1 | 32.9965 | 6.9293
2018-02-04 06:00 | 6 | 1 | 86.2776 | 18.2046 | 2018-02-04 06:00 | 6 | 1 | 86.8528 | 17.6919 | 2018-02-04 06:00 | 6 | 1 | 0 | 0 | 2018-02-04 06:00 | 6 | 1 | 33.0041 | 6.9309
2018-02-04 07:00 | 7 | 1 | 86.2867 | 18.2065 | 2018-02-04 07:00 | 7 | 1 | 86.8452 | 17.6904 | 2018-02-04 07:00 | 7 | 1 | 0 | 0 | 2018-02-04 07:00 | 7 | 1 | 33.0012 | 6.9302
2018-02-04 08:00 | 8 | 1 | 86.2989 | 18.2091 | 2018-02-04 08:00 | 8 | 1 | 86.9032 | 17.7022 | 2018-02-04 08:00 | 8 | 1 | 0 | 0 | 2018-02-04 08:00 | 8 | 1 | 33.0232 | 6.9349
2018-02-04 09:00 | 9 | 1 | 86.2867 | 18.2065 | 2018-02-04 09:00 | 9 | 1 | 86.8162 | 17.6845 | 2018-02-04 09:00 | 9 | 1 | 0 | 0 | 2018-02-04 09:00 | 9 | 1 | 32.9902 | 6.9279
2018-02-04 10:00 | 10 | 1 | 86.2882 | 18.2068 | 2018-02-04 10:00 | 10 | 1 | 86.8528 | 17.6919 | 2018-02-04 10:00 | 10 | 1 | 0 | 0 | 2018-02-04 10:00 | 10 | 1 | 33.0041 | 6.9309
2018-02-04 11:00 | 11 | 1 | 86.1845 | 18.1849 | 2018-02-04 11:00 | 11 | 1 | 86.743 | 17.6695 | 2018-02-04 11:00 | 11 | 1 | 0 | 0 | 2018-02-04 11:00 | 11 | 1 | 32.9623 | 6.9221
2018-02-04 12:00 | 12 | 1 | 86.1418 | 18.1759 | 2018-02-04 12:00 | 12 | 1 | 86.714 | 17.6636 | 2018-02-04 12:00 | 12 | 1 | 0 | 0 | 2018-02-04 12:00 | 12 | 1 | 32.9513 | 6.9198
2018-02-04 13:00 | 13 | 1 | 86.1479 | 18.1772 | 2018-02-04 13:00 | 13 | 1 | 86.7659 | 17.6742 | 2018-02-04 13:00 | 13 | 1 | 0 | 0 | 2018-02-04 13:00 | 13 | 1 | 32.971 | 6.9239
2018-02-04 14:00 | 14 | 1 | 86.1112 | 18.1695 | 2018-02-04 14:00 | 14 | 1 | 86.7018 | 17.6612 | 2018-02-04 14:00 | 14 | 1 | 0 | 0 | 2018-02-04 14:00 | 14 | 1 | 32.9467 | 6.9188
2018-02-04 15:00 | 15 | 1 | 86.2455 | 18.1978 | 2018-02-04 15:00 | 15 | 1 | 86.8482 | 17.691 | 2018-02-04 15:00 | 15 | 1 | 0 | 0 | 2018-02-04 15:00 | 15 | 1 | 33.0023 | 6.9305
2018-02-04 16:00 | 16 | 1 | 86.3447 | 18.2187 | 2018-02-04 16:00 | 16 | 1 | 86.9398 | 17.7096 | 2018-02-04 16:00 | 16 | 1 | 0 | 0 | 2018-02-04 16:00 | 16 | 1 | 33.0371 | 6.9378
2018-02-04 17:00 | 17 | 1 | 86.4805 | 18.2474 | 2018-02-04 17:00 | 17 | 1 | 86.9856 | 17.719 | 2018-02-04 17:00 | 17 | 1 | 0 | 0 | 2018-02-04 17:00 | 17 | 1 | 33.0545 | 6.9415
2018-02-04 18:00 | 18 | 1 | 86.4332 | 18.2374 | 2018-02-04 18:00 | 18 | 1 | 86.92 | 17.7056 | 2018-02-04 18:00 | 18 | 1 | 0 | 0 | 2018-02-04 18:00 | 18 | 1 | 33.0296 | 6.9362
2018-02-04 19:00 | 19 | 1 | 85.6794 | 18.0784 | 2018-02-04 19:00 | 19 | 1 | 85.9266 | 17.5032 | 2018-02-04 19:00 | 19 | 1 | 0 | 0 | 2018-02-04 19:00 | 19 | 1 | 32.6521 | 6.8569
2018-02-04 20:00 | 20 | 1 | 86.3294 | 18.2155 | 2018-02-04 20:00 | 20 | 1 | 86.5888 | 17.6381 | 2018-02-04 20:00 | 20 | 1 | 0 | 0 | 2018-02-04 20:00 | 20 | 1 | 32.9037 | 6.9098
2018-02-04 21:00 | 21 | 1 | 86.3569 | 18.2213 | 2018-02-04 21:00 | 21 | 1 | 86.6728 | 17.6552 | 2018-02-04 21:00 | 21 | 1 | 0 | 0 | 2018-02-04 21:00 | 21 | 1 | 32.9357 | 6.9165
2018-02-04 22:00 | 22 | 1 | 86.4881 | 18.249 | 2018-02-04 22:00 | 22 | 1 | 86.8086 | 17.6829 | 2018-02-04 22:00 | 22 | 1 | 0 | 0 | 2018-02-04 22:00 | 22 | 1 | 32.9873 | 6.9273
2018-02-04 23:00 | 23 | 1 | 86.4332 | 18.2374 | 2018-02-04 23:00 | 23 | 1 | 86.7353 | 17.668 | 2018-02-04 23:00 | 23 | 1 | 0 | 0 | 2018-02-04 23:00 | 23 | 1 | 32.9594 | 6.9215
2018-02-05 | 0 | 2 | 86.4088 | 18.2323 | 2018-02-05 | 0 | 2 | 86.7002 | 17.6608 | 2018-02-05 | 0 | 2 | 86.9352 | 18.4303 | 2018-02-05 | 0 | 2 | 65.9815 | 13.8561
2018-02-05 01:00 | 1 | 2 | 86.0426 | 18.155 | 2018-02-05 01:00 | 1 | 2 | 86.3127 | 17.5819 | 2018-02-05 01:00 | 1 | 2 | 86.5278 | 18.3439 | 2018-02-05 01:00 | 1 | 2 | 65.6794 | 13.7927
2018-02-05 02:00 | 2 | 2 | 86.392 | 18.2287 | 2018-02-05 02:00 | 2 | 2 | 86.6392 | 17.6484 | 2018-02-05 02:00 | 2 | 2 | 86.8421 | 18.4105 | 2018-02-05 02:00 | 2 | 2 | 65.9229 | 13.8438
2018-02-05 03:00 | 3 | 2 | 86.2776 | 18.2046 | 2018-02-05 03:00 | 3 | 2 | 86.5766 | 17.6357 | 2018-02-05 03:00 | 3 | 2 | 86.7536 | 18.3918 | 2018-02-05 03:00 | 3 | 2 | 65.8655 | 13.8317
2018-02-05 04:00 | 4 | 2 | 86.5034 | 18.2522 | 2018-02-05 04:00 | 4 | 2 | 86.8849 | 17.6985 | 2018-02-05 04:00 | 4 | 2 | 87.0283 | 18.45 | 2018-02-05 04:00 | 4 | 2 | 66.087 | 13.8783
2018-02-05 05:00 | 5 | 2 | 86.3661 | 18.2232 | 2018-02-05 05:00 | 5 | 2 | 86.772 | 17.6755 | 2018-02-05 05:00 | 5 | 2 | 87.0054 | 18.4451 | 2018-02-05 05:00 | 5 | 2 | 66.0354 | 13.8674
2018-02-05 06:00 | 6 | 2 | 86.2898 | 18.2071 | 2018-02-05 06:00 | 6 | 2 | 86.6499 | 17.6506 | 2018-02-05 06:00 | 6 | 2 | 86.8147 | 18.4047 | 2018-02-05 06:00 | 6 | 2 | 65.9165 | 13.8425
2018-02-05 07:00 | 7 | 2 | 86.2043 | 18.1891 | 2018-02-05 07:00 | 7 | 2 | 86.5278 | 17.6257 | 2018-02-05 07:00 | 7 | 2 | 86.7079 | 18.3821 | 2018-02-05 07:00 | 7 | 2 | 65.8296 | 13.8242
2018-02-05 08:00 | 8 | 2 | 86.3355 | 18.2168 | 2018-02-05 08:00 | 8 | 2 | 86.5461 | 17.6294 | 2018-02-05 08:00 | 8 | 2 | 86.8025 | 18.4021 | 2018-02-05 08:00 | 8 | 2 | 65.8725 | 13.8332
2018-02-05 09:00 | 9 | 2 | 86.3798 | 18.2261 | 2018-02-05 09:00 | 9 | 2 | 86.7262 | 17.6661 | 2018-02-05 09:00 | 9 | 2 | 86.8711 | 18.4167 | 2018-02-05 09:00 | 9 | 2 | 65.967 | 13.8531
2018-02-05 10:00 | 10 | 2 | 86.2272 | 18.1939 | 2018-02-05 10:00 | 10 | 2 | 86.5156 | 17.6232 | 2018-02-05 10:00 | 10 | 2 | 86.714 | 18.3834 | 2018-02-05 10:00 | 10 | 2 | 65.8272 | 13.8237
2018-02-05 11:00 | 11 | 2 | 86.2119 | 18.1907 | 2018-02-05 11:00 | 11 | 2 | 86.5141 | 17.6229 | 2018-02-05 11:00 | 11 | 2 | 86.7201 | 18.3847 | 2018-02-05 11:00 | 11 | 2 | 65.829 | 13.8241
2018-02-05 12:00 | 12 | 2 | 86.389 | 18.2281 | 2018-02-05 12:00 | 12 | 2 | 86.6835 | 17.6574 | 2018-02-05 12:00 | 12 | 2 | 86.8574 | 18.4138 | 2018-02-05 12:00 | 12 | 2 | 65.9455 | 13.8486
2018-02-05 13:00 | 13 | 2 | 86.4027 | 18.231 | 2018-02-05 13:00 | 13 | 2 | 86.6224 | 17.645 | 2018-02-05 13:00 | 13 | 2 | 86.7475 | 18.3905 | 2018-02-05 13:00 | 13 | 2 | 65.8806 | 13.8349
2018-02-05 14:00 | 14 | 2 | 86.3783 | 18.2258 | 2018-02-05 14:00 | 14 | 2 | 86.6606 | 17.6528 | 2018-02-05 14:00 | 14 | 2 | 86.7903 | 18.3995 | 2018-02-05 14:00 | 14 | 2 | 65.9113 | 13.8414
2018-02-05 15:00 | 15 | 2 | 86.3355 | 18.2168 | 2018-02-05 15:00 | 15 | 2 | 86.5248 | 17.6251 | 2018-02-05 15:00 | 15 | 2 | 86.7384 | 18.3885 | 2018-02-05 15:00 | 15 | 2 | 65.84 | 13.8264
2018-02-05 16:00 | 16 | 2 | 86.3493 | 18.2197 | 2018-02-05 16:00 | 16 | 2 | 86.4912 | 17.6183 | 2018-02-05 16:00 | 16 | 2 | 86.685 | 18.3772 | 2018-02-05 16:00 | 16 | 2 | 65.807 | 13.8195
2018-02-05 17:00 | 17 | 2 | 86.244 | 18.1975 | 2018-02-05 17:00 | 17 | 2 | 86.4683 | 17.6136 | 2018-02-05 17:00 | 17 | 2 | 86.6743 | 18.375 | 2018-02-05 17:00 | 17 | 2 | 65.7942 | 13.8168
2018-02-05 18:00 | 18 | 2 | 86.3142 | 18.2123 | 2018-02-05 18:00 | 18 | 2 | 86.4378 | 17.6074 | 2018-02-05 18:00 | 18 | 2 | 86.5934 | 18.3578 | 2018-02-05 18:00 | 18 | 2 | 65.7519 | 13.8079
2018-02-05 19:00 | 19 | 2 | 86.2089 | 18.1901 | 2018-02-05 19:00 | 19 | 2 | 86.3508 | 17.5897 | 2018-02-05 19:00 | 19 | 2 | 86.5583 | 18.3504 | 2018-02-05 19:00 | 19 | 2 | 65.7055 | 13.7981
2018-02-05 20:00 | 20 | 2 | 86.2181 | 18.192 | 2018-02-05 20:00 | 20 | 2 | 86.4836 | 17.6167 | 2018-02-05 20:00 | 20 | 2 | 86.6896 | 18.3782 | 2018-02-05 20:00 | 20 | 2 | 65.8058 | 13.8192
2018-02-05 21:00 | 21 | 2 | 86.1494 | 18.1775 | 2018-02-05 21:00 | 21 | 2 | 86.4759 | 17.6151 | 2018-02-05 21:00 | 21 | 2 | 86.63 | 18.3656 | 2018-02-05 21:00 | 21 | 2 | 65.7802 | 13.8139
2018-02-05 22:00 | 22 | 2 | 86.2593 | 18.2007 | 2018-02-05 22:00 | 22 | 2 | 86.5522 | 17.6307 | 2018-02-05 22:00 | 22 | 2 | 86.6468 | 18.3691 | 2018-02-05 22:00 | 22 | 2 | 65.8156 | 13.8213
2018-02-05 23:00 | 23 | 2 | 86.4424 | 18.2393 | 2018-02-05 23:00 | 23 | 2 | 86.8055 | 17.6823 | 2018-02-05 23:00 | 23 | 2 | 86.8864 | 18.4199 | 2018-02-05 23:00 | 23 | 2 | 66.0029 | 13.8606
2018-02-06 | 0 | 3 | 86.4637 | 18.2438 | 2018-02-06 | 0 | 3 | 0 | 0 | 2018-02-06 | 0 | 3 | 0 | 0 | 2018-02-06 | 0 | 3 | 0 | 0
2018-02-06 01:00 | 1 | 3 | 86.5629 | 18.2648 | 2018-02-06 01:00 | 1 | 3 | 0 | 0 | 2018-02-06 01:00 | 1 | 3 | 0 | 0 | 2018-02-06 01:00 | 1 | 3 | 0 | 0
2018-02-06 02:00 | 2 | 3 | 86.3706 | 18.2242 | 2018-02-06 02:00 | 2 | 3 | 0 | 0 | 2018-02-06 02:00 | 2 | 3 | 0 | 0 | 2018-02-06 02:00 | 2 | 3 | 0 | 0
2018-02-06 03:00 | 3 | 3 | 86.3523 | 18.2203 | 2018-02-06 03:00 | 3 | 3 | 0 | 0 | 2018-02-06 03:00 | 3 | 3 | 0 | 0 | 2018-02-06 03:00 | 3 | 3 | 0 | 0
2018-02-06 04:00 | 4 | 3 | 86.3676 | 18.2236 | 2018-02-06 04:00 | 4 | 3 | 0 | 0 | 2018-02-06 04:00 | 4 | 3 | 0 | 0 | 2018-02-06 04:00 | 4 | 3 | 0 | 0
2018-02-06 05:00 | 5 | 3 | 86.4027 | 18.231 | 2018-02-06 05:00 | 5 | 3 | 0 | 0 | 2018-02-06 05:00 | 5 | 3 | 0 | 0 | 2018-02-06 05:00 | 5 | 3 | 0 | 0
2018-02-06 06:00 | 6 | 3 | 86.4652 | 18.2442 | 2018-02-06 06:00 | 6 | 3 | 0 | 0 | 2018-02-06 06:00 | 6 | 3 | 0 | 0 | 2018-02-06 06:00 | 6 | 3 | 0 | 0
2018-02-06 07:00 | 7 | 3 | 86.4012 | 18.2307 | 2018-02-06 07:00 | 7 | 3 | 0 | 0 | 2018-02-06 07:00 | 7 | 3 | 0 | 0 | 2018-02-06 07:00 | 7 | 3 | 0 | 0
2018-02-06 08:00 | 8 | 3 | 86.4515 | 18.2413 | 2018-02-06 08:00 | 8 | 3 | 0 | 0 | 2018-02-06 08:00 | 8 | 3 | 0 | 0 | 2018-02-06 08:00 | 8 | 3 | 0 | 0
2018-02-06 09:00 | 9 | 3 | 86.2028 | 18.1888 | 2018-02-06 09:00 | 9 | 3 | 0 | 0 | 2018-02-06 09:00 | 9 | 3 | 0 | 0 | 2018-02-06 09:00 | 9 | 3 | 0 | 0
2018-02-06 10:00 | 10 | 3 | 86.2715 | 18.2033 | 2018-02-06 10:00 | 10 | 3 | 0 | 0 | 2018-02-06 10:00 | 10 | 3 | 0 | 0 | 2018-02-06 10:00 | 10 | 3 | 0 | 0
2018-02-06 11:00 | 11 | 3 | 86.7567 | 18.3057 | 2018-02-06 11:00 | 11 | 3 | 0 | 0 | 2018-02-06 11:00 | 11 | 3 | 0 | 0 | 2018-02-06 11:00 | 11 | 3 | 0 | 0
2018-02-06 12:00 | 12 | 3 | 86.6194 | 18.2767 | 2018-02-06 12:00 | 12 | 3 | 0 | 0 | 2018-02-06 12:00 | 12 | 3 | 0 | 0 | 2018-02-06 12:00 | 12 | 3 | 0 | 0
2018-02-06 13:00 | 13 | 3 | 86.6377 | 18.2806 | 2018-02-06 13:00 | 13 | 3 | 0 | 0 | 2018-02-06 13:00 | 13 | 3 | 0 | 0 | 2018-02-06 13:00 | 13 | 3 | 0 | 0
2018-02-06 14:00 | 14 | 3 | 86.8757 | 18.3308 | 2018-02-06 14:00 | 14 | 3 | 0 | 0 | 2018-02-06 14:00 | 14 | 3 | 0 | 0 | 2018-02-06 14:00 | 14 | 3 | 0 | 0
2018-02-06 15:00 | 15 | 3 | 86.7994 | 18.3147 | 2018-02-06 15:00 | 15 | 3 | 0 | 0 | 2018-02-06 15:00 | 15 | 3 | 0 | 0 | 2018-02-06 15:00 | 15 | 3 | 0 | 0
2018-02-06 16:00 | 16 | 3 | 86.7674 | 18.3079 | 2018-02-06 16:00 | 16 | 3 | 0 | 0 | 2018-02-06 16:00 | 16 | 3 | 0 | 0 | 2018-02-06 16:00 | 16 | 3 | 0 | 0
2018-02-06 17:00 | 17 | 3 | 86.7384 | 18.3018 | 2018-02-06 17:00 | 17 | 3 | 0 | 0 | 2018-02-06 17:00 | 17 | 3 | 0 | 0 | 2018-02-06 17:00 | 17 | 3 | 0 | 0
2018-02-06 18:00 | 18 | 3 | 86.7124 | 18.2963 | 2018-02-06 18:00 | 18 | 3 | 0 | 0 | 2018-02-06 18:00 | 18 | 3 | 0 | 0 | 2018-02-06 18:00 | 18 | 3 | 0 | 0
2018-02-06 19:00 | 19 | 3 | 86.8376 | 18.3227 | 2018-02-06 19:00 | 19 | 3 | 0 | 0 | 2018-02-06 19:00 | 19 | 3 | 0 | 0 | 2018-02-06 19:00 | 19 | 3 | 0 | 0
2018-02-06 20:00 | 20 | 3 | 86.627 | 18.2783 | 2018-02-06 20:00 | 20 | 3 | 0 | 0 | 2018-02-06 20:00 | 20 | 3 | 0 | 0 | 2018-02-06 20:00 | 20 | 3 | 0 | 0
2018-02-06 21:00 | 21 | 3 | 86.6239 | 18.2776 | 2018-02-06 21:00 | 21 | 3 | 0 | 0 | 2018-02-06 21:00 | 21 | 3 | 0 | 0 | 2018-02-06 21:00 | 21 | 3 | 0 | 0
2018-02-06 22:00 | 22 | 3 | 86.714 | 18.2967 | 2018-02-06 22:00 | 22 | 3 | 0 | 0 | 2018-02-06 22:00 | 22 | 3 | 0 | 0 | 2018-02-06 22:00 | 22 | 3 | 0 | 0
2018-02-06 23:00 | 23 | 3 | 86.8971 | 18.3353 | 2018-02-06 23:00 | 23 | 3 | 0 | 0 | 2018-02-06 23:00 | 23 | 3 | 0 | 0 | 2018-02-06 23:00 | 23 | 3 | 0 | 0
2018-02-07 | 0 | 4 | 0 | 0 | 2018-02-07 | 0 | 4 | 0 | 0 | 2018-02-07 | 0 | 4 | 86.6712 | 18.3743 | 2018-02-07 | 0 | 4 | 32.9351 | 6.9164
2018-02-07 01:00 | 1 | 4 | 0 | 0 | 2018-02-07 01:00 | 1 | 4 | 0 | 0 | 2018-02-07 01:00 | 1 | 4 | 86.511 | 18.3403 | 2018-02-07 01:00 | 1 | 4 | 32.8742 | 6.9036
2018-02-07 02:00 | 2 | 4 | 0 | 0 | 2018-02-07 02:00 | 2 | 4 | 0 | 0 | 2018-02-07 02:00 | 2 | 4 | 86.7628 | 18.3937 | 2018-02-07 02:00 | 2 | 4 | 32.9699 | 6.9237
2018-02-07 03:00 | 3 | 4 | 0 | 0 | 2018-02-07 03:00 | 3 | 4 | 0 | 0 | 2018-02-07 03:00 | 3 | 4 | 86.7384 | 18.3885 | 2018-02-07 03:00 | 3 | 4 | 32.9606 | 6.9217
2018-02-07 04:00 | 4 | 4 | 0 | 0 | 2018-02-07 04:00 | 4 | 4 | 0 | 0 | 2018-02-07 04:00 | 4 | 4 | 86.8376 | 18.4096 | 2018-02-07 04:00 | 4 | 4 | 32.9983 | 6.9296
2018-02-07 05:00 | 5 | 4 | 0 | 0 | 2018-02-07 05:00 | 5 | 4 | 0 | 0 | 2018-02-07 05:00 | 5 | 4 | 87.0222 | 18.4487 | 2018-02-07 05:00 | 5 | 4 | 33.0684 | 6.9444
2018-02-07 06:00 | 6 | 4 | 0 | 0 | 2018-02-07 06:00 | 6 | 4 | 0 | 0 | 2018-02-07 06:00 | 6 | 4 | 86.9627 | 18.4361 | 2018-02-07 06:00 | 6 | 4 | 33.0458 | 6.9396
2018-02-07 07:00 | 7 | 4 | 0 | 0 | 2018-02-07 07:00 | 7 | 4 | 0 | 0 | 2018-02-07 07:00 | 7 | 4 | 87.1321 | 18.472 | 2018-02-07 07:00 | 7 | 4 | 33.1102 | 6.9531
2018-02-07 08:00 | 8 | 4 | 0 | 0 | 2018-02-07 08:00 | 8 | 4 | 0 | 0 | 2018-02-07 08:00 | 8 | 4 | 87.1931 | 18.4849 | 2018-02-07 08:00 | 8 | 4 | 33.1334 | 6.958
2018-02-07 09:00 | 9 | 4 | 0 | 0 | 2018-02-07 09:00 | 9 | 4 | 0 | 0 | 2018-02-07 09:00 | 9 | 4 | 86.7155 | 18.3837 | 2018-02-07 09:00 | 9 | 4 | 32.9519 | 6.9199
2018-02-07 10:00 | 10 | 4 | 0 | 0 | 2018-02-07 10:00 | 10 | 4 | 0 | 0 | 2018-02-07 10:00 | 10 | 4 | 86.6743 | 18.375 | 2018-02-07 10:00 | 10 | 4 | 32.9362 | 6.9166
2018-02-07 11:00 | 11 | 4 | 0 | 0 | 2018-02-07 11:00 | 11 | 4 | 0 | 0 | 2018-02-07 11:00 | 11 | 4 | 86.8956 | 18.4219 | 2018-02-07 11:00 | 11 | 4 | 33.0203 | 6.9343
2018-02-07 12:00 | 12 | 4 | 0 | 0 | 2018-02-07 12:00 | 12 | 4 | 0 | 0 | 2018-02-07 12:00 | 12 | 4 | 86.9276 | 18.4287 | 2018-02-07 12:00 | 12 | 4 | 33.0325 | 6.9368
2018-02-07 13:00 | 13 | 4 | 0 | 0 | 2018-02-07 13:00 | 13 | 4 | 0 | 0 | 2018-02-07 13:00 | 13 | 4 | 87.2541 | 18.4979 | 2018-02-07 13:00 | 13 | 4 | 33.1566 | 6.9629
2018-02-07 14:00 | 14 | 4 | 0 | 0 | 2018-02-07 14:00 | 14 | 4 | 0 | 0 | 2018-02-07 14:00 | 14 | 4 | 87.4037 | 18.5296 | 2018-02-07 14:00 | 14 | 4 | 33.2134 | 6.9748
2018-02-07 15:00 | 15 | 4 | 0 | 0 | 2018-02-07 15:00 | 15 | 4 | 0 | 0 | 2018-02-07 15:00 | 15 | 4 | 87.2129 | 18.4891 | 2018-02-07 15:00 | 15 | 4 | 33.1409 | 6.9596
2018-02-07 16:00 | 16 | 4 | 0 | 0 | 2018-02-07 16:00 | 16 | 4 | 0 | 0 | 2018-02-07 16:00 | 16 | 4 | 86.9718 | 18.438 | 2018-02-07 16:00 | 16 | 4 | 33.0493 | 6.9403
2018-02-07 17:00 | 17 | 4 | 0 | 0 | 2018-02-07 17:00 | 17 | 4 | 0 | 0 | 2018-02-07 17:00 | 17 | 4 | 87.1397 | 18.4736 | 2018-02-07 17:00 | 17 | 4 | 33.1131 | 6.9537
2018-02-07 18:00 | 18 | 4 | 0 | 0 | 2018-02-07 18:00 | 18 | 4 | 0 | 0 | 2018-02-07 18:00 | 18 | 4 | 87.2435 | 18.4956 | 2018-02-07 18:00 | 18 | 4 | 33.1525 | 6.962
2018-02-07 19:00 | 19 | 4 | 0 | 0 | 2018-02-07 19:00 | 19 | 4 | 0 | 0 | 2018-02-07 19:00 | 19 | 4 | 86.8894 | 18.4206 | 2018-02-07 19:00 | 19 | 4 | 33.018 | 6.9338
2018-02-07 20:00 | 20 | 4 | 0 | 0 | 2018-02-07 20:00 | 20 | 4 | 0 | 0 | 2018-02-07 20:00 | 20 | 4 | 87.1839 | 18.483 | 2018-02-07 20:00 | 20 | 4 | 33.1299 | 6.9573
2018-02-07 21:00 | 21 | 4 | 0 | 0 | 2018-02-07 21:00 | 21 | 4 | 0 | 0 | 2018-02-07 21:00 | 21 | 4 | 87.2419 | 18.4953 | 2018-02-07 21:00 | 21 | 4 | 33.1519 | 6.9619
2018-02-07 22:00 | 22 | 4 | 0 | 0 | 2018-02-07 22:00 | 22 | 4 | 0 | 0 | 2018-02-07 22:00 | 22 | 4 | 87.1733 | 18.4807 | 2018-02-07 22:00 | 22 | 4 | 33.1259 | 6.9564
2018-02-07 23:00 | 23 | 4 | 0 | 0 | 2018-02-07 23:00 | 23 | 4 | 0 | 0 | 2018-02-07 23:00 | 23 | 4 | 87.2557 | 18.4982 | 2018-02-07 23:00 | 23 | 4 | 33.1572 | 6.963
2018-02-08 | 0 | 5 | 86.5492 | 18.2619 | 2018-02-08 | 0 | 5 | 0 | 0 | 2018-02-08 | 0 | 5 | 0 | 0 | 2018-02-08 | 0 | 5 | 0 | 0
2018-02-08 01:00 | 1 | 5 | 86.7201 | 18.2979 | 2018-02-08 01:00 | 1 | 5 | 0 | 0 | 2018-02-08 01:00 | 1 | 5 | 0 | 0 | 2018-02-08 01:00 | 1 | 5 | 0 | 0
2018-02-08 02:00 | 2 | 5 | 86.5095 | 18.2535 | 2018-02-08 02:00 | 2 | 5 | 0 | 0 | 2018-02-08 02:00 | 2 | 5 | 0 | 0 | 2018-02-08 02:00 | 2 | 5 | 0 | 0
2018-02-08 03:00 | 3 | 5 | 86.4576 | 18.2426 | 2018-02-08 03:00 | 3 | 5 | 0 | 0 | 2018-02-08 03:00 | 3 | 5 | 0 | 0 | 2018-02-08 03:00 | 3 | 5 | 0 | 0
2018-02-08 04:00 | 4 | 5 | 86.6316 | 18.2793 | 2018-02-08 04:00 | 4 | 5 | 0 | 0 | 2018-02-08 04:00 | 4 | 5 | 0 | 0 | 2018-02-08 04:00 | 4 | 5 | 0 | 0
2018-02-08 05:00 | 5 | 5 | 86.569 | 18.2661 | 2018-02-08 05:00 | 5 | 5 | 0 | 0 | 2018-02-08 05:00 | 5 | 5 | 0 | 0 | 2018-02-08 05:00 | 5 | 5 | 0 | 0
2018-02-08 06:00 | 6 | 5 | 86.6468 | 18.2825 | 2018-02-08 06:00 | 6 | 5 | 0 | 0 | 2018-02-08 06:00 | 6 | 5 | 0 | 0 | 2018-02-08 06:00 | 6 | 5 | 0 | 0
2018-02-08 07:00 | 7 | 5 | 86.6361 | 18.2802 | 2018-02-08 07:00 | 7 | 5 | 0 | 0 | 2018-02-08 07:00 | 7 | 5 | 0 | 0 | 2018-02-08 07:00 | 7 | 5 | 0 | 0
2018-02-08 08:00 | 8 | 5 | 86.6819 | 18.2899 | 2018-02-08 08:00 | 8 | 5 | 0 | 0 | 2018-02-08 08:00 | 8 | 5 | 0 | 0 | 2018-02-08 08:00 | 8 | 5 | 0 | 0
2018-02-08 09:00 | 9 | 5 | 86.7094 | 18.2957 | 2018-02-08 09:00 | 9 | 5 | 0 | 0 | 2018-02-08 09:00 | 9 | 5 | 0 | 0 | 2018-02-08 09:00 | 9 | 5 | 0 | 0
2018-02-08 10:00 | 10 | 5 | 86.7933 | 18.3134 | 2018-02-08 10:00 | 10 | 5 | 0 | 0 | 2018-02-08 10:00 | 10 | 5 | 0 | 0 | 2018-02-08 10:00 | 10 | 5 | 0 | 0
2018-02-08 11:00 | 11 | 5 | 86.8009 | 18.315 | 2018-02-08 11:00 | 11 | 5 | 0 | 0 | 2018-02-08 11:00 | 11 | 5 | 0 | 0 | 2018-02-08 11:00 | 11 | 5 | 0 | 0
2018-02-08 12:00 | 12 | 5 | 86.6728 | 18.288 | 2018-02-08 12:00 | 12 | 5 | 0 | 0 | 2018-02-08 12:00 | 12 | 5 | 0 | 0 | 2018-02-08 12:00 | 12 | 5 | 0 | 0
2018-02-08 13:00 | 13 | 5 | 86.6316 | 18.2793 | 2018-02-08 13:00 | 13 | 5 | 0 | 0 | 2018-02-08 13:00 | 13 | 5 | 0 | 0 | 2018-02-08 13:00 | 13 | 5 | 0 | 0
2018-02-08 14:00 | 14 | 5 | 86.6316 | 18.2793 | 2018-02-08 14:00 | 14 | 5 | 0 | 0 | 2018-02-08 14:00 | 14 | 5 | 0 | 0 | 2018-02-08 14:00 | 14 | 5 | 0 | 0
2018-02-08 15:00 | 15 | 5 | 86.6636 | 18.286 | 2018-02-08 15:00 | 15 | 5 | 0 | 0 | 2018-02-08 15:00 | 15 | 5 | 0 | 0 | 2018-02-08 15:00 | 15 | 5 | 0 | 0
2018-02-08 16:00 | 16 | 5 | 86.5568 | 18.2635 | 2018-02-08 16:00 | 16 | 5 | 0 | 0 | 2018-02-08 16:00 | 16 | 5 | 0 | 0 | 2018-02-08 16:00 | 16 | 5 | 0 | 0
2018-02-08 17:00 | 17 | 5 | 86.6865 | 18.2909 | 2018-02-08 17:00 | 17 | 5 | 0 | 0 | 2018-02-08 17:00 | 17 | 5 | 0 | 0 | 2018-02-08 17:00 | 17 | 5 | 0 | 0
2018-02-08 18:00 | 18 | 5 | 86.7262 | 18.2992 | 2018-02-08 18:00 | 18 | 5 | 0 | 0 | 2018-02-08 18:00 | 18 | 5 | 0 | 0 | 2018-02-08 18:00 | 18 | 5 | 0 | 0
2018-02-08 19:00 | 19 | 5 | 86.5187 | 18.2554 | 2018-02-08 19:00 | 19 | 5 | 0 | 0 | 2018-02-08 19:00 | 19 | 5 | 0 | 0 | 2018-02-08 19:00 | 19 | 5 | 0 | 0
2018-02-08 20:00 | 20 | 5 | 86.5766 | 18.2677 | 2018-02-08 20:00 | 20 | 5 | 0 | 0 | 2018-02-08 20:00 | 20 | 5 | 0 | 0 | 2018-02-08 20:00 | 20 | 5 | 0 | 0
2018-02-08 21:00 | 21 | 5 | 86.6194 | 18.2767 | 2018-02-08 21:00 | 21 | 5 | 0 | 0 | 2018-02-08 21:00 | 21 | 5 | 0 | 0 | 2018-02-08 21:00 | 21 | 5 | 0 | 0
2018-02-08 22:00 | 22 | 5 | 86.6743 | 18.2883 | 2018-02-08 22:00 | 22 | 5 | 0 | 0 | 2018-02-08 22:00 | 22 | 5 | 0 | 0 | 2018-02-08 22:00 | 22 | 5 | 0 | 0
2018-02-08 23:00 | 23 | 5 | 86.5644 | 18.2651 | 2018-02-08 23:00 | 23 | 5 | 0 | 0 | 2018-02-08 23:00 | 23 | 5 | 0 | 0 | 2018-02-08 23:00 | 23 | 5 | 0 | 0
2018-02-09 | 0 | 6 | 86.2226 | 18.193 | 2018-02-09 | 0 | 6 | 86.688 | 17.6583 | 2018-02-09 | 0 | 6 | 0 | 0 | 2018-02-09 | 0 | 6 | 32.9414 | 6.9177
2018-02-09 01:00 | 1 | 6 | 86.1128 | 18.1698 | 2018-02-09 01:00 | 1 | 6 | 86.5232 | 17.6248 | 2018-02-09 01:00 | 1 | 6 | 0 | 0 | 2018-02-09 01:00 | 1 | 6 | 32.8788 | 6.9046
2018-02-09 02:00 | 2 | 6 | 86.2791 | 18.2049 | 2018-02-09 02:00 | 2 | 6 | 86.6896 | 17.6587 | 2018-02-09 02:00 | 2 | 6 | 0 | 0 | 2018-02-09 02:00 | 2 | 6 | 32.942 | 6.9178
2018-02-09 03:00 | 3 | 6 | 86.0014 | 18.1463 | 2018-02-09 03:00 | 3 | 6 | 86.4485 | 17.6096 | 2018-02-09 03:00 | 3 | 6 | 0 | 0 | 2018-02-09 03:00 | 3 | 6 | 32.8504 | 6.8986
2018-02-09 04:00 | 4 | 6 | 86.0533 | 18.1572 | 2018-02-09 04:00 | 4 | 6 | 86.4347 | 17.6067 | 2018-02-09 04:00 | 4 | 6 | 0 | 0 | 2018-02-09 04:00 | 4 | 6 | 32.8452 | 6.8975
2018-02-09 05:00 | 5 | 6 | 86.2257 | 18.1936 | 2018-02-09 05:00 | 5 | 6 | 86.6117 | 17.6428 | 2018-02-09 05:00 | 5 | 6 | 0 | 0 | 2018-02-09 05:00 | 5 | 6 | 32.9124 | 6.9116
2018-02-09 06:00 | 6 | 6 | 86.4332 | 18.2374 | 2018-02-09 06:00 | 6 | 6 | 86.9352 | 17.7087 | 2018-02-09 06:00 | 6 | 6 | 0 | 0 | 2018-02-09 06:00 | 6 | 6 | 33.0354 | 6.9374
2018-02-09 07:00 | 7 | 6 | 86.5873 | 18.2699 | 2018-02-09 07:00 | 7 | 6 | 87.0619 | 17.7345 | 2018-02-09 07:00 | 7 | 6 | 0 | 0 | 2018-02-09 07:00 | 7 | 6 | 33.0835 | 6.9475
2018-02-09 08:00 | 8 | 6 | 86.3691 | 18.2239 | 2018-02-09 08:00 | 8 | 6 | 86.7811 | 17.6773 | 2018-02-09 08:00 | 8 | 6 | 0 | 0 | 2018-02-09 08:00 | 8 | 6 | 32.9768 | 6.9251
2018-02-09 09:00 | 9 | 6 | 86.334 | 18.2165 | 2018-02-09 09:00 | 9 | 6 | 86.7399 | 17.6689 | 2018-02-09 09:00 | 9 | 6 | 0 | 0 | 2018-02-09 09:00 | 9 | 6 | 32.9612 | 6.9218
2018-02-09 10:00 | 10 | 6 | 86.5126 | 18.2542 | 2018-02-09 10:00 | 10 | 6 | 86.862 | 17.6938 | 2018-02-09 10:00 | 10 | 6 | 0 | 0 | 2018-02-09 10:00 | 10 | 6 | 33.0076 | 6.9316
2018-02-09 11:00 | 11 | 6 | 86.5003 | 18.2516 | 2018-02-09 11:00 | 11 | 6 | 86.9306 | 17.7078 | 2018-02-09 11:00 | 11 | 6 | 0 | 0 | 2018-02-09 11:00 | 11 | 6 | 33.0336 | 6.9371
2018-02-09 12:00 | 12 | 6 | 86.7002 | 18.2937 | 2018-02-09 12:00 | 12 | 6 | 87.1412 | 17.7507 | 2018-02-09 12:00 | 12 | 6 | 0 | 0 | 2018-02-09 12:00 | 12 | 6 | 33.1137 | 6.9539
2018-02-09 13:00 | 13 | 6 | 86.363 | 18.2226 | 2018-02-09 13:00 | 13 | 6 | 86.8009 | 17.6813 | 2018-02-09 13:00 | 13 | 6 | 0 | 0 | 2018-02-09 13:00 | 13 | 6 | 32.9843 | 6.9267
2018-02-09 14:00 | 14 | 6 | 86.4408 | 18.239 | 2018-02-09 14:00 | 14 | 6 | 86.8635 | 17.6941 | 2018-02-09 14:00 | 14 | 6 | 0 | 0 | 2018-02-09 14:00 | 14 | 6 | 33.0081 | 6.9317
2018-02-09 15:00 | 15 | 6 | 86.2943 | 18.2081 | 2018-02-09 15:00 | 15 | 6 | 86.6743 | 17.6556 | 2018-02-09 15:00 | 15 | 6 | 0 | 0 | 2018-02-09 15:00 | 15 | 6 | 32.9362 | 6.9166
2018-02-09 16:00 | 16 | 6 | 86.3706 | 18.2242 | 2018-02-09 16:00 | 16 | 6 | 86.7491 | 17.6708 | 2018-02-09 16:00 | 16 | 6 | 0 | 0 | 2018-02-09 16:00 | 16 | 6 | 32.9647 | 6.9226
2018-02-09 17:00 | 17 | 6 | 86.2882 | 18.2068 | 2018-02-09 17:00 | 17 | 6 | 86.7445 | 17.6699 | 2018-02-09 17:00 | 17 | 6 | 0 | 0 | 2018-02-09 17:00 | 17 | 6 | 32.9629 | 6.9222
2018-02-09 18:00 | 18 | 6 | 86.1875 | 18.1856 | 2018-02-09 18:00 | 18 | 6 | 86.6667 | 17.654 | 2018-02-09 18:00 | 18 | 6 | 0 | 0 | 2018-02-09 18:00 | 18 | 6 | 32.9333 | 6.916
2018-02-09 19:00 | 19 | 6 | 86.099 | 18.1669 | 2018-02-09 19:00 | 19 | 6 | 86.5431 | 17.6288 | 2018-02-09 19:00 | 19 | 6 | 0 | 0 | 2018-02-09 19:00 | 19 | 6 | 32.8864 | 6.9061
2018-02-09 20:00 | 20 | 6 | 86.1997 | 18.1881 | 2018-02-09 20:00 | 20 | 6 | 86.5187 | 17.6239 | 2018-02-09 20:00 | 20 | 6 | 0 | 0 | 2018-02-09 20:00 | 20 | 6 | 32.8771 | 6.9042
2018-02-09 21:00 | 21 | 6 | 86.3767 | 18.2255 | 2018-02-09 21:00 | 21 | 6 | 86.7247 | 17.6658 | 2018-02-09 21:00 | 21 | 6 | 0 | 0 | 2018-02-09 21:00 | 21 | 6 | 32.9554 | 6.9206
2018-02-09 22:00 | 22 | 6 | 86.3691 | 18.2239 | 2018-02-09 22:00 | 22 | 6 | 86.7659 | 17.6742 | 2018-02-09 22:00 | 22 | 6 | 0 | 0 | 2018-02-09 22:00 | 22 | 6 | 32.971 | 6.9239
2018-02-09 23:00 | 23 | 6 | 86.4012 | 18.2307 | 2018-02-09 23:00 | 23 | 6 | 86.7918 | 17.6795 | 2018-02-09 23:00 | 23 | 6 | 0 | 0 | 2018-02-09 23:00 | 23 | 6 | 32.9809 | 6.926
2018-02-10 | 0 | 7 | 86.0121 | 18.1486 | 2018-02-10 | 0 | 7 | 0 | 0 | 2018-02-10 | 0 | 7 | 86.5507 | 18.3487 | 2018-02-10 | 0 | 7 | 32.8893 | 6.9067
2018-02-10 01:00 | 1 | 7 | 85.919 | 18.1289 | 2018-02-10 01:00 | 1 | 7 | 0 | 0 | 2018-02-10 01:00 | 1 | 7 | 86.5324 | 18.3449 | 2018-02-10 01:00 | 1 | 7 | 32.8823 | 6.9053
2018-02-10 02:00 | 2 | 7 | 86.0533 | 18.1572 | 2018-02-10 02:00 | 2 | 7 | 0 | 0 | 2018-02-10 02:00 | 2 | 7 | 86.6453 | 18.3688 | 2018-02-10 02:00 | 2 | 7 | 32.9252 | 6.9143
2018-02-10 03:00 | 3 | 7 | 86.1677 | 18.1814 | 2018-02-10 03:00 | 3 | 7 | 0 | 0 | 2018-02-10 03:00 | 3 | 7 | 86.7002 | 18.3804 | 2018-02-10 03:00 | 3 | 7 | 32.9461 | 6.9187
2018-02-10 04:00 | 4 | 7 | 86.3081 | 18.211 | 2018-02-10 04:00 | 4 | 7 | 0 | 0 | 2018-02-10 04:00 | 4 | 7 | 86.8513 | 18.4125 | 2018-02-10 04:00 | 4 | 7 | 33.0035 | 6.9307
2018-02-10 05:00 | 5 | 7 | 86.2562 | 18.2001 | 2018-02-10 05:00 | 5 | 7 | 0 | 0 | 2018-02-10 05:00 | 5 | 7 | 86.8605 | 18.4144 | 2018-02-10 05:00 | 5 | 7 | 33.007 | 6.9315
2018-02-10 06:00 | 6 | 7 | 86.1234 | 18.172 | 2018-02-10 06:00 | 6 | 7 | 0 | 0 | 2018-02-10 06:00 | 6 | 7 | 86.6682 | 18.3737 | 2018-02-10 06:00 | 6 | 7 | 32.9339 | 6.9161
2018-02-10 07:00 | 7 | 7 | 86.1906 | 18.1862 | 2018-02-10 07:00 | 7 | 7 | 0 | 0 | 2018-02-10 07:00 | 7 | 7 | 86.7247 | 18.3856 | 2018-02-10 07:00 | 7 | 7 | 32.9554 | 6.9206
2018-02-10 08:00 | 8 | 7 | 86.36 | 18.222 | 2018-02-10 08:00 | 8 | 7 | 0 | 0 | 2018-02-10 08:00 | 8 | 7 | 86.952 | 18.4338 | 2018-02-10 08:00 | 8 | 7 | 33.0418 | 6.9388
2018-02-10 09:00 | 9 | 7 | 86.4912 | 18.2496 | 2018-02-10 09:00 | 9 | 7 | 0 | 0 | 2018-02-10 09:00 | 9 | 7 | 87.0588 | 18.4565 | 2018-02-10 09:00 | 9 | 7 | 33.0823 | 6.9473
2018-02-10 10:00 | 10 | 7 | 86.1982 | 18.1878 | 2018-02-10 10:00 | 10 | 7 | 0 | 0 | 2018-02-10 10:00 | 10 | 7 | 86.6392 | 18.3675 | 2018-02-10 10:00 | 10 | 7 | 32.9229 | 6.9138
2018-02-10 11:00 | 11 | 7 | 86.1707 | 18.182 | 2018-02-10 11:00 | 11 | 7 | 0 | 0 | 2018-02-10 11:00 | 11 | 7 | 86.8849 | 18.4196 | 2018-02-10 11:00 | 11 | 7 | 33.0163 | 6.9334
2018-02-10 12:00 | 12 | 7 | 86.5019 | 18.2519 | 2018-02-10 12:00 | 12 | 7 | 0 | 0 | 2018-02-10 12:00 | 12 | 7 | 87.1504 | 18.4759 | 2018-02-10 12:00 | 12 | 7 | 33.1172 | 6.9546
2018-02-10 13:00 | 13 | 7 | 86.6148 | 18.2757 | 2018-02-10 13:00 | 13 | 7 | 0 | 0 | 2018-02-10 13:00 | 13 | 7 | 87.3167 | 18.5111 | 2018-02-10 13:00 | 13 | 7 | 33.1803 | 6.9679
2018-02-10 14:00 | 14 | 7 | 86.4439 | 18.2397 | 2018-02-10 14:00 | 14 | 7 | 0 | 0 | 2018-02-10 14:00 | 14 | 7 | 87.0832 | 18.4616 | 2018-02-10 14:00 | 14 | 7 | 33.0916 | 6.9492
2018-02-10 15:00 | 15 | 7 | 86.5522 | 18.2625 | 2018-02-10 15:00 | 15 | 7 | 0 | 0 | 2018-02-10 15:00 | 15 | 7 | 87.2938 | 18.5063 | 2018-02-10 15:00 | 15 | 7 | 33.1716 | 6.966
2018-02-10 16:00 | 16 | 7 | 86.5644 | 18.2651 | 2018-02-10 16:00 | 16 | 7 | 0 | 0 | 2018-02-10 16:00 | 16 | 7 | 87.3579 | 18.5199 | 2018-02-10 16:00 | 16 | 7 | 33.196 | 6.9712
2018-02-10 17:00 | 17 | 7 | 86.7445 | 18.3031 | 2018-02-10 17:00 | 17 | 7 | 0 | 0 | 2018-02-10 17:00 | 17 | 7 | 87.57 | 18.5648 | 2018-02-10 17:00 | 17 | 7 | 33.2766 | 6.9881
2018-02-10 18:00 | 18 | 7 | 86.4668 | 18.2445 | 2018-02-10 18:00 | 18 | 7 | 0 | 0 | 2018-02-10 18:00 | 18 | 7 | 87.3014 | 18.5079 | 2018-02-10 18:00 | 18 | 7 | 33.1745 | 6.9667
2018-02-10 19:00 | 19 | 7 | 86.3661 | 18.2232 | 2018-02-10 19:00 | 19 | 7 | 0 | 0 | 2018-02-10 19:00 | 19 | 7 | 87.0954 | 18.4642 | 2018-02-10 19:00 | 19 | 7 | 33.0963 | 6.9502
2018-02-10 20:00 | 20 | 7 | 86.1173 | 18.1708 | 2018-02-10 20:00 | 20 | 7 | 0 | 0 | 2018-02-10 20:00 | 20 | 7 | 86.891 | 18.4209 | 2018-02-10 20:00 | 20 | 7 | 33.0186 | 6.9339
2018-02-10 21:00 | 21 | 7 | 86.1555 | 18.1788 | 2018-02-10 21:00 | 21 | 7 | 0 | 0 | 2018-02-10 21:00 | 21 | 7 | 86.9245 | 18.428 | 2018-02-10 21:00 | 21 | 7 | 33.0313 | 6.9366
2018-02-10 22:00 | 22 | 7 | 86.2211 | 18.1927 | 2018-02-10 22:00 | 22 | 7 | 0 | 0 | 2018-02-10 22:00 | 22 | 7 | 87.0054 | 18.4451 | 2018-02-10 22:00 | 22 | 7 | 33.0621 | 6.943
2018-02-10 23:00 | 23 | 7 | 86.2226 | 18.193 | 2018-02-10 23:00 | 23 | 7 | 0 | 0 | 2018-02-10 23:00 | 23 | 7 | 87.0787 | 18.4607 | 2018-02-10 23:00 | 23 | 7 | 33.0899 | 6.9489
2018-02-11 | 0 | 1 | 86.2364 | 18.1959 | 2018-02-11 | 0 | 1 | 86.7994 | 17.681 | 2018-02-11 | 0 | 1 | 0 | 0 | 2018-02-11 | 0 | 1 | 32.9838 | 6.9266
2018-02-11 01:00 | 1 | 1 | 86.3188 | 18.2133 | 2018-02-11 01:00 | 1 | 1 | 86.952 | 17.7121 | 2018-02-11 01:00 | 1 | 1 | 0 | 0 | 2018-02-11 01:00 | 1 | 1 | 33.0418 | 6.9388
2018-02-11 02:00 | 2 | 1 | 86.2119 | 18.1907 | 2018-02-11 02:00 | 2 | 1 | 86.8177 | 17.6848 | 2018-02-11 02:00 | 2 | 1 | 0 | 0 | 2018-02-11 02:00 | 2 | 1 | 32.9907 | 6.9281
2018-02-11 03:00 | 3 | 1 | 86.1845 | 18.1849 | 2018-02-11 03:00 | 3 | 1 | 86.7857 | 17.6782 | 2018-02-11 03:00 | 3 | 1 | 0 | 0 | 2018-02-11 03:00 | 3 | 1 | 32.9786 | 6.9255
2018-02-11 04:00 | 4 | 1 | 86.2455 | 18.1978 | 2018-02-11 04:00 | 4 | 1 | 86.833 | 17.6879 | 2018-02-11 04:00 | 4 | 1 | 0 | 0 | 2018-02-11 04:00 | 4 | 1 | 32.9965 | 6.9293
2018-02-11 05:00 | 5 | 1 | 86.2333 | 18.1952 | 2018-02-11 05:00 | 5 | 1 | 86.833 | 17.6879 | 2018-02-11 05:00 | 5 | 1 | 0 | 0 | 2018-02-11 05:00 | 5 | 1 | 32.9965 | 6.9293
2018-02-11 06:00 | 6 | 1 | 86.2776 | 18.2046 | 2018-02-11 06:00 | 6 | 1 | 86.8528 | 17.6919 | 2018-02-11 06:00 | 6 | 1 | 0 | 0 | 2018-02-11 06:00 | 6 | 1 | 33.0041 | 6.9309
2018-02-11 07:00 | 7 | 1 | 86.2867 | 18.2065 | 2018-02-11 07:00 | 7 | 1 | 86.8452 | 17.6904 | 2018-02-11 07:00 | 7 | 1 | 0 | 0 | 2018-02-11 07:00 | 7 | 1 | 33.0012 | 6.9302
2018-02-11 08:00 | 8 | 1 | 86.2989 | 18.2091 | 2018-02-11 08:00 | 8 | 1 | 86.9032 | 17.7022 | 2018-02-11 08:00 | 8 | 1 | 0 | 0 | 2018-02-11 08:00 | 8 | 1 | 33.0232 | 6.9349
2018-02-11 09:00 | 9 | 1 | 86.2867 | 18.2065 | 2018-02-11 09:00 | 9 | 1 | 86.8162 | 17.6845 | 2018-02-11 09:00 | 9 | 1 | 0 | 0 | 2018-02-11 09:00 | 9 | 1 | 32.9902 | 6.9279
2018-02-11 10:00 | 10 | 1 | 86.2882 | 18.2068 | 2018-02-11 10:00 | 10 | 1 | 86.8528 | 17.6919 | 2018-02-11 10:00 | 10 | 1 | 0 | 0 | 2018-02-11 10:00 | 10 | 1 | 33.0041 | 6.9309
2018-02-11 11:00 | 11 | 1 | 86.1845 | 18.1849 | 2018-02-11 11:00 | 11 | 1 | 86.743 | 17.6695 | 2018-02-11 11:00 | 11 | 1 | 0 | 0 | 2018-02-11 11:00 | 11 | 1 | 32.9623 | 6.9221
2018-02-11 12:00 | 12 | 1 | 86.1418 | 18.1759 | 2018-02-11 12:00 | 12 | 1 | 86.714 | 17.6636 | 2018-02-11 12:00 | 12 | 1 | 0 | 0 | 2018-02-11 12:00 | 12 | 1 | 32.9513 | 6.9198
2018-02-11 13:00 | 13 | 1 | 86.1479 | 18.1772 | 2018-02-11 13:00 | 13 | 1 | 86.7659 | 17.6742 | 2018-02-11 13:00 | 13 | 1 | 0 | 0 | 2018-02-11 13:00 | 13 | 1 | 32.971 | 6.9239
2018-02-11 14:00 | 14 | 1 | 86.1112 | 18.1695 | 2018-02-11 14:00 | 14 | 1 | 86.7018 | 17.6612 | 2018-02-11 14:00 | 14 | 1 | 0 | 0 | 2018-02-11 14:00 | 14 | 1 | 32.9467 | 6.9188
2018-02-11 15:00 | 15 | 1 | 86.2455 | 18.1978 | 2018-02-11 15:00 | 15 | 1 | 86.8482 | 17.691 | 2018-02-11 15:00 | 15 | 1 | 0 | 0 | 2018-02-11 15:00 | 15 | 1 | 33.0023 | 6.9305
2018-02-11 16:00 | 16 | 1 | 86.3447 | 18.2187 | 2018-02-11 16:00 | 16 | 1 | 86.9398 | 17.7096 | 2018-02-11 16:00 | 16 | 1 | 0 | 0 | 2018-02-11 16:00 | 16 | 1 | 33.0371 | 6.9378
2018-02-11 17:00 | 17 | 1 | 86.4805 | 18.2474 | 2018-02-11 17:00 | 17 | 1 | 86.9856 | 17.719 | 2018-02-11 17:00 | 17 | 1 | 0 | 0 | 2018-02-11 17:00 | 17 | 1 | 33.0545 | 6.9415
2018-02-11 18:00 | 18 | 1 | 86.4332 | 18.2374 | 2018-02-11 18:00 | 18 | 1 | 86.92 | 17.7056 | 2018-02-11 18:00 | 18 | 1 | 0 | 0 | 2018-02-11 18:00 | 18 | 1 | 33.0296 | 6.9362
2018-02-11 19:00 | 19 | 1 | 85.6794 | 18.0784 | 2018-02-11 19:00 | 19 | 1 | 85.9266 | 17.5032 | 2018-02-11 19:00 | 19 | 1 | 0 | 0 | 2018-02-11 19:00 | 19 | 1 | 32.6521 | 6.8569
2018-02-11 20:00 | 20 | 1 | 86.3294 | 18.2155 | 2018-02-11 20:00 | 20 | 1 | 86.5888 | 17.6381 | 2018-02-11 20:00 | 20 | 1 | 0 | 0 | 2018-02-11 20:00 | 20 | 1 | 32.9037 | 6.9098
2018-02-11 21:00 | 21 | 1 | 86.3569 | 18.2213 | 2018-02-11 21:00 | 21 | 1 | 86.6728 | 17.6552 | 2018-02-11 21:00 | 21 | 1 | 0 | 0 | 2018-02-11 21:00 | 21 | 1 | 32.9357 | 6.9165
2018-02-11 22:00 | 22 | 1 | 86.4881 | 18.249 | 2018-02-11 22:00 | 22 | 1 | 86.8086 | 17.6829 | 2018-02-11 22:00 | 22 | 1 | 0 | 0 | 2018-02-11 22:00 | 22 | 1 | 32.9873 | 6.9273
2018-02-11 23:00 | 23 | 1 | 86.4332 | 18.2374 | 2018-02-11 23:00 | 23 | 1 | 86.7353 | 17.668 | 2018-02-11 23:00 | 23 | 1 | 0 | 0 | 2018-02-11 23:00 | 23 | 1 | 32.9594 | 6.9215
2018-02-12 | 0 | 2 | 86.4088 | 18.2323 | 2018-02-12 | 0 | 2 | 86.7002 | 17.6608 | 2018-02-12 | 0 | 2 | 86.9352 | 18.4303 | 2018-02-12 | 0 | 2 | 65.9815 | 13.8561
2018-02-12 01:00 | 1 | 2 | 86.0426 | 18.155 | 2018-02-12 01:00 | 1 | 2 | 86.3127 | 17.5819 | 2018-02-12 01:00 | 1 | 2 | 86.5278 | 18.3439 | 2018-02-12 01:00 | 1 | 2 | 65.6794 | 13.7927
2018-02-12 02:00 | 2 | 2 | 86.392 | 18.2287 | 2018-02-12 02:00 | 2 | 2 | 86.6392 | 17.6484 | 2018-02-12 02:00 | 2 | 2 | 86.8421 | 18.4105 | 2018-02-12 02:00 | 2 | 2 | 65.9229 | 13.8438
2018-02-12 03:00 | 3 | 2 | 86.2776 | 18.2046 | 2018-02-12 03:00 | 3 | 2 | 86.5766 | 17.6357 | 2018-02-12 03:00 | 3 | 2 | 86.7536 | 18.3918 | 2018-02-12 03:00 | 3 | 2 | 65.8655 | 13.8317
2018-02-12 04:00 | 4 | 2 | 86.5034 | 18.2522 | 2018-02-12 04:00 | 4 | 2 | 86.8849 | 17.6985 | 2018-02-12 04:00 | 4 | 2 | 87.0283 | 18.45 | 2018-02-12 04:00 | 4 | 2 | 66.087 | 13.8783
2018-02-12 05:00 | 5 | 2 | 86.3661 | 18.2232 | 2018-02-12 05:00 | 5 | 2 | 86.772 | 17.6755 | 2018-02-12 05:00 | 5 | 2 | 87.0054 | 18.4451 | 2018-02-12 05:00 | 5 | 2 | 66.0354 | 13.8674
2018-02-12 06:00 | 6 | 2 | 86.2898 | 18.2071 | 2018-02-12 06:00 | 6 | 2 | 86.6499 | 17.6506 | 2018-02-12 06:00 | 6 | 2 | 86.8147 | 18.4047 | 2018-02-12 06:00 | 6 | 2 | 65.9165 | 13.8425
2018-02-12 07:00 | 7 | 2 | 86.2043 | 18.1891 | 2018-02-12 07:00 | 7 | 2 | 86.5278 | 17.6257 | 2018-02-12 07:00 | 7 | 2 | 86.7079 | 18.3821 | 2018-02-12 07:00 | 7 | 2 | 65.8296 | 13.8242
2018-02-12 08:00 | 8 | 2 | 86.3355 | 18.2168 | 2018-02-12 08:00 | 8 | 2 | 86.5461 | 17.6294 | 2018-02-12 08:00 | 8 | 2 | 86.8025 | 18.4021 | 2018-02-12 08:00 | 8 | 2 | 65.8725 | 13.8332
2018-02-12 09:00 | 9 | 2 | 86.3798 | 18.2261 | 2018-02-12 09:00 | 9 | 2 | 86.7262 | 17.6661 | 2018-02-12 09:00 | 9 | 2 | 86.8711 | 18.4167 | 2018-02-12 09:00 | 9 | 2 | 65.967 | 13.8531
2018-02-12 10:00 | 10 | 2 | 86.2272 | 18.1939 | 2018-02-12 10:00 | 10 | 2 | 86.5156 | 17.6232 | 2018-02-12 10:00 | 10 | 2 | 86.714 | 18.3834 | 2018-02-12 10:00 | 10 | 2 | 65.8272 | 13.8237
2018-02-12 11:00 | 11 | 2 | 86.2119 | 18.1907 | 2018-02-12 11:00 | 11 | 2 | 86.5141 | 17.6229 | 2018-02-12 11:00 | 11 | 2 | 86.7201 | 18.3847 | 2018-02-12 11:00 | 11 | 2 | 65.829 | 13.8241
2018-02-12 12:00 | 12 | 2 | 86.389 | 18.2281 | 2018-02-12 12:00 | 12 | 2 | 86.6835 | 17.6574 | 2018-02-12 12:00 | 12 | 2 | 86.8574 | 18.4138 | 2018-02-12 12:00 | 12 | 2 | 65.9455 | 13.8486
2018-02-12 13:00 | 13 | 2 | 86.4027 | 18.231 | 2018-02-12 13:00 | 13 | 2 | 86.6224 | 17.645 | 2018-02-12 13:00 | 13 | 2 | 86.7475 | 18.3905 | 2018-02-12 13:00 | 13 | 2 | 65.8806 | 13.8349
2018-02-12 14:00 | 14 | 2 | 86.3783 | 18.2258 | 2018-02-12 14:00 | 14 | 2 | 86.6606 | 17.6528 | 2018-02-12 14:00 | 14 | 2 | 86.7903 | 18.3995 | 2018-02-12 14:00 | 14 | 2 | 65.9113 | 13.8414
2018-02-12 15:00 | 15 | 2 | 86.3355 | 18.2168 | 2018-02-12 15:00 | 15 | 2 | 86.5248 | 17.6251 | 2018-02-12 15:00 | 15 | 2 | 86.7384 | 18.3885 | 2018-02-12 15:00 | 15 | 2 | 65.84 | 13.8264
2018-02-12 16:00 | 16 | 2 | 86.3493 | 18.2197 | 2018-02-12 16:00 | 16 | 2 | 86.4912 | 17.6183 | 2018-02-12 16:00 | 16 | 2 | 86.685 | 18.3772 | 2018-02-12 16:00 | 16 | 2 | 65.807 | 13.8195
2018-02-12 17:00 | 17 | 2 | 86.244 | 18.1975 | 2018-02-12 17:00 | 17 | 2 | 86.4683 | 17.6136 | 2018-02-12 17:00 | 17 | 2 | 86.6743 | 18.375 | 2018-02-12 17:00 | 17 | 2 | 65.7942 | 13.8168
2018-02-12 18:00 | 18 | 2 | 86.3142 | 18.2123 | 2018-02-12 18:00 | 18 | 2 | 86.4378 | 17.6074 | 2018-02-12 18:00 | 18 | 2 | 86.5934 | 18.3578 | 2018-02-12 18:00 | 18 | 2 | 65.7519 | 13.8079
2018-02-12 19:00 | 19 | 2 | 86.2089 | 18.1901 | 2018-02-12 19:00 | 19 | 2 | 86.3508 | 17.5897 | 2018-02-12 19:00 | 19 | 2 | 86.5583 | 18.3504 | 2018-02-12 19:00 | 19 | 2 | 65.7055 | 13.7981
2018-02-12 20:00 | 20 | 2 | 86.2181 | 18.192 | 2018-02-12 20:00 | 20 | 2 | 86.4836 | 17.6167 | 2018-02-12 20:00 | 20 | 2 | 86.6896 | 18.3782 | 2018-02-12 20:00 | 20 | 2 | 65.8058 | 13.8192
2018-02-12 21:00 | 21 | 2 | 86.1494 | 18.1775 | 2018-02-12 21:00 | 21 | 2 | 86.4759 | 17.6151 | 2018-02-12 21:00 | 21 | 2 | 86.63 | 18.3656 | 2018-02-12 21:00 | 21 | 2 | 65.7802 | 13.8139
2018-02-12 22:00 | 22 | 2 | 86.2593 | 18.2007 | 2018-02-12 22:00 | 22 | 2 | 86.5522 | 17.6307 | 2018-02-12 22:00 | 22 | 2 | 86.6468 | 18.3691 | 2018-02-12 22:00 | 22 | 2 | 65.8156 | 13.8213
2018-02-12 23:00 | 23 | 2 | 86.4424 | 18.2393 | 2018-02-12 23:00 | 23 | 2 | 86.8055 | 17.6823 | 2018-02-12 23:00 | 23 | 2 | 86.8864 | 18.4199 | 2018-02-12 23:00 | 23 | 2 | 66.0029 | 13.8606
2018-02-13 | 0 | 3 | 86.4637 | 18.2438 | 2018-02-13 | 0 | 3 | 0 | 0 | 2018-02-13 | 0 | 3 | 0 | 0 | 2018-02-13 | 0 | 3 | 0 | 0
2018-02-13 01:00 | 1 | 3 | 86.5629 | 18.2648 | 2018-02-13 01:00 | 1 | 3 | 0 | 0 | 2018-02-13 01:00 | 1 | 3 | 0 | 0 | 2018-02-13 01:00 | 1 | 3 | 0 | 0
2018-02-13 02:00 | 2 | 3 | 86.3706 | 18.2242 | 2018-02-13 02:00 | 2 | 3 | 0 | 0 | 2018-02-13 02:00 | 2 | 3 | 0 | 0 | 2018-02-13 02:00 | 2 | 3 | 0 | 0
2018-02-13 03:00 | 3 | 3 | 86.3523 | 18.2203 | 2018-02-13 03:00 | 3 | 3 | 0 | 0 | 2018-02-13 03:00 | 3 | 3 | 0 | 0 | 2018-02-13 03:00 | 3 | 3 | 0 | 0
2018-02-13 04:00 | 4 | 3 | 86.3676 | 18.2236 | 2018-02-13 04:00 | 4 | 3 | 0 | 0 | 2018-02-13 04:00 | 4 | 3 | 0 | 0 | 2018-02-13 04:00 | 4 | 3 | 0 | 0
2018-02-13 05:00 | 5 | 3 | 86.4027 | 18.231 | 2018-02-13 05:00 | 5 | 3 | 0 | 0 | 2018-02-13 05:00 | 5 | 3 | 0 | 0 | 2018-02-13 05:00 | 5 | 3 | 0 | 0
2018-02-13 06:00 | 6 | 3 | 86.4652 | 18.2442 | 2018-02-13 06:00 | 6 | 3 | 0 | 0 | 2018-02-13 06:00 | 6 | 3 | 0 | 0 | 2018-02-13 06:00 | 6 | 3 | 0 | 0
2018-02-13 07:00 | 7 | 3 | 86.4012 | 18.2307 | 2018-02-13 07:00 | 7 | 3 | 0 | 0 | 2018-02-13 07:00 | 7 | 3 | 0 | 0 | 2018-02-13 07:00 | 7 | 3 | 0 | 0
2018-02-13 08:00 | 8 | 3 | 86.4515 | 18.2413 | 2018-02-13 08:00 | 8 | 3 | 0 | 0 | 2018-02-13 08:00 | 8 | 3 | 0 | 0 | 2018-02-13 08:00 | 8 | 3 | 0 | 0
2018-02-13 09:00 | 9 | 3 | 86.2028 | 18.1888 | 2018-02-13 09:00 | 9 | 3 | 0 | 0 | 2018-02-13 09:00 | 9 | 3 | 0 | 0 | 2018-02-13 09:00 | 9 | 3 | 0 | 0
2018-02-13 10:00 | 10 | 3 | 86.2715 | 18.2033 | 2018-02-13 10:00 | 10 | 3 | 0 | 0 | 2018-02-13 10:00 | 10 | 3 | 0 | 0 | 2018-02-13 10:00 | 10 | 3 | 0 | 0
2018-02-13 11:00 | 11 | 3 | 86.7567 | 18.3057 | 2018-02-13 11:00 | 11 | 3 | 0 | 0 | 2018-02-13 11:00 | 11 | 3 | 0 | 0 | 2018-02-13 11:00 | 11 | 3 | 0 | 0
2018-02-13 12:00 | 12 | 3 | 86.6194 | 18.2767 | 2018-02-13 12:00 | 12 | 3 | 0 | 0 | 2018-02-13 12:00 | 12 | 3 | 0 | 0 | 2018-02-13 12:00 | 12 | 3 | 0 | 0
2018-02-13 13:00 | 13 | 3 | 86.6377 | 18.2806 | 2018-02-13 13:00 | 13 | 3 | 0 | 0 | 2018-02-13 13:00 | 13 | 3 | 0 | 0 | 2018-02-13 13:00 | 13 | 3 | 0 | 0
2018-02-13 14:00 | 14 | 3 | 86.8757 | 18.3308 | 2018-02-13 14:00 | 14 | 3 | 0 | 0 | 2018-02-13 14:00 | 14 | 3 | 0 | 0 | 2018-02-13 14:00 | 14 | 3 | 0 | 0
2018-02-13 15:00 | 15 | 3 | 86.7994 | 18.3147 | 2018-02-13 15:00 | 15 | 3 | 0 | 0 | 2018-02-13 15:00 | 15 | 3 | 0 | 0 | 2018-02-13 15:00 | 15 | 3 | 0 | 0
2018-02-13 16:00 | 16 | 3 | 86.7674 | 18.3079 | 2018-02-13 16:00 | 16 | 3 | 0 | 0 | 2018-02-13 16:00 | 16 | 3 | 0 | 0 | 2018-02-13 16:00 | 16 | 3 | 0 | 0
2018-02-13 17:00 | 17 | 3 | 86.7384 | 18.3018 | 2018-02-13 17:00 | 17 | 3 | 0 | 0 | 2018-02-13 17:00 | 17 | 3 | 0 | 0 | 2018-02-13 17:00 | 17 | 3 | 0 | 0
2018-02-13 18:00 | 18 | 3 | 86.7124 | 18.2963 | 2018-02-13 18:00 | 18 | 3 | 0 | 0 | 2018-02-13 18:00 | 18 | 3 | 0 | 0 | 2018-02-13 18:00 | 18 | 3 | 0 | 0
2018-02-13 19:00 | 19 | 3 | 86.8376 | 18.3227 | 2018-02-13 19:00 | 19 | 3 | 0 | 0 | 2018-02-13 19:00 | 19 | 3 | 0 | 0 | 2018-02-13 19:00 | 19 | 3 | 0 | 0
2018-02-13 20:00 | 20 | 3 | 86.627 | 18.2783 | 2018-02-13 20:00 | 20 | 3 | 0 | 0 | 2018-02-13 20:00 | 20 | 3 | 0 | 0 | 2018-02-13 20:00 | 20 | 3 | 0 | 0
2018-02-13 21:00 | 21 | 3 | 86.6239 | 18.2776 | 2018-02-13 21:00 | 21 | 3 | 0 | 0 | 2018-02-13 21:00 | 21 | 3 | 0 | 0 | 2018-02-13 21:00 | 21 | 3 | 0 | 0
2018-02-13 22:00 | 22 | 3 | 86.714 | 18.2967 | 2018-02-13 22:00 | 22 | 3 | 0 | 0 | 2018-02-13 22:00 | 22 | 3 | 0 | 0 | 2018-02-13 22:00 | 22 | 3 | 0 | 0
2018-02-13 23:00 | 23 | 3 | 86.8971 | 18.3353 | 2018-02-13 23:00 | 23 | 3 | 0 | 0 | 2018-02-13 23:00 | 23 | 3 | 0 | 0 | 2018-02-13 23:00 | 23 | 3 | 0 | 0
2018-02-14 | 0 | 4 | 0 | 0 | 2018-02-14 | 0 | 4 | 0 | 0 | 2018-02-14 | 0 | 4 | 86.6712 | 18.3743 | 2018-02-14 | 0 | 4 | 32.9351 | 6.9164
2018-02-14 01:00 | 1 | 4 | 0 | 0 | 2018-02-14 01:00 | 1 | 4 | 0 | 0 | 2018-02-14 01:00 | 1 | 4 | 86.511 | 18.3403 | 2018-02-14 01:00 | 1 | 4 | 32.8742 | 6.9036
2018-02-14 02:00 | 2 | 4 | 0 | 0 | 2018-02-14 02:00 | 2 | 4 | 0 | 0 | 2018-02-14 02:00 | 2 | 4 | 86.7628 | 18.3937 | 2018-02-14 02:00 | 2 | 4 | 32.9699 | 6.9237
2018-02-14 03:00 | 3 | 4 | 0 | 0 | 2018-02-14 03:00 | 3 | 4 | 0 | 0 | 2018-02-14 03:00 | 3 | 4 | 86.7384 | 18.3885 | 2018-02-14 03:00 | 3 | 4 | 32.9606 | 6.9217
2018-02-14 04:00 | 4 | 4 | 0 | 0 | 2018-02-14 04:00 | 4 | 4 | 0 | 0 | 2018-02-14 04:00 | 4 | 4 | 86.8376 | 18.4096 | 2018-02-14 04:00 | 4 | 4 | 32.9983 | 6.9296
2018-02-14 05:00 | 5 | 4 | 0 | 0 | 2018-02-14 05:00 | 5 | 4 | 0 | 0 | 2018-02-14 05:00 | 5 | 4 | 87.0222 | 18.4487 | 2018-02-14 05:00 | 5 | 4 | 33.0684 | 6.9444
2018-02-14 06:00 | 6 | 4 | 0 | 0 | 2018-02-14 06:00 | 6 | 4 | 0 | 0 | 2018-02-14 06:00 | 6 | 4 | 86.9627 | 18.4361 | 2018-02-14 06:00 | 6 | 4 | 33.0458 | 6.9396
2018-02-14 07:00 | 7 | 4 | 0 | 0 | 2018-02-14 07:00 | 7 | 4 | 0 | 0 | 2018-02-14 07:00 | 7 | 4 | 87.1321 | 18.472 | 2018-02-14 07:00 | 7 | 4 | 33.1102 | 6.9531
2018-02-14 08:00 | 8 | 4 | 0 | 0 | 2018-02-14 08:00 | 8 | 4 | 0 | 0 | 2018-02-14 08:00 | 8 | 4 | 87.1931 | 18.4849 | 2018-02-14 08:00 | 8 | 4 | 33.1334 | 6.958
2018-02-14 09:00 | 9 | 4 | 0 | 0 | 2018-02-14 09:00 | 9 | 4 | 0 | 0 | 2018-02-14 09:00 | 9 | 4 | 86.7155 | 18.3837 | 2018-02-14 09:00 | 9 | 4 | 32.9519 | 6.9199
2018-02-14 10:00 | 10 | 4 | 0 | 0 | 2018-02-14 10:00 | 10 | 4 | 0 | 0 | 2018-02-14 10:00 | 10 | 4 | 86.6743 | 18.375 | 2018-02-14 10:00 | 10 | 4 | 32.9362 | 6.9166
2018-02-14 11:00 | 11 | 4 | 0 | 0 | 2018-02-14 11:00 | 11 | 4 | 0 | 0 | 2018-02-14 11:00 | 11 | 4 | 86.8956 | 18.4219 | 2018-02-14 11:00 | 11 | 4 | 33.0203 | 6.9343
2018-02-14 12:00 | 12 | 4 | 0 | 0 | 2018-02-14 12:00 | 12 | 4 | 0 | 0 | 2018-02-14 12:00 | 12 | 4 | 86.9276 | 18.4287 | 2018-02-14 12:00 | 12 | 4 | 33.0325 | 6.9368
2018-02-14 13:00 | 13 | 4 | 0 | 0 | 2018-02-14 13:00 | 13 | 4 | 0 | 0 | 2018-02-14 13:00 | 13 | 4 | 87.2541 | 18.4979 | 2018-02-14 13:00 | 13 | 4 | 33.1566 | 6.9629
2018-02-14 14:00 | 14 | 4 | 0 | 0 | 2018-02-14 14:00 | 14 | 4 | 0 | 0 | 2018-02-14 14:00 | 14 | 4 | 87.4037 | 18.5296 | 2018-02-14 14:00 | 14 | 4 | 33.2134 | 6.9748
2018-02-14 15:00 | 15 | 4 | 0 | 0 | 2018-02-14 15:00 | 15 | 4 | 0 | 0 | 2018-02-14 15:00 | 15 | 4 | 87.2129 | 18.4891 | 2018-02-14 15:00 | 15 | 4 | 33.1409 | 6.9596
2018-02-14 16:00 | 16 | 4 | 0 | 0 | 2018-02-14 16:00 | 16 | 4 | 0 | 0 | 2018-02-14 16:00 | 16 | 4 | 86.9718 | 18.438 | 2018-02-14 16:00 | 16 | 4 | 33.0493 | 6.9403
2018-02-14 17:00 | 17 | 4 | 0 | 0 | 2018-02-14 17:00 | 17 | 4 | 0 | 0 | 2018-02-14 17:00 | 17 | 4 | 87.1397 | 18.4736 | 2018-02-14 17:00 | 17 | 4 | 33.1131 | 6.9537
2018-02-14 18:00 | 18 | 4 | 0 | 0 | 2018-02-14 18:00 | 18 | 4 | 0 | 0 | 2018-02-14 18:00 | 18 | 4 | 87.2435 | 18.4956 | 2018-02-14 18:00 | 18 | 4 | 33.1525 | 6.962
2018-02-14 19:00 | 19 | 4 | 0 | 0 | 2018-02-14 19:00 | 19 | 4 | 0 | 0 | 2018-02-14 19:00 | 19 | 4 | 86.8894 | 18.4206 | 2018-02-14 19:00 | 19 | 4 | 33.018 | 6.9338
2018-02-14 20:00 | 20 | 4 | 0 | 0 | 2018-02-14 20:00 | 20 | 4 | 0 | 0 | 2018-02-14 20:00 | 20 | 4 | 87.1839 | 18.483 | 2018-02-14 20:00 | 20 | 4 | 33.1299 | 6.9573
2018-02-14 21:00 | 21 | 4 | 0 | 0 | 2018-02-14 21:00 | 21 | 4 | 0 | 0 | 2018-02-14 21:00 | 21 | 4 | 87.2419 | 18.4953 | 2018-02-14 21:00 | 21 | 4 | 33.1519 | 6.9619
2018-02-14 22:00 | 22 | 4 | 0 | 0 | 2018-02-14 22:00 | 22 | 4 | 0 | 0 | 2018-02-14 22:00 | 22 | 4 | 87.1733 | 18.4807 | 2018-02-14 22:00 | 22 | 4 | 33.1259 | 6.9564
2018-02-14 23:00 | 23 | 4 | 0 | 0 | 2018-02-14 23:00 | 23 | 4 | 0 | 0 | 2018-02-14 23:00 | 23 | 4 | 87.2557 | 18.4982 | 2018-02-14 23:00 | 23 | 4 | 33.1572 | 6.963
2018-02-15 | 0 | 5 | 86.5492 | 18.2619 | 2018-02-15 | 0 | 5 | 0 | 0 | 2018-02-15 | 0 | 5 | 0 | 0 | 2018-02-15 | 0 | 5 | 0 | 0
2018-02-15 01:00 | 1 | 5 | 86.7201 | 18.2979 | 2018-02-15 01:00 | 1 | 5 | 0 | 0 | 2018-02-15 01:00 | 1 | 5 | 0 | 0 | 2018-02-15 01:00 | 1 | 5 | 0 | 0
2018-02-15 02:00 | 2 | 5 | 86.5095 | 18.2535 | 2018-02-15 02:00 | 2 | 5 | 0 | 0 | 2018-02-15 02:00 | 2 | 5 | 0 | 0 | 2018-02-15 02:00 | 2 | 5 | 0 | 0
2018-02-15 03:00 | 3 | 5 | 86.4576 | 18.2426 | 2018-02-15 03:00 | 3 | 5 | 0 | 0 | 2018-02-15 03:00 | 3 | 5 | 0 | 0 | 2018-02-15 03:00 | 3 | 5 | 0 | 0
2018-02-15 04:00 | 4 | 5 | 86.6316 | 18.2793 | 2018-02-15 04:00 | 4 | 5 | 0 | 0 | 2018-02-15 04:00 | 4 | 5 | 0 | 0 | 2018-02-15 04:00 | 4 | 5 | 0 | 0
2018-02-15 05:00 | 5 | 5 | 86.569 | 18.2661 | 2018-02-15 05:00 | 5 | 5 | 0 | 0 | 2018-02-15 05:00 | 5 | 5 | 0 | 0 | 2018-02-15 05:00 | 5 | 5 | 0 | 0
2018-02-15 06:00 | 6 | 5 | 86.6468 | 18.2825 | 2018-02-15 06:00 | 6 | 5 | 0 | 0 | 2018-02-15 06:00 | 6 | 5 | 0 | 0 | 2018-02-15 06:00 | 6 | 5 | 0 | 0
2018-02-15 07:00 | 7 | 5 | 86.6361 | 18.2802 | 2018-02-15 07:00 | 7 | 5 | 0 | 0 | 2018-02-15 07:00 | 7 | 5 | 0 | 0 | 2018-02-15 07:00 | 7 | 5 | 0 | 0
2018-02-15 08:00 | 8 | 5 | 86.6819 | 18.2899 | 2018-02-15 08:00 | 8 | 5 | 0 | 0 | 2018-02-15 08:00 | 8 | 5 | 0 | 0 | 2018-02-15 08:00 | 8 | 5 | 0 | 0
2018-02-15 09:00 | 9 | 5 | 86.7094 | 18.2957 | 2018-02-15 09:00 | 9 | 5 | 0 | 0 | 2018-02-15 09:00 | 9 | 5 | 0 | 0 | 2018-02-15 09:00 | 9 | 5 | 0 | 0
2018-02-15 10:00 | 10 | 5 | 86.7933 | 18.3134 | 2018-02-15 10:00 | 10 | 5 | 0 | 0 | 2018-02-15 10:00 | 10 | 5 | 0 | 0 | 2018-02-15 10:00 | 10 | 5 | 0 | 0
2018-02-15 11:00 | 11 | 5 | 86.8009 | 18.315 | 2018-02-15 11:00 | 11 | 5 | 0 | 0 | 2018-02-15 11:00 | 11 | 5 | 0 | 0 | 2018-02-15 11:00 | 11 | 5 | 0 | 0
2018-02-15 12:00 | 12 | 5 | 86.6728 | 18.288 | 2018-02-15 12:00 | 12 | 5 | 0 | 0 | 2018-02-15 12:00 | 12 | 5 | 0 | 0 | 2018-02-15 12:00 | 12 | 5 | 0 | 0
2018-02-15 13:00 | 13 | 5 | 86.6316 | 18.2793 | 2018-02-15 13:00 | 13 | 5 | 0 | 0 | 2018-02-15 13:00 | 13 | 5 | 0 | 0 | 2018-02-15 13:00 | 13 | 5 | 0 | 0
2018-02-15 14:00 | 14 | 5 | 86.6316 | 18.2793 | 2018-02-15 14:00 | 14 | 5 | 0 | 0 | 2018-02-15 14:00 | 14 | 5 | 0 | 0 | 2018-02-15 14:00 | 14 | 5 | 0 | 0
2018-02-15 15:00 | 15 | 5 | 86.6636 | 18.286 | 2018-02-15 15:00 | 15 | 5 | 0 | 0 | 2018-02-15 15:00 | 15 | 5 | 0 | 0 | 2018-02-15 15:00 | 15 | 5 | 0 | 0
2018-02-15 16:00 | 16 | 5 | 86.5568 | 18.2635 | 2018-02-15 16:00 | 16 | 5 | 0 | 0 | 2018-02-15 16:00 | 16 | 5 | 0 | 0 | 2018-02-15 16:00 | 16 | 5 | 0 | 0
2018-02-15 17:00 | 17 | 5 | 86.6865 | 18.2909 | 2018-02-15 17:00 | 17 | 5 | 0 | 0 | 2018-02-15 17:00 | 17 | 5 | 0 | 0 | 2018-02-15 17:00 | 17 | 5 | 0 | 0
2018-02-15 18:00 | 18 | 5 | 86.7262 | 18.2992 | 2018-02-15 18:00 | 18 | 5 | 0 | 0 | 2018-02-15 18:00 | 18 | 5 | 0 | 0 | 2018-02-15 18:00 | 18 | 5 | 0 | 0
2018-02-15 19:00 | 19 | 5 | 86.5187 | 18.2554 | 2018-02-15 19:00 | 19 | 5 | 0 | 0 | 2018-02-15 19:00 | 19 | 5 | 0 | 0 | 2018-02-15 19:00 | 19 | 5 | 0 | 0
2018-02-15 20:00 | 20 | 5 | 86.5766 | 18.2677 | 2018-02-15 20:00 | 20 | 5 | 0 | 0 | 2018-02-15 20:00 | 20 | 5 | 0 | 0 | 2018-02-15 20:00 | 20 | 5 | 0 | 0
2018-02-15 21:00 | 21 | 5 | 86.6194 | 18.2767 | 2018-02-15 21:00 | 21 | 5 | 0 | 0 | 2018-02-15 21:00 | 21 | 5 | 0 | 0 | 2018-02-15 21:00 | 21 | 5 | 0 | 0
2018-02-15 22:00 | 22 | 5 | 86.6743 | 18.2883 | 2018-02-15 22:00 | 22 | 5 | 0 | 0 | 2018-02-15 22:00 | 22 | 5 | 0 | 0 | 2018-02-15 22:00 | 22 | 5 | 0 | 0
2018-02-15 23:00 | 23 | 5 | 86.5644 | 18.2651 | 2018-02-15 23:00 | 23 | 5 | 0 | 0 | 2018-02-15 23:00 | 23 | 5 | 0 | 0 | 2018-02-15 23:00 | 23 | 5 | 0 | 0
2018-02-16 | 0 | 6 | 86.2226 | 18.193 | 2018-02-16 | 0 | 6 | 86.688 | 17.6583 | 2018-02-16 | 0 | 6 | 0 | 0 | 2018-02-16 | 0 | 6 | 32.9414 | 6.9177
2018-02-16 01:00 | 1 | 6 | 86.1128 | 18.1698 | 2018-02-16 01:00 | 1 | 6 | 86.5232 | 17.6248 | 2018-02-16 01:00 | 1 | 6 | 0 | 0 | 2018-02-16 01:00 | 1 | 6 | 32.8788 | 6.9046
2018-02-16 02:00 | 2 | 6 | 86.2791 | 18.2049 | 2018-02-16 02:00 | 2 | 6 | 86.6896 | 17.6587 | 2018-02-16 02:00 | 2 | 6 | 0 | 0 | 2018-02-16 02:00 | 2 | 6 | 32.942 | 6.9178
2018-02-16 03:00 | 3 | 6 | 86.0014 | 18.1463 | 2018-02-16 03:00 | 3 | 6 | 86.4485 | 17.6096 | 2018-02-16 03:00 | 3 | 6 | 0 | 0 | 2018-02-16 03:00 | 3 | 6 | 32.8504 | 6.8986
2018-02-16 04:00 | 4 | 6 | 86.0533 | 18.1572 | 2018-02-16 04:00 | 4 | 6 | 86.4347 | 17.6067 | 2018-02-16 04:00 | 4 | 6 | 0 | 0 | 2018-02-16 04:00 | 4 | 6 | 32.8452 | 6.8975
2018-02-16 05:00 | 5 | 6 | 86.2257 | 18.1936 | 2018-02-16 05:00 | 5 | 6 | 86.6117 | 17.6428 | 2018-02-16 05:00 | 5 | 6 | 0 | 0 | 2018-02-16 05:00 | 5 | 6 | 32.9124 | 6.9116
2018-02-16 06:00 | 6 | 6 | 86.4332 | 18.2374 | 2018-02-16 06:00 | 6 | 6 | 86.9352 | 17.7087 | 2018-02-16 06:00 | 6 | 6 | 0 | 0 | 2018-02-16 06:00 | 6 | 6 | 33.0354 | 6.9374
2018-02-16 07:00 | 7 | 6 | 86.5873 | 18.2699 | 2018-02-16 07:00 | 7 | 6 | 87.0619 | 17.7345 | 2018-02-16 07:00 | 7 | 6 | 0 | 0 | 2018-02-16 07:00 | 7 | 6 | 33.0835 | 6.9475
2018-02-16 08:00 | 8 | 6 | 86.3691 | 18.2239 | 2018-02-16 08:00 | 8 | 6 | 86.7811 | 17.6773 | 2018-02-16 08:00 | 8 | 6 | 0 | 0 | 2018-02-16 08:00 | 8 | 6 | 32.9768 | 6.9251
2018-02-16 09:00 | 9 | 6 | 86.334 | 18.2165 | 2018-02-16 09:00 | 9 | 6 | 86.7399 | 17.6689 | 2018-02-16 09:00 | 9 | 6 | 0 | 0 | 2018-02-16 09:00 | 9 | 6 | 32.9612 | 6.9218
2018-02-16 10:00 | 10 | 6 | 86.5126 | 18.2542 | 2018-02-16 10:00 | 10 | 6 | 86.862 | 17.6938 | 2018-02-16 10:00 | 10 | 6 | 0 | 0 | 2018-02-16 10:00 | 10 | 6 | 33.0076 | 6.9316
2018-02-16 11:00 | 11 | 6 | 86.5003 | 18.2516 | 2018-02-16 11:00 | 11 | 6 | 86.9306 | 17.7078 | 2018-02-16 11:00 | 11 | 6 | 0 | 0 | 2018-02-16 11:00 | 11 | 6 | 33.0336 | 6.9371
2018-02-16 12:00 | 12 | 6 | 86.7002 | 18.2937 | 2018-02-16 12:00 | 12 | 6 | 87.1412 | 17.7507 | 2018-02-16 12:00 | 12 | 6 | 0 | 0 | 2018-02-16 12:00 | 12 | 6 | 33.1137 | 6.9539
2018-02-16 13:00 | 13 | 6 | 86.363 | 18.2226 | 2018-02-16 13:00 | 13 | 6 | 86.8009 | 17.6813 | 2018-02-16 13:00 | 13 | 6 | 0 | 0 | 2018-02-16 13:00 | 13 | 6 | 32.9843 | 6.9267
2018-02-16 14:00 | 14 | 6 | 86.4408 | 18.239 | 2018-02-16 14:00 | 14 | 6 | 86.8635 | 17.6941 | 2018-02-16 14:00 | 14 | 6 | 0 | 0 | 2018-02-16 14:00 | 14 | 6 | 33.0081 | 6.9317
2018-02-16 15:00 | 15 | 6 | 86.2943 | 18.2081 | 2018-02-16 15:00 | 15 | 6 | 86.6743 | 17.6556 | 2018-02-16 15:00 | 15 | 6 | 0 | 0 | 2018-02-16 15:00 | 15 | 6 | 32.9362 | 6.9166
2018-02-16 16:00 | 16 | 6 | 86.3706 | 18.2242 | 2018-02-16 16:00 | 16 | 6 | 86.7491 | 17.6708 | 2018-02-16 16:00 | 16 | 6 | 0 | 0 | 2018-02-16 16:00 | 16 | 6 | 32.9647 | 6.9226
2018-02-16 17:00 | 17 | 6 | 86.2882 | 18.2068 | 2018-02-16 17:00 | 17 | 6 | 86.7445 | 17.6699 | 2018-02-16 17:00 | 17 | 6 | 0 | 0 | 2018-02-16 17:00 | 17 | 6 | 32.9629 | 6.9222
2018-02-16 18:00 | 18 | 6 | 86.1875 | 18.1856 | 2018-02-16 18:00 | 18 | 6 | 86.6667 | 17.654 | 2018-02-16 18:00 | 18 | 6 | 0 | 0 | 2018-02-16 18:00 | 18 | 6 | 32.9333 | 6.916
2018-02-16 19:00 | 19 | 6 | 86.099 | 18.1669 | 2018-02-16 19:00 | 19 | 6 | 86.5431 | 17.6288 | 2018-02-16 19:00 | 19 | 6 | 0 | 0 | 2018-02-16 19:00 | 19 | 6 | 32.8864 | 6.9061
2018-02-16 20:00 | 20 | 6 | 86.1997 | 18.1881 | 2018-02-16 20:00 | 20 | 6 | 86.5187 | 17.6239 | 2018-02-16 20:00 | 20 | 6 | 0 | 0 | 2018-02-16 20:00 | 20 | 6 | 32.8771 | 6.9042
2018-02-16 21:00 | 21 | 6 | 86.3767 | 18.2255 | 2018-02-16 21:00 | 21 | 6 | 86.7247 | 17.6658 | 2018-02-16 21:00 | 21 | 6 | 0 | 0 | 2018-02-16 21:00 | 21 | 6 | 32.9554 | 6.9206
2018-02-16 22:00 | 22 | 6 | 86.3691 | 18.2239 | 2018-02-16 22:00 | 22 | 6 | 86.7659 | 17.6742 | 2018-02-16 22:00 | 22 | 6 | 0 | 0 | 2018-02-16 22:00 | 22 | 6 | 32.971 | 6.9239
2018-02-16 23:00 | 23 | 6 | 86.4012 | 18.2307 | 2018-02-16 23:00 | 23 | 6 | 86.7918 | 17.6795 | 2018-02-16 23:00 | 23 | 6 | 0 | 0 | 2018-02-16 23:00 | 23 | 6 | 32.9809 | 6.926
2018-02-17 | 0 | 7 | 86.0121 | 18.1486 | 2018-02-17 | 0 | 7 | 0 | 0 | 2018-02-17 | 0 | 7 | 86.5507 | 18.3487 | 2018-02-17 | 0 | 7 | 32.8893 | 6.9067
2018-02-17 01:00 | 1 | 7 | 85.919 | 18.1289 | 2018-02-17 01:00 | 1 | 7 | 0 | 0 | 2018-02-17 01:00 | 1 | 7 | 86.5324 | 18.3449 | 2018-02-17 01:00 | 1 | 7 | 32.8823 | 6.9053
2018-02-17 02:00 | 2 | 7 | 86.0533 | 18.1572 | 2018-02-17 02:00 | 2 | 7 | 0 | 0 | 2018-02-17 02:00 | 2 | 7 | 86.6453 | 18.3688 | 2018-02-17 02:00 | 2 | 7 | 32.9252 | 6.9143
2018-02-17 03:00 | 3 | 7 | 86.1677 | 18.1814 | 2018-02-17 03:00 | 3 | 7 | 0 | 0 | 2018-02-17 03:00 | 3 | 7 | 86.7002 | 18.3804 | 2018-02-17 03:00 | 3 | 7 | 32.9461 | 6.9187
2018-02-17 04:00 | 4 | 7 | 86.3081 | 18.211 | 2018-02-17 04:00 | 4 | 7 | 0 | 0 | 2018-02-17 04:00 | 4 | 7 | 86.8513 | 18.4125 | 2018-02-17 04:00 | 4 | 7 | 33.0035 | 6.9307
2018-02-17 05:00 | 5 | 7 | 86.2562 | 18.2001 | 2018-02-17 05:00 | 5 | 7 | 0 | 0 | 2018-02-17 05:00 | 5 | 7 | 86.8605 | 18.4144 | 2018-02-17 05:00 | 5 | 7 | 33.007 | 6.9315
2018-02-17 06:00 | 6 | 7 | 86.1234 | 18.172 | 2018-02-17 06:00 | 6 | 7 | 0 | 0 | 2018-02-17 06:00 | 6 | 7 | 86.6682 | 18.3737 | 2018-02-17 06:00 | 6 | 7 | 32.9339 | 6.9161
2018-02-17 07:00 | 7 | 7 | 86.1906 | 18.1862 | 2018-02-17 07:00 | 7 | 7 | 0 | 0 | 2018-02-17 07:00 | 7 | 7 | 86.7247 | 18.3856 | 2018-02-17 07:00 | 7 | 7 | 32.9554 | 6.9206
2018-02-17 08:00 | 8 | 7 | 86.36 | 18.222 | 2018-02-17 08:00 | 8 | 7 | 0 | 0 | 2018-02-17 08:00 | 8 | 7 | 86.952 | 18.4338 | 2018-02-17 08:00 | 8 | 7 | 33.0418 | 6.9388
2018-02-17 09:00 | 9 | 7 | 86.4912 | 18.2496 | 2018-02-17 09:00 | 9 | 7 | 0 | 0 | 2018-02-17 09:00 | 9 | 7 | 87.0588 | 18.4565 | 2018-02-17 09:00 | 9 | 7 | 33.0823 | 6.9473
2018-02-17 10:00 | 10 | 7 | 86.1982 | 18.1878 | 2018-02-17 10:00 | 10 | 7 | 0 | 0 | 2018-02-17 10:00 | 10 | 7 | 86.6392 | 18.3675 | 2018-02-17 10:00 | 10 | 7 | 32.9229 | 6.9138
2018-02-17 11:00 | 11 | 7 | 86.1707 | 18.182 | 2018-02-17 11:00 | 11 | 7 | 0 | 0 | 2018-02-17 11:00 | 11 | 7 | 86.8849 | 18.4196 | 2018-02-17 11:00 | 11 | 7 | 33.0163 | 6.9334
2018-02-17 12:00 | 12 | 7 | 86.5019 | 18.2519 | 2018-02-17 12:00 | 12 | 7 | 0 | 0 | 2018-02-17 12:00 | 12 | 7 | 87.1504 | 18.4759 | 2018-02-17 12:00 | 12 | 7 | 33.1172 | 6.9546
2018-02-17 13:00 | 13 | 7 | 86.6148 | 18.2757 | 2018-02-17 13:00 | 13 | 7 | 0 | 0 | 2018-02-17 13:00 | 13 | 7 | 87.3167 | 18.5111 | 2018-02-17 13:00 | 13 | 7 | 33.1803 | 6.9679
2018-02-17 14:00 | 14 | 7 | 86.4439 | 18.2397 | 2018-02-17 14:00 | 14 | 7 | 0 | 0 | 2018-02-17 14:00 | 14 | 7 | 87.0832 | 18.4616 | 2018-02-17 14:00 | 14 | 7 | 33.0916 | 6.9492
2018-02-17 15:00 | 15 | 7 | 86.5522 | 18.2625 | 2018-02-17 15:00 | 15 | 7 | 0 | 0 | 2018-02-17 15:00 | 15 | 7 | 87.2938 | 18.5063 | 2018-02-17 15:00 | 15 | 7 | 33.1716 | 6.966
2018-02-17 16:00 | 16 | 7 | 86.5644 | 18.2651 | 2018-02-17 16:00 | 16 | 7 | 0 | 0 | 2018-02-17 16:00 | 16 | 7 | 87.3579 | 18.5199 | 2018-02-17 16:00 | 16 | 7 | 33.196 | 6.9712
2018-02-17 17:00 | 17 | 7 | 86.7445 | 18.3031 | 2018-02-17 17:00 | 17 | 7 | 0 | 0 | 2018-02-17 17:00 | 17 | 7 | 87.57 | 18.5648 | 2018-02-17 17:00 | 17 | 7 | 33.2766 | 6.9881
2018-02-17 18:00 | 18 | 7 | 86.4668 | 18.2445 | 2018-02-17 18:00 | 18 | 7 | 0 | 0 | 2018-02-17 18:00 | 18 | 7 | 87.3014 | 18.5079 | 2018-02-17 18:00 | 18 | 7 | 33.1745 | 6.9667
2018-02-17 19:00 | 19 | 7 | 86.3661 | 18.2232 | 2018-02-17 19:00 | 19 | 7 | 0 | 0 | 2018-02-17 19:00 | 19 | 7 | 87.0954 | 18.4642 | 2018-02-17 19:00 | 19 | 7 | 33.0963 | 6.9502
2018-02-17 20:00 | 20 | 7 | 86.1173 | 18.1708 | 2018-02-17 20:00 | 20 | 7 | 0 | 0 | 2018-02-17 20:00 | 20 | 7 | 86.891 | 18.4209 | 2018-02-17 20:00 | 20 | 7 | 33.0186 | 6.9339
2018-02-17 21:00 | 21 | 7 | 86.1555 | 18.1788 | 2018-02-17 21:00 | 21 | 7 | 0 | 0 | 2018-02-17 21:00 | 21 | 7 | 86.9245 | 18.428 | 2018-02-17 21:00 | 21 | 7 | 33.0313 | 6.9366
2018-02-17 22:00 | 22 | 7 | 86.2211 | 18.1927 | 2018-02-17 22:00 | 22 | 7 | 0 | 0 | 2018-02-17 22:00 | 22 | 7 | 87.0054 | 18.4451 | 2018-02-17 22:00 | 22 | 7 | 33.0621 | 6.943
2018-02-17 23:00 | 23 | 7 | 86.2226 | 18.193 | 2018-02-17 23:00 | 23 | 7 | 0 | 0 | 2018-02-17 23:00 | 23 | 7 | 87.0787 | 18.4607 | 2018-02-17 23:00 | 23 | 7 | 33.0899 | 6.9489
2018-02-18 | 0 | 1 | 86.2364 | 18.1959 | 2018-02-18 | 0 | 1 | 86.7994 | 17.681 | 2018-02-18 | 0 | 1 | 0 | 0 | 2018-02-18 | 0 | 1 | 32.9838 | 6.9266
2018-02-18 01:00 | 1 | 1 | 86.3188 | 18.2133 | 2018-02-18 01:00 | 1 | 1 | 86.952 | 17.7121 | 2018-02-18 01:00 | 1 | 1 | 0 | 0 | 2018-02-18 01:00 | 1 | 1 | 33.0418 | 6.9388
2018-02-18 02:00 | 2 | 1 | 86.2119 | 18.1907 | 2018-02-18 02:00 | 2 | 1 | 86.8177 | 17.6848 | 2018-02-18 02:00 | 2 | 1 | 0 | 0 | 2018-02-18 02:00 | 2 | 1 | 32.9907 | 6.9281
2018-02-18 03:00 | 3 | 1 | 86.1845 | 18.1849 | 2018-02-18 03:00 | 3 | 1 | 86.7857 | 17.6782 | 2018-02-18 03:00 | 3 | 1 | 0 | 0 | 2018-02-18 03:00 | 3 | 1 | 32.9786 | 6.9255
2018-02-18 04:00 | 4 | 1 | 86.2455 | 18.1978 | 2018-02-18 04:00 | 4 | 1 | 86.833 | 17.6879 | 2018-02-18 04:00 | 4 | 1 | 0 | 0 | 2018-02-18 04:00 | 4 | 1 | 32.9965 | 6.9293
2018-02-18 05:00 | 5 | 1 | 86.2333 | 18.1952 | 2018-02-18 05:00 | 5 | 1 | 86.833 | 17.6879 | 2018-02-18 05:00 | 5 | 1 | 0 | 0 | 2018-02-18 05:00 | 5 | 1 | 32.9965 | 6.9293
2018-02-18 06:00 | 6 | 1 | 86.2776 | 18.2046 | 2018-02-18 06:00 | 6 | 1 | 86.8528 | 17.6919 | 2018-02-18 06:00 | 6 | 1 | 0 | 0 | 2018-02-18 06:00 | 6 | 1 | 33.0041 | 6.9309
2018-02-18 07:00 | 7 | 1 | 86.2867 | 18.2065 | 2018-02-18 07:00 | 7 | 1 | 86.8452 | 17.6904 | 2018-02-18 07:00 | 7 | 1 | 0 | 0 | 2018-02-18 07:00 | 7 | 1 | 33.0012 | 6.9302
2018-02-18 08:00 | 8 | 1 | 86.2989 | 18.2091 | 2018-02-18 08:00 | 8 | 1 | 86.9032 | 17.7022 | 2018-02-18 08:00 | 8 | 1 | 0 | 0 | 2018-02-18 08:00 | 8 | 1 | 33.0232 | 6.9349
2018-02-18 09:00 | 9 | 1 | 86.2867 | 18.2065 | 2018-02-18 09:00 | 9 | 1 | 86.8162 | 17.6845 | 2018-02-18 09:00 | 9 | 1 | 0 | 0 | 2018-02-18 09:00 | 9 | 1 | 32.9902 | 6.9279
2018-02-18 10:00 | 10 | 1 | 86.2882 | 18.2068 | 2018-02-18 10:00 | 10 | 1 | 86.8528 | 17.6919 | 2018-02-18 10:00 | 10 | 1 | 0 | 0 | 2018-02-18 10:00 | 10 | 1 | 33.0041 | 6.9309
2018-02-18 11:00 | 11 | 1 | 86.1845 | 18.1849 | 2018-02-18 11:00 | 11 | 1 | 86.743 | 17.6695 | 2018-02-18 11:00 | 11 | 1 | 0 | 0 | 2018-02-18 11:00 | 11 | 1 | 32.9623 | 6.9221
2018-02-18 12:00 | 12 | 1 | 86.1418 | 18.1759 | 2018-02-18 12:00 | 12 | 1 | 86.714 | 17.6636 | 2018-02-18 12:00 | 12 | 1 | 0 | 0 | 2018-02-18 12:00 | 12 | 1 | 32.9513 | 6.9198
2018-02-18 13:00 | 13 | 1 | 86.1479 | 18.1772 | 2018-02-18 13:00 | 13 | 1 | 86.7659 | 17.6742 | 2018-02-18 13:00 | 13 | 1 | 0 | 0 | 2018-02-18 13:00 | 13 | 1 | 32.971 | 6.9239
2018-02-18 14:00 | 14 | 1 | 86.1112 | 18.1695 | 2018-02-18 14:00 | 14 | 1 | 86.7018 | 17.6612 | 2018-02-18 14:00 | 14 | 1 | 0 | 0 | 2018-02-18 14:00 | 14 | 1 | 32.9467 | 6.9188
2018-02-18 15:00 | 15 | 1 | 86.2455 | 18.1978 | 2018-02-18 15:00 | 15 | 1 | 86.8482 | 17.691 | 2018-02-18 15:00 | 15 | 1 | 0 | 0 | 2018-02-18 15:00 | 15 | 1 | 33.0023 | 6.9305
2018-02-18 16:00 | 16 | 1 | 86.3447 | 18.2187 | 2018-02-18 16:00 | 16 | 1 | 86.9398 | 17.7096 | 2018-02-18 16:00 | 16 | 1 | 0 | 0 | 2018-02-18 16:00 | 16 | 1 | 33.0371 | 6.9378
2018-02-18 17:00 | 17 | 1 | 86.4805 | 18.2474 | 2018-02-18 17:00 | 17 | 1 | 86.9856 | 17.719 | 2018-02-18 17:00 | 17 | 1 | 0 | 0 | 2018-02-18 17:00 | 17 | 1 | 33.0545 | 6.9415
2018-02-18 18:00 | 18 | 1 | 86.4332 | 18.2374 | 2018-02-18 18:00 | 18 | 1 | 86.92 | 17.7056 | 2018-02-18 18:00 | 18 | 1 | 0 | 0 | 2018-02-18 18:00 | 18 | 1 | 33.0296 | 6.9362
2018-02-18 19:00 | 19 | 1 | 85.6794 | 18.0784 | 2018-02-18 19:00 | 19 | 1 | 85.9266 | 17.5032 | 2018-02-18 19:00 | 19 | 1 | 0 | 0 | 2018-02-18 19:00 | 19 | 1 | 32.6521 | 6.8569
2018-02-18 20:00 | 20 | 1 | 86.3294 | 18.2155 | 2018-02-18 20:00 | 20 | 1 | 86.5888 | 17.6381 | 2018-02-18 20:00 | 20 | 1 | 0 | 0 | 2018-02-18 20:00 | 20 | 1 | 32.9037 | 6.9098
2018-02-18 21:00 | 21 | 1 | 86.3569 | 18.2213 | 2018-02-18 21:00 | 21 | 1 | 86.6728 | 17.6552 | 2018-02-18 21:00 | 21 | 1 | 0 | 0 | 2018-02-18 21:00 | 21 | 1 | 32.9357 | 6.9165
2018-02-18 22:00 | 22 | 1 | 86.4881 | 18.249 | 2018-02-18 22:00 | 22 | 1 | 86.8086 | 17.6829 | 2018-02-18 22:00 | 22 | 1 | 0 | 0 | 2018-02-18 22:00 | 22 | 1 | 32.9873 | 6.9273
2018-02-18 23:00 | 23 | 1 | 86.4332 | 18.2374 | 2018-02-18 23:00 | 23 | 1 | 86.7353 | 17.668 | 2018-02-18 23:00 | 23 | 1 | 0 | 0 | 2018-02-18 23:00 | 23 | 1 | 32.9594 | 6.9215
2018-02-19 | 0 | 2 | 86.4088 | 18.2323 | 2018-02-19 | 0 | 2 | 86.7002 | 17.6608 | 2018-02-19 | 0 | 2 | 86.9352 | 18.4303 | 2018-02-19 | 0 | 2 | 65.9815 | 13.8561
2018-02-19 01:00 | 1 | 2 | 86.0426 | 18.155 | 2018-02-19 01:00 | 1 | 2 | 86.3127 | 17.5819 | 2018-02-19 01:00 | 1 | 2 | 86.5278 | 18.3439 | 2018-02-19 01:00 | 1 | 2 | 65.6794 | 13.7927
2018-02-19 02:00 | 2 | 2 | 86.392 | 18.2287 | 2018-02-19 02:00 | 2 | 2 | 86.6392 | 17.6484 | 2018-02-19 02:00 | 2 | 2 | 86.8421 | 18.4105 | 2018-02-19 02:00 | 2 | 2 | 65.9229 | 13.8438
2018-02-19 03:00 | 3 | 2 | 86.2776 | 18.2046 | 2018-02-19 03:00 | 3 | 2 | 86.5766 | 17.6357 | 2018-02-19 03:00 | 3 | 2 | 86.7536 | 18.3918 | 2018-02-19 03:00 | 3 | 2 | 65.8655 | 13.8317
2018-02-19 04:00 | 4 | 2 | 86.5034 | 18.2522 | 2018-02-19 04:00 | 4 | 2 | 86.8849 | 17.6985 | 2018-02-19 04:00 | 4 | 2 | 87.0283 | 18.45 | 2018-02-19 04:00 | 4 | 2 | 66.087 | 13.8783
2018-02-19 05:00 | 5 | 2 | 86.3661 | 18.2232 | 2018-02-19 05:00 | 5 | 2 | 86.772 | 17.6755 | 2018-02-19 05:00 | 5 | 2 | 87.0054 | 18.4451 | 2018-02-19 05:00 | 5 | 2 | 66.0354 | 13.8674
2018-02-19 06:00 | 6 | 2 | 86.2898 | 18.2071 | 2018-02-19 06:00 | 6 | 2 | 86.6499 | 17.6506 | 2018-02-19 06:00 | 6 | 2 | 86.8147 | 18.4047 | 2018-02-19 06:00 | 6 | 2 | 65.9165 | 13.8425
2018-02-19 07:00 | 7 | 2 | 86.2043 | 18.1891 | 2018-02-19 07:00 | 7 | 2 | 86.5278 | 17.6257 | 2018-02-19 07:00 | 7 | 2 | 86.7079 | 18.3821 | 2018-02-19 07:00 | 7 | 2 | 65.8296 | 13.8242
2018-02-19 08:00 | 8 | 2 | 86.3355 | 18.2168 | 2018-02-19 08:00 | 8 | 2 | 86.5461 | 17.6294 | 2018-02-19 08:00 | 8 | 2 | 86.8025 | 18.4021 | 2018-02-19 08:00 | 8 | 2 | 65.8725 | 13.8332
2018-02-19 09:00 | 9 | 2 | 86.3798 | 18.2261 | 2018-02-19 09:00 | 9 | 2 | 86.7262 | 17.6661 | 2018-02-19 09:00 | 9 | 2 | 86.8711 | 18.4167 | 2018-02-19 09:00 | 9 | 2 | 65.967 | 13.8531
2018-02-19 10:00 | 10 | 2 | 86.2272 | 18.1939 | 2018-02-19 10:00 | 10 | 2 | 86.5156 | 17.6232 | 2018-02-19 10:00 | 10 | 2 | 86.714 | 18.3834 | 2018-02-19 10:00 | 10 | 2 | 65.8272 | 13.8237
2018-02-19 11:00 | 11 | 2 | 86.2119 | 18.1907 | 2018-02-19 11:00 | 11 | 2 | 86.5141 | 17.6229 | 2018-02-19 11:00 | 11 | 2 | 86.7201 | 18.3847 | 2018-02-19 11:00 | 11 | 2 | 65.829 | 13.8241
2018-02-19 12:00 | 12 | 2 | 86.389 | 18.2281 | 2018-02-19 12:00 | 12 | 2 | 86.6835 | 17.6574 | 2018-02-19 12:00 | 12 | 2 | 86.8574 | 18.4138 | 2018-02-19 12:00 | 12 | 2 | 65.9455 | 13.8486
2018-02-19 13:00 | 13 | 2 | 86.4027 | 18.231 | 2018-02-19 13:00 | 13 | 2 | 86.6224 | 17.645 | 2018-02-19 13:00 | 13 | 2 | 86.7475 | 18.3905 | 2018-02-19 13:00 | 13 | 2 | 65.8806 | 13.8349
2018-02-19 14:00 | 14 | 2 | 86.3783 | 18.2258 | 2018-02-19 14:00 | 14 | 2 | 86.6606 | 17.6528 | 2018-02-19 14:00 | 14 | 2 | 86.7903 | 18.3995 | 2018-02-19 14:00 | 14 | 2 | 65.9113 | 13.8414
2018-02-19 15:00 | 15 | 2 | 86.3355 | 18.2168 | 2018-02-19 15:00 | 15 | 2 | 86.5248 | 17.6251 | 2018-02-19 15:00 | 15 | 2 | 86.7384 | 18.3885 | 2018-02-19 15:00 | 15 | 2 | 65.84 | 13.8264
2018-02-19 16:00 | 16 | 2 | 86.3493 | 18.2197 | 2018-02-19 16:00 | 16 | 2 | 86.4912 | 17.6183 | 2018-02-19 16:00 | 16 | 2 | 86.685 | 18.3772 | 2018-02-19 16:00 | 16 | 2 | 65.807 | 13.8195
2018-02-19 17:00 | 17 | 2 | 86.244 | 18.1975 | 2018-02-19 17:00 | 17 | 2 | 86.4683 | 17.6136 | 2018-02-19 17:00 | 17 | 2 | 86.6743 | 18.375 | 2018-02-19 17:00 | 17 | 2 | 65.7942 | 13.8168
2018-02-19 18:00 | 18 | 2 | 86.3142 | 18.2123 | 2018-02-19 18:00 | 18 | 2 | 86.4378 | 17.6074 | 2018-02-19 18:00 | 18 | 2 | 86.5934 | 18.3578 | 2018-02-19 18:00 | 18 | 2 | 65.7519 | 13.8079
2018-02-19 19:00 | 19 | 2 | 86.2089 | 18.1901 | 2018-02-19 19:00 | 19 | 2 | 86.3508 | 17.5897 | 2018-02-19 19:00 | 19 | 2 | 86.5583 | 18.3504 | 2018-02-19 19:00 | 19 | 2 | 65.7055 | 13.7981
2018-02-19 20:00 | 20 | 2 | 86.2181 | 18.192 | 2018-02-19 20:00 | 20 | 2 | 86.4836 | 17.6167 | 2018-02-19 20:00 | 20 | 2 | 86.6896 | 18.3782 | 2018-02-19 20:00 | 20 | 2 | 65.8058 | 13.8192
2018-02-19 21:00 | 21 | 2 | 86.1494 | 18.1775 | 2018-02-19 21:00 | 21 | 2 | 86.4759 | 17.6151 | 2018-02-19 21:00 | 21 | 2 | 86.63 | 18.3656 | 2018-02-19 21:00 | 21 | 2 | 65.7802 | 13.8139
2018-02-19 22:00 | 22 | 2 | 86.2593 | 18.2007 | 2018-02-19 22:00 | 22 | 2 | 86.5522 | 17.6307 | 2018-02-19 22:00 | 22 | 2 | 86.6468 | 18.3691 | 2018-02-19 22:00 | 22 | 2 | 65.8156 | 13.8213
2018-02-19 23:00 | 23 | 2 | 86.4424 | 18.2393 | 2018-02-19 23:00 | 23 | 2 | 86.8055 | 17.6823 | 2018-02-19 23:00 | 23 | 2 | 86.8864 | 18.4199 | 2018-02-19 23:00 | 23 | 2 | 66.0029 | 13.8606
2018-02-20 | 0 | 3 | 86.4637 | 18.2438 | 2018-02-20 | 0 | 3 | 0 | 0 | 2018-02-20 | 0 | 3 | 0 | 0 | 2018-02-20 | 0 | 3 | 0 | 0
2018-02-20 01:00 | 1 | 3 | 86.5629 | 18.2648 | 2018-02-20 01:00 | 1 | 3 | 0 | 0 | 2018-02-20 01:00 | 1 | 3 | 0 | 0 | 2018-02-20 01:00 | 1 | 3 | 0 | 0
2018-02-20 02:00 | 2 | 3 | 86.3706 | 18.2242 | 2018-02-20 02:00 | 2 | 3 | 0 | 0 | 2018-02-20 02:00 | 2 | 3 | 0 | 0 | 2018-02-20 02:00 | 2 | 3 | 0 | 0
2018-02-20 03:00 | 3 | 3 | 86.3523 | 18.2203 | 2018-02-20 03:00 | 3 | 3 | 0 | 0 | 2018-02-20 03:00 | 3 | 3 | 0 | 0 | 2018-02-20 03:00 | 3 | 3 | 0 | 0
2018-02-20 04:00 | 4 | 3 | 86.3676 | 18.2236 | 2018-02-20 04:00 | 4 | 3 | 0 | 0 | 2018-02-20 04:00 | 4 | 3 | 0 | 0 | 2018-02-20 04:00 | 4 | 3 | 0 | 0
2018-02-20 05:00 | 5 | 3 | 86.4027 | 18.231 | 2018-02-20 05:00 | 5 | 3 | 0 | 0 | 2018-02-20 05:00 | 5 | 3 | 0 | 0 | 2018-02-20 05:00 | 5 | 3 | 0 | 0
2018-02-20 06:00 | 6 | 3 | 86.4652 | 18.2442 | 2018-02-20 06:00 | 6 | 3 | 0 | 0 | 2018-02-20 06:00 | 6 | 3 | 0 | 0 | 2018-02-20 06:00 | 6 | 3 | 0 | 0
2018-02-20 07:00 | 7 | 3 | 86.4012 | 18.2307 | 2018-02-20 07:00 | 7 | 3 | 0 | 0 | 2018-02-20 07:00 | 7 | 3 | 0 | 0 | 2018-02-20 07:00 | 7 | 3 | 0 | 0
2018-02-20 08:00 | 8 | 3 | 86.4515 | 18.2413 | 2018-02-20 08:00 | 8 | 3 | 0 | 0 | 2018-02-20 08:00 | 8 | 3 | 0 | 0 | 2018-02-20 08:00 | 8 | 3 | 0 | 0
2018-02-20 09:00 | 9 | 3 | 86.2028 | 18.1888 | 2018-02-20 09:00 | 9 | 3 | 0 | 0 | 2018-02-20 09:00 | 9 | 3 | 0 | 0 | 2018-02-20 09:00 | 9 | 3 | 0 | 0
2018-02-20 10:00 | 10 | 3 | 86.2715 | 18.2033 | 2018-02-20 10:00 | 10 | 3 | 0 | 0 | 2018-02-20 10:00 | 10 | 3 | 0 | 0 | 2018-02-20 10:00 | 10 | 3 | 0 | 0
2018-02-20 11:00 | 11 | 3 | 86.7567 | 18.3057 | 2018-02-20 11:00 | 11 | 3 | 0 | 0 | 2018-02-20 11:00 | 11 | 3 | 0 | 0 | 2018-02-20 11:00 | 11 | 3 | 0 | 0
2018-02-20 12:00 | 12 | 3 | 86.6194 | 18.2767 | 2018-02-20 12:00 | 12 | 3 | 0 | 0 | 2018-02-20 12:00 | 12 | 3 | 0 | 0 | 2018-02-20 12:00 | 12 | 3 | 0 | 0
2018-02-20 13:00 | 13 | 3 | 86.6377 | 18.2806 | 2018-02-20 13:00 | 13 | 3 | 0 | 0 | 2018-02-20 13:00 | 13 | 3 | 0 | 0 | 2018-02-20 13:00 | 13 | 3 | 0 | 0
2018-02-20 14:00 | 14 | 3 | 86.8757 | 18.3308 | 2018-02-20 14:00 | 14 | 3 | 0 | 0 | 2018-02-20 14:00 | 14 | 3 | 0 | 0 | 2018-02-20 14:00 | 14 | 3 | 0 | 0
2018-02-20 15:00 | 15 | 3 | 86.7994 | 18.3147 | 2018-02-20 15:00 | 15 | 3 | 0 | 0 | 2018-02-20 15:00 | 15 | 3 | 0 | 0 | 2018-02-20 15:00 | 15 | 3 | 0 | 0
2018-02-20 16:00 | 16 | 3 | 86.7674 | 18.3079 | 2018-02-20 16:00 | 16 | 3 | 0 | 0 | 2018-02-20 16:00 | 16 | 3 | 0 | 0 | 2018-02-20 16:00 | 16 | 3 | 0 | 0
2018-02-20 17:00 | 17 | 3 | 86.7384 | 18.3018 | 2018-02-20 17:00 | 17 | 3 | 0 | 0 | 2018-02-20 17:00 | 17 | 3 | 0 | 0 | 2018-02-20 17:00 | 17 | 3 | 0 | 0
2018-02-20 18:00 | 18 | 3 | 86.7124 | 18.2963 | 2018-02-20 18:00 | 18 | 3 | 0 | 0 | 2018-02-20 18:00 | 18 | 3 | 0 | 0 | 2018-02-20 18:00 | 18 | 3 | 0 | 0
2018-02-20 19:00 | 19 | 3 | 86.8376 | 18.3227 | 2018-02-20 19:00 | 19 | 3 | 0 | 0 | 2018-02-20 19:00 | 19 | 3 | 0 | 0 | 2018-02-20 19:00 | 19 | 3 | 0 | 0
2018-02-20 20:00 | 20 | 3 | 86.627 | 18.2783 | 2018-02-20 20:00 | 20 | 3 | 0 | 0 | 2018-02-20 20:00 | 20 | 3 | 0 | 0 | 2018-02-20 20:00 | 20 | 3 | 0 | 0
2018-02-20 21:00 | 21 | 3 | 86.6239 | 18.2776 | 2018-02-20 21:00 | 21 | 3 | 0 | 0 | 2018-02-20 21:00 | 21 | 3 | 0 | 0 | 2018-02-20 21:00 | 21 | 3 | 0 | 0
2018-02-20 22:00 | 22 | 3 | 86.714 | 18.2967 | 2018-02-20 22:00 | 22 | 3 | 0 | 0 | 2018-02-20 22:00 | 22 | 3 | 0 | 0 | 2018-02-20 22:00 | 22 | 3 | 0 | 0
2018-02-20 23:00 | 23 | 3 | 86.8971 | 18.3353 | 2018-02-20 23:00 | 23 | 3 | 0 | 0 | 2018-02-20 23:00 | 23 | 3 | 0 | 0 | 2018-02-20 23:00 | 23 | 3 | 0 | 0
2018-02-21 | 0 | 4 | 0 | 0 | 2018-02-21 | 0 | 4 | 0 | 0 | 2018-02-21 | 0 | 4 | 86.6712 | 18.3743 | 2018-02-21 | 0 | 4 | 32.9351 | 6.9164
2018-02-21 01:00 | 1 | 4 | 0 | 0 | 2018-02-21 01:00 | 1 | 4 | 0 | 0 | 2018-02-21 01:00 | 1 | 4 | 86.511 | 18.3403 | 2018-02-21 01:00 | 1 | 4 | 32.8742 | 6.9036
2018-02-21 02:00 | 2 | 4 | 0 | 0 | 2018-02-21 02:00 | 2 | 4 | 0 | 0 | 2018-02-21 02:00 | 2 | 4 | 86.7628 | 18.3937 | 2018-02-21 02:00 | 2 | 4 | 32.9699 | 6.9237
2018-02-21 03:00 | 3 | 4 | 0 | 0 | 2018-02-21 03:00 | 3 | 4 | 0 | 0 | 2018-02-21 03:00 | 3 | 4 | 86.7384 | 18.3885 | 2018-02-21 03:00 | 3 | 4 | 32.9606 | 6.9217
2018-02-21 04:00 | 4 | 4 | 0 | 0 | 2018-02-21 04:00 | 4 | 4 | 0 | 0 | 2018-02-21 04:00 | 4 | 4 | 86.8376 | 18.4096 | 2018-02-21 04:00 | 4 | 4 | 32.9983 | 6.9296
2018-02-21 05:00 | 5 | 4 | 0 | 0 | 2018-02-21 05:00 | 5 | 4 | 0 | 0 | 2018-02-21 05:00 | 5 | 4 | 87.0222 | 18.4487 | 2018-02-21 05:00 | 5 | 4 | 33.0684 | 6.9444
2018-02-21 06:00 | 6 | 4 | 0 | 0 | 2018-02-21 06:00 | 6 | 4 | 0 | 0 | 2018-02-21 06:00 | 6 | 4 | 86.9627 | 18.4361 | 2018-02-21 06:00 | 6 | 4 | 33.0458 | 6.9396
2018-02-21 07:00 | 7 | 4 | 0 | 0 | 2018-02-21 07:00 | 7 | 4 | 0 | 0 | 2018-02-21 07:00 | 7 | 4 | 87.1321 | 18.472 | 2018-02-21 07:00 | 7 | 4 | 33.1102 | 6.9531
2018-02-21 08:00 | 8 | 4 | 0 | 0 | 2018-02-21 08:00 | 8 | 4 | 0 | 0 | 2018-02-21 08:00 | 8 | 4 | 87.1931 | 18.4849 | 2018-02-21 08:00 | 8 | 4 | 33.1334 | 6.958
2018-02-21 09:00 | 9 | 4 | 0 | 0 | 2018-02-21 09:00 | 9 | 4 | 0 | 0 | 2018-02-21 09:00 | 9 | 4 | 86.7155 | 18.3837 | 2018-02-21 09:00 | 9 | 4 | 32.9519 | 6.9199
2018-02-21 10:00 | 10 | 4 | 0 | 0 | 2018-02-21 10:00 | 10 | 4 | 0 | 0 | 2018-02-21 10:00 | 10 | 4 | 86.6743 | 18.375 | 2018-02-21 10:00 | 10 | 4 | 32.9362 | 6.9166
2018-02-21 11:00 | 11 | 4 | 0 | 0 | 2018-02-21 11:00 | 11 | 4 | 0 | 0 | 2018-02-21 11:00 | 11 | 4 | 86.8956 | 18.4219 | 2018-02-21 11:00 | 11 | 4 | 33.0203 | 6.9343
2018-02-21 12:00 | 12 | 4 | 0 | 0 | 2018-02-21 12:00 | 12 | 4 | 0 | 0 | 2018-02-21 12:00 | 12 | 4 | 86.9276 | 18.4287 | 2018-02-21 12:00 | 12 | 4 | 33.0325 | 6.9368
2018-02-21 13:00 | 13 | 4 | 0 | 0 | 2018-02-21 13:00 | 13 | 4 | 0 | 0 | 2018-02-21 13:00 | 13 | 4 | 87.2541 | 18.4979 | 2018-02-21 13:00 | 13 | 4 | 33.1566 | 6.9629
2018-02-21 14:00 | 14 | 4 | 0 | 0 | 2018-02-21 14:00 | 14 | 4 | 0 | 0 | 2018-02-21 14:00 | 14 | 4 | 87.4037 | 18.5296 | 2018-02-21 14:00 | 14 | 4 | 33.2134 | 6.9748
2018-02-21 15:00 | 15 | 4 | 0 | 0 | 2018-02-21 15:00 | 15 | 4 | 0 | 0 | 2018-02-21 15:00 | 15 | 4 | 87.2129 | 18.4891 | 2018-02-21 15:00 | 15 | 4 | 33.1409 | 6.9596
2018-02-21 16:00 | 16 | 4 | 0 | 0 | 2018-02-21 16:00 | 16 | 4 | 0 | 0 | 2018-02-21 16:00 | 16 | 4 | 86.9718 | 18.438 | 2018-02-21 16:00 | 16 | 4 | 33.0493 | 6.9403
2018-02-21 17:00 | 17 | 4 | 0 | 0 | 2018-02-21 17:00 | 17 | 4 | 0 | 0 | 2018-02-21 17:00 | 17 | 4 | 87.1397 | 18.4736 | 2018-02-21 17:00 | 17 | 4 | 33.1131 | 6.9537
2018-02-21 18:00 | 18 | 4 | 0 | 0 | 2018-02-21 18:00 | 18 | 4 | 0 | 0 | 2018-02-21 18:00 | 18 | 4 | 87.2435 | 18.4956 | 2018-02-21 18:00 | 18 | 4 | 33.1525 | 6.962
2018-02-21 19:00 | 19 | 4 | 0 | 0 | 2018-02-21 19:00 | 19 | 4 | 0 | 0 | 2018-02-21 19:00 | 19 | 4 | 86.8894 | 18.4206 | 2018-02-21 19:00 | 19 | 4 | 33.018 | 6.9338
2018-02-21 20:00 | 20 | 4 | 0 | 0 | 2018-02-21 20:00 | 20 | 4 | 0 | 0 | 2018-02-21 20:00 | 20 | 4 | 87.1839 | 18.483 | 2018-02-21 20:00 | 20 | 4 | 33.1299 | 6.9573
2018-02-21 21:00 | 21 | 4 | 0 | 0 | 2018-02-21 21:00 | 21 | 4 | 0 | 0 | 2018-02-21 21:00 | 21 | 4 | 87.2419 | 18.4953 | 2018-02-21 21:00 | 21 | 4 | 33.1519 | 6.9619
2018-02-21 22:00 | 22 | 4 | 0 | 0 | 2018-02-21 22:00 | 22 | 4 | 0 | 0 | 2018-02-21 22:00 | 22 | 4 | 87.1733 | 18.4807 | 2018-02-21 22:00 | 22 | 4 | 33.1259 | 6.9564
2018-02-21 23:00 | 23 | 4 | 0 | 0 | 2018-02-21 23:00 | 23 | 4 | 0 | 0 | 2018-02-21 23:00 | 23 | 4 | 87.2557 | 18.4982 | 2018-02-21 23:00 | 23 | 4 | 33.1572 | 6.963
2018-02-22 | 0 | 5 | 86.5492 | 18.2619 | 2018-02-22 | 0 | 5 | 0 | 0 | 2018-02-22 | 0 | 5 | 0 | 0 | 2018-02-22 | 0 | 5 | 0 | 0
2018-02-22 01:00 | 1 | 5 | 86.7201 | 18.2979 | 2018-02-22 01:00 | 1 | 5 | 0 | 0 | 2018-02-22 01:00 | 1 | 5 | 0 | 0 | 2018-02-22 01:00 | 1 | 5 | 0 | 0
2018-02-22 02:00 | 2 | 5 | 86.5095 | 18.2535 | 2018-02-22 02:00 | 2 | 5 | 0 | 0 | 2018-02-22 02:00 | 2 | 5 | 0 | 0 | 2018-02-22 02:00 | 2 | 5 | 0 | 0
2018-02-22 03:00 | 3 | 5 | 86.4576 | 18.2426 | 2018-02-22 03:00 | 3 | 5 | 0 | 0 | 2018-02-22 03:00 | 3 | 5 | 0 | 0 | 2018-02-22 03:00 | 3 | 5 | 0 | 0
2018-02-22 04:00 | 4 | 5 | 86.6316 | 18.2793 | 2018-02-22 04:00 | 4 | 5 | 0 | 0 | 2018-02-22 04:00 | 4 | 5 | 0 | 0 | 2018-02-22 04:00 | 4 | 5 | 0 | 0
2018-02-22 05:00 | 5 | 5 | 86.569 | 18.2661 | 2018-02-22 05:00 | 5 | 5 | 0 | 0 | 2018-02-22 05:00 | 5 | 5 | 0 | 0 | 2018-02-22 05:00 | 5 | 5 | 0 | 0
2018-02-22 06:00 | 6 | 5 | 86.6468 | 18.2825 | 2018-02-22 06:00 | 6 | 5 | 0 | 0 | 2018-02-22 06:00 | 6 | 5 | 0 | 0 | 2018-02-22 06:00 | 6 | 5 | 0 | 0
2018-02-22 07:00 | 7 | 5 | 86.6361 | 18.2802 | 2018-02-22 07:00 | 7 | 5 | 0 | 0 | 2018-02-22 07:00 | 7 | 5 | 0 | 0 | 2018-02-22 07:00 | 7 | 5 | 0 | 0
2018-02-22 08:00 | 8 | 5 | 86.6819 | 18.2899 | 2018-02-22 08:00 | 8 | 5 | 0 | 0 | 2018-02-22 08:00 | 8 | 5 | 0 | 0 | 2018-02-22 08:00 | 8 | 5 | 0 | 0
2018-02-22 09:00 | 9 | 5 | 86.7094 | 18.2957 | 2018-02-22 09:00 | 9 | 5 | 0 | 0 | 2018-02-22 09:00 | 9 | 5 | 0 | 0 | 2018-02-22 09:00 | 9 | 5 | 0 | 0
2018-02-22 10:00 | 10 | 5 | 86.7933 | 18.3134 | 2018-02-22 10:00 | 10 | 5 | 0 | 0 | 2018-02-22 10:00 | 10 | 5 | 0 | 0 | 2018-02-22 10:00 | 10 | 5 | 0 | 0
2018-02-22 11:00 | 11 | 5 | 86.8009 | 18.315 | 2018-02-22 11:00 | 11 | 5 | 0 | 0 | 2018-02-22 11:00 | 11 | 5 | 0 | 0 | 2018-02-22 11:00 | 11 | 5 | 0 | 0
2018-02-22 12:00 | 12 | 5 | 86.6728 | 18.288 | 2018-02-22 12:00 | 12 | 5 | 0 | 0 | 2018-02-22 12:00 | 12 | 5 | 0 | 0 | 2018-02-22 12:00 | 12 | 5 | 0 | 0
2018-02-22 13:00 | 13 | 5 | 86.6316 | 18.2793 | 2018-02-22 13:00 | 13 | 5 | 0 | 0 | 2018-02-22 13:00 | 13 | 5 | 0 | 0 | 2018-02-22 13:00 | 13 | 5 | 0 | 0
2018-02-22 14:00 | 14 | 5 | 86.6316 | 18.2793 | 2018-02-22 14:00 | 14 | 5 | 0 | 0 | 2018-02-22 14:00 | 14 | 5 | 0 | 0 | 2018-02-22 14:00 | 14 | 5 | 0 | 0
2018-02-22 15:00 | 15 | 5 | 86.6636 | 18.286 | 2018-02-22 15:00 | 15 | 5 | 0 | 0 | 2018-02-22 15:00 | 15 | 5 | 0 | 0 | 2018-02-22 15:00 | 15 | 5 | 0 | 0
2018-02-22 16:00 | 16 | 5 | 86.5568 | 18.2635 | 2018-02-22 16:00 | 16 | 5 | 0 | 0 | 2018-02-22 16:00 | 16 | 5 | 0 | 0 | 2018-02-22 16:00 | 16 | 5 | 0 | 0
2018-02-22 17:00 | 17 | 5 | 86.6865 | 18.2909 | 2018-02-22 17:00 | 17 | 5 | 0 | 0 | 2018-02-22 17:00 | 17 | 5 | 0 | 0 | 2018-02-22 17:00 | 17 | 5 | 0 | 0
2018-02-22 18:00 | 18 | 5 | 86.7262 | 18.2992 | 2018-02-22 18:00 | 18 | 5 | 0 | 0 | 2018-02-22 18:00 | 18 | 5 | 0 | 0 | 2018-02-22 18:00 | 18 | 5 | 0 | 0
2018-02-22 19:00 | 19 | 5 | 86.5187 | 18.2554 | 2018-02-22 19:00 | 19 | 5 | 0 | 0 | 2018-02-22 19:00 | 19 | 5 | 0 | 0 | 2018-02-22 19:00 | 19 | 5 | 0 | 0
2018-02-22 20:00 | 20 | 5 | 86.5766 | 18.2677 | 2018-02-22 20:00 | 20 | 5 | 0 | 0 | 2018-02-22 20:00 | 20 | 5 | 0 | 0 | 2018-02-22 20:00 | 20 | 5 | 0 | 0
2018-02-22 21:00 | 21 | 5 | 86.6194 | 18.2767 | 2018-02-22 21:00 | 21 | 5 | 0 | 0 | 2018-02-22 21:00 | 21 | 5 | 0 | 0 | 2018-02-22 21:00 | 21 | 5 | 0 | 0
2018-02-22 22:00 | 22 | 5 | 86.6743 | 18.2883 | 2018-02-22 22:00 | 22 | 5 | 0 | 0 | 2018-02-22 22:00 | 22 | 5 | 0 | 0 | 2018-02-22 22:00 | 22 | 5 | 0 | 0
2018-02-22 23:00 | 23 | 5 | 86.5644 | 18.2651 | 2018-02-22 23:00 | 23 | 5 | 0 | 0 | 2018-02-22 23:00 | 23 | 5 | 0 | 0 | 2018-02-22 23:00 | 23 | 5 | 0 | 0
2018-02-23 | 0 | 6 | 86.2226 | 18.193 | 2018-02-23 | 0 | 6 | 86.688 | 17.6583 | 2018-02-23 | 0 | 6 | 0 | 0 | 2018-02-23 | 0 | 6 | 32.9414 | 6.9177
2018-02-23 01:00 | 1 | 6 | 86.1128 | 18.1698 | 2018-02-23 01:00 | 1 | 6 | 86.5232 | 17.6248 | 2018-02-23 01:00 | 1 | 6 | 0 | 0 | 2018-02-23 01:00 | 1 | 6 | 32.8788 | 6.9046
2018-02-23 02:00 | 2 | 6 | 86.2791 | 18.2049 | 2018-02-23 02:00 | 2 | 6 | 86.6896 | 17.6587 | 2018-02-23 02:00 | 2 | 6 | 0 | 0 | 2018-02-23 02:00 | 2 | 6 | 32.942 | 6.9178
2018-02-23 03:00 | 3 | 6 | 86.0014 | 18.1463 | 2018-02-23 03:00 | 3 | 6 | 86.4485 | 17.6096 | 2018-02-23 03:00 | 3 | 6 | 0 | 0 | 2018-02-23 03:00 | 3 | 6 | 32.8504 | 6.8986
2018-02-23 04:00 | 4 | 6 | 86.0533 | 18.1572 | 2018-02-23 04:00 | 4 | 6 | 86.4347 | 17.6067 | 2018-02-23 04:00 | 4 | 6 | 0 | 0 | 2018-02-23 04:00 | 4 | 6 | 32.8452 | 6.8975
2018-02-23 05:00 | 5 | 6 | 86.2257 | 18.1936 | 2018-02-23 05:00 | 5 | 6 | 86.6117 | 17.6428 | 2018-02-23 05:00 | 5 | 6 | 0 | 0 | 2018-02-23 05:00 | 5 | 6 | 32.9124 | 6.9116
2018-02-23 06:00 | 6 | 6 | 86.4332 | 18.2374 | 2018-02-23 06:00 | 6 | 6 | 86.9352 | 17.7087 | 2018-02-23 06:00 | 6 | 6 | 0 | 0 | 2018-02-23 06:00 | 6 | 6 | 33.0354 | 6.9374
2018-02-23 07:00 | 7 | 6 | 86.5873 | 18.2699 | 2018-02-23 07:00 | 7 | 6 | 87.0619 | 17.7345 | 2018-02-23 07:00 | 7 | 6 | 0 | 0 | 2018-02-23 07:00 | 7 | 6 | 33.0835 | 6.9475
2018-02-23 08:00 | 8 | 6 | 86.3691 | 18.2239 | 2018-02-23 08:00 | 8 | 6 | 86.7811 | 17.6773 | 2018-02-23 08:00 | 8 | 6 | 0 | 0 | 2018-02-23 08:00 | 8 | 6 | 32.9768 | 6.9251
2018-02-23 09:00 | 9 | 6 | 86.334 | 18.2165 | 2018-02-23 09:00 | 9 | 6 | 86.7399 | 17.6689 | 2018-02-23 09:00 | 9 | 6 | 0 | 0 | 2018-02-23 09:00 | 9 | 6 | 32.9612 | 6.9218
2018-02-23 10:00 | 10 | 6 | 86.5126 | 18.2542 | 2018-02-23 10:00 | 10 | 6 | 86.862 | 17.6938 | 2018-02-23 10:00 | 10 | 6 | 0 | 0 | 2018-02-23 10:00 | 10 | 6 | 33.0076 | 6.9316
2018-02-23 11:00 | 11 | 6 | 86.5003 | 18.2516 | 2018-02-23 11:00 | 11 | 6 | 86.9306 | 17.7078 | 2018-02-23 11:00 | 11 | 6 | 0 | 0 | 2018-02-23 11:00 | 11 | 6 | 33.0336 | 6.9371
2018-02-23 12:00 | 12 | 6 | 86.7002 | 18.2937 | 2018-02-23 12:00 | 12 | 6 | 87.1412 | 17.7507 | 2018-02-23 12:00 | 12 | 6 | 0 | 0 | 2018-02-23 12:00 | 12 | 6 | 33.1137 | 6.9539
2018-02-23 13:00 | 13 | 6 | 86.363 | 18.2226 | 2018-02-23 13:00 | 13 | 6 | 86.8009 | 17.6813 | 2018-02-23 13:00 | 13 | 6 | 0 | 0 | 2018-02-23 13:00 | 13 | 6 | 32.9843 | 6.9267
2018-02-23 14:00 | 14 | 6 | 86.4408 | 18.239 | 2018-02-23 14:00 | 14 | 6 | 86.8635 | 17.6941 | 2018-02-23 14:00 | 14 | 6 | 0 | 0 | 2018-02-23 14:00 | 14 | 6 | 33.0081 | 6.9317
2018-02-23 15:00 | 15 | 6 | 86.2943 | 18.2081 | 2018-02-23 15:00 | 15 | 6 | 86.6743 | 17.6556 | 2018-02-23 15:00 | 15 | 6 | 0 | 0 | 2018-02-23 15:00 | 15 | 6 | 32.9362 | 6.9166
2018-02-23 16:00 | 16 | 6 | 86.3706 | 18.2242 | 2018-02-23 16:00 | 16 | 6 | 86.7491 | 17.6708 | 2018-02-23 16:00 | 16 | 6 | 0 | 0 | 2018-02-23 16:00 | 16 | 6 | 32.9647 | 6.9226
2018-02-23 17:00 | 17 | 6 | 86.2882 | 18.2068 | 2018-02-23 17:00 | 17 | 6 | 86.7445 | 17.6699 | 2018-02-23 17:00 | 17 | 6 | 0 | 0 | 2018-02-23 17:00 | 17 | 6 | 32.9629 | 6.9222
2018-02-23 18:00 | 18 | 6 | 86.1875 | 18.1856 | 2018-02-23 18:00 | 18 | 6 | 86.6667 | 17.654 | 2018-02-23 18:00 | 18 | 6 | 0 | 0 | 2018-02-23 18:00 | 18 | 6 | 32.9333 | 6.916
2018-02-23 19:00 | 19 | 6 | 86.099 | 18.1669 | 2018-02-23 19:00 | 19 | 6 | 86.5431 | 17.6288 | 2018-02-23 19:00 | 19 | 6 | 0 | 0 | 2018-02-23 19:00 | 19 | 6 | 32.8864 | 6.9061
2018-02-23 20:00 | 20 | 6 | 86.1997 | 18.1881 | 2018-02-23 20:00 | 20 | 6 | 86.5187 | 17.6239 | 2018-02-23 20:00 | 20 | 6 | 0 | 0 | 2018-02-23 20:00 | 20 | 6 | 32.8771 | 6.9042
2018-02-23 21:00 | 21 | 6 | 86.3767 | 18.2255 | 2018-02-23 21:00 | 21 | 6 | 86.7247 | 17.6658 | 2018-02-23 21:00 | 21 | 6 | 0 | 0 | 2018-02-23 21:00 | 21 | 6 | 32.9554 | 6.9206
2018-02-23 22:00 | 22 | 6 | 86.3691 | 18.2239 | 2018-02-23 22:00 | 22 | 6 | 86.7659 | 17.6742 | 2018-02-23 22:00 | 22 | 6 | 0 | 0 | 2018-02-23 22:00 | 22 | 6 | 32.971 | 6.9239
2018-02-23 23:00 | 23 | 6 | 86.4012 | 18.2307 | 2018-02-23 23:00 | 23 | 6 | 86.7918 | 17.6795 | 2018-02-23 23:00 | 23 | 6 | 0 | 0 | 2018-02-23 23:00 | 23 | 6 | 32.9809 | 6.926
2018-02-24 | 0 | 7 | 86.0121 | 18.1486 | 2018-02-24 | 0 | 7 | 0 | 0 | 2018-02-24 | 0 | 7 | 86.5507 | 18.3487 | 2018-02-24 | 0 | 7 | 32.8893 | 6.9067
2018-02-24 01:00 | 1 | 7 | 85.919 | 18.1289 | 2018-02-24 01:00 | 1 | 7 | 0 | 0 | 2018-02-24 01:00 | 1 | 7 | 86.5324 | 18.3449 | 2018-02-24 01:00 | 1 | 7 | 32.8823 | 6.9053
2018-02-24 02:00 | 2 | 7 | 86.0533 | 18.1572 | 2018-02-24 02:00 | 2 | 7 | 0 | 0 | 2018-02-24 02:00 | 2 | 7 | 86.6453 | 18.3688 | 2018-02-24 02:00 | 2 | 7 | 32.9252 | 6.9143
2018-02-24 03:00 | 3 | 7 | 86.1677 | 18.1814 | 2018-02-24 03:00 | 3 | 7 | 0 | 0 | 2018-02-24 03:00 | 3 | 7 | 86.7002 | 18.3804 | 2018-02-24 03:00 | 3 | 7 | 32.9461 | 6.9187
2018-02-24 04:00 | 4 | 7 | 86.3081 | 18.211 | 2018-02-24 04:00 | 4 | 7 | 0 | 0 | 2018-02-24 04:00 | 4 | 7 | 86.8513 | 18.4125 | 2018-02-24 04:00 | 4 | 7 | 33.0035 | 6.9307
2018-02-24 05:00 | 5 | 7 | 86.2562 | 18.2001 | 2018-02-24 05:00 | 5 | 7 | 0 | 0 | 2018-02-24 05:00 | 5 | 7 | 86.8605 | 18.4144 | 2018-02-24 05:00 | 5 | 7 | 33.007 | 6.9315
2018-02-24 06:00 | 6 | 7 | 86.1234 | 18.172 | 2018-02-24 06:00 | 6 | 7 | 0 | 0 | 2018-02-24 06:00 | 6 | 7 | 86.6682 | 18.3737 | 2018-02-24 06:00 | 6 | 7 | 32.9339 | 6.9161
2018-02-24 07:00 | 7 | 7 | 86.1906 | 18.1862 | 2018-02-24 07:00 | 7 | 7 | 0 | 0 | 2018-02-24 07:00 | 7 | 7 | 86.7247 | 18.3856 | 2018-02-24 07:00 | 7 | 7 | 32.9554 | 6.9206
2018-02-24 08:00 | 8 | 7 | 86.36 | 18.222 | 2018-02-24 08:00 | 8 | 7 | 0 | 0 | 2018-02-24 08:00 | 8 | 7 | 86.952 | 18.4338 | 2018-02-24 08:00 | 8 | 7 | 33.0418 | 6.9388
2018-02-24 09:00 | 9 | 7 | 86.4912 | 18.2496 | 2018-02-24 09:00 | 9 | 7 | 0 | 0 | 2018-02-24 09:00 | 9 | 7 | 87.0588 | 18.4565 | 2018-02-24 09:00 | 9 | 7 | 33.0823 | 6.9473
2018-02-24 10:00 | 10 | 7 | 86.1982 | 18.1878 | 2018-02-24 10:00 | 10 | 7 | 0 | 0 | 2018-02-24 10:00 | 10 | 7 | 86.6392 | 18.3675 | 2018-02-24 10:00 | 10 | 7 | 32.9229 | 6.9138
2018-02-24 11:00 | 11 | 7 | 86.1707 | 18.182 | 2018-02-24 11:00 | 11 | 7 | 0 | 0 | 2018-02-24 11:00 | 11 | 7 | 86.8849 | 18.4196 | 2018-02-24 11:00 | 11 | 7 | 33.0163 | 6.9334
2018-02-24 12:00 | 12 | 7 | 86.5019 | 18.2519 | 2018-02-24 12:00 | 12 | 7 | 0 | 0 | 2018-02-24 12:00 | 12 | 7 | 87.1504 | 18.4759 | 2018-02-24 12:00 | 12 | 7 | 33.1172 | 6.9546
2018-02-24 13:00 | 13 | 7 | 86.6148 | 18.2757 | 2018-02-24 13:00 | 13 | 7 | 0 | 0 | 2018-02-24 13:00 | 13 | 7 | 87.3167 | 18.5111 | 2018-02-24 13:00 | 13 | 7 | 33.1803 | 6.9679
2018-02-24 14:00 | 14 | 7 | 86.4439 | 18.2397 | 2018-02-24 14:00 | 14 | 7 | 0 | 0 | 2018-02-24 14:00 | 14 | 7 | 87.0832 | 18.4616 | 2018-02-24 14:00 | 14 | 7 | 33.0916 | 6.9492
2018-02-24 15:00 | 15 | 7 | 86.5522 | 18.2625 | 2018-02-24 15:00 | 15 | 7 | 0 | 0 | 2018-02-24 15:00 | 15 | 7 | 87.2938 | 18.5063 | 2018-02-24 15:00 | 15 | 7 | 33.1716 | 6.966
2018-02-24 16:00 | 16 | 7 | 86.5644 | 18.2651 | 2018-02-24 16:00 | 16 | 7 | 0 | 0 | 2018-02-24 16:00 | 16 | 7 | 87.3579 | 18.5199 | 2018-02-24 16:00 | 16 | 7 | 33.196 | 6.9712
2018-02-24 17:00 | 17 | 7 | 86.7445 | 18.3031 | 2018-02-24 17:00 | 17 | 7 | 0 | 0 | 2018-02-24 17:00 | 17 | 7 | 87.57 | 18.5648 | 2018-02-24 17:00 | 17 | 7 | 33.2766 | 6.9881
2018-02-24 18:00 | 18 | 7 | 86.4668 | 18.2445 | 2018-02-24 18:00 | 18 | 7 | 0 | 0 | 2018-02-24 18:00 | 18 | 7 | 87.3014 | 18.5079 | 2018-02-24 18:00 | 18 | 7 | 33.1745 | 6.9667
2018-02-24 19:00 | 19 | 7 | 86.3661 | 18.2232 | 2018-02-24 19:00 | 19 | 7 | 0 | 0 | 2018-02-24 19:00 | 19 | 7 | 87.0954 | 18.4642 | 2018-02-24 19:00 | 19 | 7 | 33.0963 | 6.9502
2018-02-24 20:00 | 20 | 7 | 86.1173 | 18.1708 | 2018-02-24 20:00 | 20 | 7 | 0 | 0 | 2018-02-24 20:00 | 20 | 7 | 86.891 | 18.4209 | 2018-02-24 20:00 | 20 | 7 | 33.0186 | 6.9339
2018-02-24 21:00 | 21 | 7 | 86.1555 | 18.1788 | 2018-02-24 21:00 | 21 | 7 | 0 | 0 | 2018-02-24 21:00 | 21 | 7 | 86.9245 | 18.428 | 2018-02-24 21:00 | 21 | 7 | 33.0313 | 6.9366
2018-02-24 22:00 | 22 | 7 | 86.2211 | 18.1927 | 2018-02-24 22:00 | 22 | 7 | 0 | 0 | 2018-02-24 22:00 | 22 | 7 | 87.0054 | 18.4451 | 2018-02-24 22:00 | 22 | 7 | 33.0621 | 6.943
2018-02-24 23:00 | 23 | 7 | 86.2226 | 18.193 | 2018-02-24 23:00 | 23 | 7 | 0 | 0 | 2018-02-24 23:00 | 23 | 7 | 87.0787 | 18.4607 | 2018-02-24 23:00 | 23 | 7 | 33.0899 | 6.9489
2018-02-25 | 0 | 1 | 86.2364 | 18.1959 | 2018-02-25 | 0 | 1 | 86.7994 | 17.681 | 2018-02-25 | 0 | 1 | 0 | 0 | 2018-02-25 | 0 | 1 | 32.9838 | 6.9266
2018-02-25 01:00 | 1 | 1 | 86.3188 | 18.2133 | 2018-02-25 01:00 | 1 | 1 | 86.952 | 17.7121 | 2018-02-25 01:00 | 1 | 1 | 0 | 0 | 2018-02-25 01:00 | 1 | 1 | 33.0418 | 6.9388
2018-02-25 02:00 | 2 | 1 | 86.2119 | 18.1907 | 2018-02-25 02:00 | 2 | 1 | 86.8177 | 17.6848 | 2018-02-25 02:00 | 2 | 1 | 0 | 0 | 2018-02-25 02:00 | 2 | 1 | 32.9907 | 6.9281
2018-02-25 03:00 | 3 | 1 | 86.1845 | 18.1849 | 2018-02-25 03:00 | 3 | 1 | 86.7857 | 17.6782 | 2018-02-25 03:00 | 3 | 1 | 0 | 0 | 2018-02-25 03:00 | 3 | 1 | 32.9786 | 6.9255
2018-02-25 04:00 | 4 | 1 | 86.2455 | 18.1978 | 2018-02-25 04:00 | 4 | 1 | 86.833 | 17.6879 | 2018-02-25 04:00 | 4 | 1 | 0 | 0 | 2018-02-25 04:00 | 4 | 1 | 32.9965 | 6.9293
2018-02-25 05:00 | 5 | 1 | 86.2333 | 18.1952 | 2018-02-25 05:00 | 5 | 1 | 86.833 | 17.6879 | 2018-02-25 05:00 | 5 | 1 | 0 | 0 | 2018-02-25 05:00 | 5 | 1 | 32.9965 | 6.9293
2018-02-25 06:00 | 6 | 1 | 86.2776 | 18.2046 | 2018-02-25 06:00 | 6 | 1 | 86.8528 | 17.6919 | 2018-02-25 06:00 | 6 | 1 | 0 | 0 | 2018-02-25 06:00 | 6 | 1 | 33.0041 | 6.9309
2018-02-25 07:00 | 7 | 1 | 86.2867 | 18.2065 | 2018-02-25 07:00 | 7 | 1 | 86.8452 | 17.6904 | 2018-02-25 07:00 | 7 | 1 | 0 | 0 | 2018-02-25 07:00 | 7 | 1 | 33.0012 | 6.9302
2018-02-25 08:00 | 8 | 1 | 86.2989 | 18.2091 | 2018-02-25 08:00 | 8 | 1 | 86.9032 | 17.7022 | 2018-02-25 08:00 | 8 | 1 | 0 | 0 | 2018-02-25 08:00 | 8 | 1 | 33.0232 | 6.9349
2018-02-25 09:00 | 9 | 1 | 86.2867 | 18.2065 | 2018-02-25 09:00 | 9 | 1 | 86.8162 | 17.6845 | 2018-02-25 09:00 | 9 | 1 | 0 | 0 | 2018-02-25 09:00 | 9 | 1 | 32.9902 | 6.9279
2018-02-25 10:00 | 10 | 1 | 86.2882 | 18.2068 | 2018-02-25 10:00 | 10 | 1 | 86.8528 | 17.6919 | 2018-02-25 10:00 | 10 | 1 | 0 | 0 | 2018-02-25 10:00 | 10 | 1 | 33.0041 | 6.9309
2018-02-25 11:00 | 11 | 1 | 86.1845 | 18.1849 | 2018-02-25 11:00 | 11 | 1 | 86.743 | 17.6695 | 2018-02-25 11:00 | 11 | 1 | 0 | 0 | 2018-02-25 11:00 | 11 | 1 | 32.9623 | 6.9221
2018-02-25 12:00 | 12 | 1 | 86.1418 | 18.1759 | 2018-02-25 12:00 | 12 | 1 | 86.714 | 17.6636 | 2018-02-25 12:00 | 12 | 1 | 0 | 0 | 2018-02-25 12:00 | 12 | 1 | 32.9513 | 6.9198
2018-02-25 13:00 | 13 | 1 | 86.1479 | 18.1772 | 2018-02-25 13:00 | 13 | 1 | 86.7659 | 17.6742 | 2018-02-25 13:00 | 13 | 1 | 0 | 0 | 2018-02-25 13:00 | 13 | 1 | 32.971 | 6.9239
2018-02-25 14:00 | 14 | 1 | 86.1112 | 18.1695 | 2018-02-25 14:00 | 14 | 1 | 86.7018 | 17.6612 | 2018-02-25 14:00 | 14 | 1 | 0 | 0 | 2018-02-25 14:00 | 14 | 1 | 32.9467 | 6.9188
2018-02-25 15:00 | 15 | 1 | 86.2455 | 18.1978 | 2018-02-25 15:00 | 15 | 1 | 86.8482 | 17.691 | 2018-02-25 15:00 | 15 | 1 | 0 | 0 | 2018-02-25 15:00 | 15 | 1 | 33.0023 | 6.9305
2018-02-25 16:00 | 16 | 1 | 86.3447 | 18.2187 | 2018-02-25 16:00 | 16 | 1 | 86.9398 | 17.7096 | 2018-02-25 16:00 | 16 | 1 | 0 | 0 | 2018-02-25 16:00 | 16 | 1 | 33.0371 | 6.9378
2018-02-25 17:00 | 17 | 1 | 86.4805 | 18.2474 | 2018-02-25 17:00 | 17 | 1 | 86.9856 | 17.719 | 2018-02-25 17:00 | 17 | 1 | 0 | 0 | 2018-02-25 17:00 | 17 | 1 | 33.0545 | 6.9415
2018-02-25 18:00 | 18 | 1 | 86.4332 | 18.2374 | 2018-02-25 18:00 | 18 | 1 | 86.92 | 17.7056 | 2018-02-25 18:00 | 18 | 1 | 0 | 0 | 2018-02-25 18:00 | 18 | 1 | 33.0296 | 6.9362
2018-02-25 19:00 | 19 | 1 | 85.6794 | 18.0784 | 2018-02-25 19:00 | 19 | 1 | 85.9266 | 17.5032 | 2018-02-25 19:00 | 19 | 1 | 0 | 0 | 2018-02-25 19:00 | 19 | 1 | 32.6521 | 6.8569
2018-02-25 20:00 | 20 | 1 | 86.3294 | 18.2155 | 2018-02-25 20:00 | 20 | 1 | 86.5888 | 17.6381 | 2018-02-25 20:00 | 20 | 1 | 0 | 0 | 2018-02-25 20:00 | 20 | 1 | 32.9037 | 6.9098
2018-02-25 21:00 | 21 | 1 | 86.3569 | 18.2213 | 2018-02-25 21:00 | 21 | 1 | 86.6728 | 17.6552 | 2018-02-25 21:00 | 21 | 1 | 0 | 0 | 2018-02-25 21:00 | 21 | 1 | 32.9357 | 6.9165
2018-02-25 22:00 | 22 | 1 | 86.4881 | 18.249 | 2018-02-25 22:00 | 22 | 1 | 86.8086 | 17.6829 | 2018-02-25 22:00 | 22 | 1 | 0 | 0 | 2018-02-25 22:00 | 22 | 1 | 32.9873 | 6.9273
2018-02-25 23:00 | 23 | 1 | 86.4332 | 18.2374 | 2018-02-25 23:00 | 23 | 1 | 86.7353 | 17.668 | 2018-02-25 23:00 | 23 | 1 | 0 | 0 | 2018-02-25 23:00 | 23 | 1 | 32.9594 | 6.9215
2018-02-26 | 0 | 2 | 86.4088 | 18.2323 | 2018-02-26 | 0 | 2 | 86.7002 | 17.6608 | 2018-02-26 | 0 | 2 | 86.9352 | 18.4303 | 2018-02-26 | 0 | 2 | 65.9815 | 13.8561
2018-02-26 01:00 | 1 | 2 | 86.0426 | 18.155 | 2018-02-26 01:00 | 1 | 2 | 86.3127 | 17.5819 | 2018-02-26 01:00 | 1 | 2 | 86.5278 | 18.3439 | 2018-02-26 01:00 | 1 | 2 | 65.6794 | 13.7927
2018-02-26 02:00 | 2 | 2 | 86.392 | 18.2287 | 2018-02-26 02:00 | 2 | 2 | 86.6392 | 17.6484 | 2018-02-26 02:00 | 2 | 2 | 86.8421 | 18.4105 | 2018-02-26 02:00 | 2 | 2 | 65.9229 | 13.8438
2018-02-26 03:00 | 3 | 2 | 86.2776 | 18.2046 | 2018-02-26 03:00 | 3 | 2 | 86.5766 | 17.6357 | 2018-02-26 03:00 | 3 | 2 | 86.7536 | 18.3918 | 2018-02-26 03:00 | 3 | 2 | 65.8655 | 13.8317
2018-02-26 04:00 | 4 | 2 | 86.5034 | 18.2522 | 2018-02-26 04:00 | 4 | 2 | 86.8849 | 17.6985 | 2018-02-26 04:00 | 4 | 2 | 87.0283 | 18.45 | 2018-02-26 04:00 | 4 | 2 | 66.087 | 13.8783
2018-02-26 05:00 | 5 | 2 | 86.3661 | 18.2232 | 2018-02-26 05:00 | 5 | 2 | 86.772 | 17.6755 | 2018-02-26 05:00 | 5 | 2 | 87.0054 | 18.4451 | 2018-02-26 05:00 | 5 | 2 | 66.0354 | 13.8674
2018-02-26 06:00 | 6 | 2 | 86.2898 | 18.2071 | 2018-02-26 06:00 | 6 | 2 | 86.6499 | 17.6506 | 2018-02-26 06:00 | 6 | 2 | 86.8147 | 18.4047 | 2018-02-26 06:00 | 6 | 2 | 65.9165 | 13.8425
2018-02-26 07:00 | 7 | 2 | 86.2043 | 18.1891 | 2018-02-26 07:00 | 7 | 2 | 86.5278 | 17.6257 | 2018-02-26 07:00 | 7 | 2 | 86.7079 | 18.3821 | 2018-02-26 07:00 | 7 | 2 | 65.8296 | 13.8242
2018-02-26 08:00 | 8 | 2 | 86.3355 | 18.2168 | 2018-02-26 08:00 | 8 | 2 | 86.5461 | 17.6294 | 2018-02-26 08:00 | 8 | 2 | 86.8025 | 18.4021 | 2018-02-26 08:00 | 8 | 2 | 65.8725 | 13.8332
2018-02-26 09:00 | 9 | 2 | 86.3798 | 18.2261 | 2018-02-26 09:00 | 9 | 2 | 86.7262 | 17.6661 | 2018-02-26 09:00 | 9 | 2 | 86.8711 | 18.4167 | 2018-02-26 09:00 | 9 | 2 | 65.967 | 13.8531
2018-02-26 10:00 | 10 | 2 | 86.2272 | 18.1939 | 2018-02-26 10:00 | 10 | 2 | 86.5156 | 17.6232 | 2018-02-26 10:00 | 10 | 2 | 86.714 | 18.3834 | 2018-02-26 10:00 | 10 | 2 | 65.8272 | 13.8237
2018-02-26 11:00 | 11 | 2 | 86.2119 | 18.1907 | 2018-02-26 11:00 | 11 | 2 | 86.5141 | 17.6229 | 2018-02-26 11:00 | 11 | 2 | 86.7201 | 18.3847 | 2018-02-26 11:00 | 11 | 2 | 65.829 | 13.8241
2018-02-26 12:00 | 12 | 2 | 86.389 | 18.2281 | 2018-02-26 12:00 | 12 | 2 | 86.6835 | 17.6574 | 2018-02-26 12:00 | 12 | 2 | 86.8574 | 18.4138 | 2018-02-26 12:00 | 12 | 2 | 65.9455 | 13.8486
2018-02-26 13:00 | 13 | 2 | 86.4027 | 18.231 | 2018-02-26 13:00 | 13 | 2 | 86.6224 | 17.645 | 2018-02-26 13:00 | 13 | 2 | 86.7475 | 18.3905 | 2018-02-26 13:00 | 13 | 2 | 65.8806 | 13.8349
2018-02-26 14:00 | 14 | 2 | 86.3783 | 18.2258 | 2018-02-26 14:00 | 14 | 2 | 86.6606 | 17.6528 | 2018-02-26 14:00 | 14 | 2 | 86.7903 | 18.3995 | 2018-02-26 14:00 | 14 | 2 | 65.9113 | 13.8414
2018-02-26 15:00 | 15 | 2 | 86.3355 | 18.2168 | 2018-02-26 15:00 | 15 | 2 | 86.5248 | 17.6251 | 2018-02-26 15:00 | 15 | 2 | 86.7384 | 18.3885 | 2018-02-26 15:00 | 15 | 2 | 65.84 | 13.8264
2018-02-26 16:00 | 16 | 2 | 86.3493 | 18.2197 | 2018-02-26 16:00 | 16 | 2 | 86.4912 | 17.6183 | 2018-02-26 16:00 | 16 | 2 | 86.685 | 18.3772 | 2018-02-26 16:00 | 16 | 2 | 65.807 | 13.8195
2018-02-26 17:00 | 17 | 2 | 86.244 | 18.1975 | 2018-02-26 17:00 | 17 | 2 | 86.4683 | 17.6136 | 2018-02-26 17:00 | 17 | 2 | 86.6743 | 18.375 | 2018-02-26 17:00 | 17 | 2 | 65.7942 | 13.8168
2018-02-26 18:00 | 18 | 2 | 86.3142 | 18.2123 | 2018-02-26 18:00 | 18 | 2 | 86.4378 | 17.6074 | 2018-02-26 18:00 | 18 | 2 | 86.5934 | 18.3578 | 2018-02-26 18:00 | 18 | 2 | 65.7519 | 13.8079
2018-02-26 19:00 | 19 | 2 | 86.2089 | 18.1901 | 2018-02-26 19:00 | 19 | 2 | 86.3508 | 17.5897 | 2018-02-26 19:00 | 19 | 2 | 86.5583 | 18.3504 | 2018-02-26 19:00 | 19 | 2 | 65.7055 | 13.7981
2018-02-26 20:00 | 20 | 2 | 86.2181 | 18.192 | 2018-02-26 20:00 | 20 | 2 | 86.4836 | 17.6167 | 2018-02-26 20:00 | 20 | 2 | 86.6896 | 18.3782 | 2018-02-26 20:00 | 20 | 2 | 65.8058 | 13.8192
2018-02-26 21:00 | 21 | 2 | 86.1494 | 18.1775 | 2018-02-26 21:00 | 21 | 2 | 86.4759 | 17.6151 | 2018-02-26 21:00 | 21 | 2 | 86.63 | 18.3656 | 2018-02-26 21:00 | 21 | 2 | 65.7802 | 13.8139
2018-02-26 22:00 | 22 | 2 | 86.2593 | 18.2007 | 2018-02-26 22:00 | 22 | 2 | 86.5522 | 17.6307 | 2018-02-26 22:00 | 22 | 2 | 86.6468 | 18.3691 | 2018-02-26 22:00 | 22 | 2 | 65.8156 | 13.8213
2018-02-26 23:00 | 23 | 2 | 86.4424 | 18.2393 | 2018-02-26 23:00 | 23 | 2 | 86.8055 | 17.6823 | 2018-02-26 23:00 | 23 | 2 | 86.8864 | 18.4199 | 2018-02-26 23:00 | 23 | 2 | 66.0029 | 13.8606
2018-02-27 | 0 | 3 | 86.4637 | 18.2438 | 2018-02-27 | 0 | 3 | 0 | 0 | 2018-02-27 | 0 | 3 | 0 | 0 | 2018-02-27 | 0 | 3 | 0 | 0
2018-02-27 01:00 | 1 | 3 | 86.5629 | 18.2648 | 2018-02-27 01:00 | 1 | 3 | 0 | 0 | 2018-02-27 01:00 | 1 | 3 | 0 | 0 | 2018-02-27 01:00 | 1 | 3 | 0 | 0
2018-02-27 02:00 | 2 | 3 | 86.3706 | 18.2242 | 2018-02-27 02:00 | 2 | 3 | 0 | 0 | 2018-02-27 02:00 | 2 | 3 | 0 | 0 | 2018-02-27 02:00 | 2 | 3 | 0 | 0
2018-02-27 03:00 | 3 | 3 | 86.3523 | 18.2203 | 2018-02-27 03:00 | 3 | 3 | 0 | 0 | 2018-02-27 03:00 | 3 | 3 | 0 | 0 | 2018-02-27 03:00 | 3 | 3 | 0 | 0
2018-02-27 04:00 | 4 | 3 | 86.3676 | 18.2236 | 2018-02-27 04:00 | 4 | 3 | 0 | 0 | 2018-02-27 04:00 | 4 | 3 | 0 | 0 | 2018-02-27 04:00 | 4 | 3 | 0 | 0
2018-02-27 05:00 | 5 | 3 | 86.4027 | 18.231 | 2018-02-27 05:00 | 5 | 3 | 0 | 0 | 2018-02-27 05:00 | 5 | 3 | 0 | 0 | 2018-02-27 05:00 | 5 | 3 | 0 | 0
2018-02-27 06:00 | 6 | 3 | 86.4652 | 18.2442 | 2018-02-27 06:00 | 6 | 3 | 0 | 0 | 2018-02-27 06:00 | 6 | 3 | 0 | 0 | 2018-02-27 06:00 | 6 | 3 | 0 | 0
2018-02-27 07:00 | 7 | 3 | 86.4012 | 18.2307 | 2018-02-27 07:00 | 7 | 3 | 0 | 0 | 2018-02-27 07:00 | 7 | 3 | 0 | 0 | 2018-02-27 07:00 | 7 | 3 | 0 | 0
2018-02-27 08:00 | 8 | 3 | 86.4515 | 18.2413 | 2018-02-27 08:00 | 8 | 3 | 0 | 0 | 2018-02-27 08:00 | 8 | 3 | 0 | 0 | 2018-02-27 08:00 | 8 | 3 | 0 | 0
2018-02-27 09:00 | 9 | 3 | 86.2028 | 18.1888 | 2018-02-27 09:00 | 9 | 3 | 0 | 0 | 2018-02-27 09:00 | 9 | 3 | 0 | 0 | 2018-02-27 09:00 | 9 | 3 | 0 | 0
2018-02-27 10:00 | 10 | 3 | 86.2715 | 18.2033 | 2018-02-27 10:00 | 10 | 3 | 0 | 0 | 2018-02-27 10:00 | 10 | 3 | 0 | 0 | 2018-02-27 10:00 | 10 | 3 | 0 | 0
2018-02-27 11:00 | 11 | 3 | 86.7567 | 18.3057 | 2018-02-27 11:00 | 11 | 3 | 0 | 0 | 2018-02-27 11:00 | 11 | 3 | 0 | 0 | 2018-02-27 11:00 | 11 | 3 | 0 | 0
2018-02-27 12:00 | 12 | 3 | 86.6194 | 18.2767 | 2018-02-27 12:00 | 12 | 3 | 0 | 0 | 2018-02-27 12:00 | 12 | 3 | 0 | 0 | 2018-02-27 12:00 | 12 | 3 | 0 | 0
2018-02-27 13:00 | 13 | 3 | 86.6377 | 18.2806 | 2018-02-27 13:00 | 13 | 3 | 0 | 0 | 2018-02-27 13:00 | 13 | 3 | 0 | 0 | 2018-02-27 13:00 | 13 | 3 | 0 | 0
2018-02-27 14:00 | 14 | 3 | 86.8757 | 18.3308 | 2018-02-27 14:00 | 14 | 3 | 0 | 0 | 2018-02-27 14:00 | 14 | 3 | 0 | 0 | 2018-02-27 14:00 | 14 | 3 | 0 | 0
2018-02-27 15:00 | 15 | 3 | 86.7994 | 18.3147 | 2018-02-27 15:00 | 15 | 3 | 0 | 0 | 2018-02-27 15:00 | 15 | 3 | 0 | 0 | 2018-02-27 15:00 | 15 | 3 | 0 | 0
2018-02-27 16:00 | 16 | 3 | 86.7674 | 18.3079 | 2018-02-27 16:00 | 16 | 3 | 0 | 0 | 2018-02-27 16:00 | 16 | 3 | 0 | 0 | 2018-02-27 16:00 | 16 | 3 | 0 | 0
2018-02-27 17:00 | 17 | 3 | 86.7384 | 18.3018 | 2018-02-27 17:00 | 17 | 3 | 0 | 0 | 2018-02-27 17:00 | 17 | 3 | 0 | 0 | 2018-02-27 17:00 | 17 | 3 | 0 | 0
2018-02-27 18:00 | 18 | 3 | 86.7124 | 18.2963 | 2018-02-27 18:00 | 18 | 3 | 0 | 0 | 2018-02-27 18:00 | 18 | 3 | 0 | 0 | 2018-02-27 18:00 | 18 | 3 | 0 | 0
2018-02-27 19:00 | 19 | 3 | 86.8376 | 18.3227 | 2018-02-27 19:00 | 19 | 3 | 0 | 0 | 2018-02-27 19:00 | 19 | 3 | 0 | 0 | 2018-02-27 19:00 | 19 | 3 | 0 | 0
2018-02-27 20:00 | 20 | 3 | 86.627 | 18.2783 | 2018-02-27 20:00 | 20 | 3 | 0 | 0 | 2018-02-27 20:00 | 20 | 3 | 0 | 0 | 2018-02-27 20:00 | 20 | 3 | 0 | 0
2018-02-27 21:00 | 21 | 3 | 86.6239 | 18.2776 | 2018-02-27 21:00 | 21 | 3 | 0 | 0 | 2018-02-27 21:00 | 21 | 3 | 0 | 0 | 2018-02-27 21:00 | 21 | 3 | 0 | 0
2018-02-27 22:00 | 22 | 3 | 86.714 | 18.2967 | 2018-02-27 22:00 | 22 | 3 | 0 | 0 | 2018-02-27 22:00 | 22 | 3 | 0 | 0 | 2018-02-27 22:00 | 22 | 3 | 0 | 0
2018-02-27 23:00 | 23 | 3 | 86.8971 | 18.3353 | 2018-02-27 23:00 | 23 | 3 | 0 | 0 | 2018-02-27 23:00 | 23 | 3 | 0 | 0 | 2018-02-27 23:00 | 23 | 3 | 0 | 0
2018-02-28 | 0 | 4 | 0 | 0 | 2018-02-28 | 0 | 4 | 0 | 0 | 2018-02-28 | 0 | 4 | 86.6712 | 18.3743 | 2018-02-28 | 0 | 4 | 32.9351 | 6.9164
2018-02-28 01:00 | 1 | 4 | 0 | 0 | 2018-02-28 01:00 | 1 | 4 | 0 | 0 | 2018-02-28 01:00 | 1 | 4 | 86.511 | 18.3403 | 2018-02-28 01:00 | 1 | 4 | 32.8742 | 6.9036
2018-02-28 02:00 | 2 | 4 | 0 | 0 | 2018-02-28 02:00 | 2 | 4 | 0 | 0 | 2018-02-28 02:00 | 2 | 4 | 86.7628 | 18.3937 | 2018-02-28 02:00 | 2 | 4 | 32.9699 | 6.9237
2018-02-28 03:00 | 3 | 4 | 0 | 0 | 2018-02-28 03:00 | 3 | 4 | 0 | 0 | 2018-02-28 03:00 | 3 | 4 | 86.7384 | 18.3885 | 2018-02-28 03:00 | 3 | 4 | 32.9606 | 6.9217
2018-02-28 04:00 | 4 | 4 | 0 | 0 | 2018-02-28 04:00 | 4 | 4 | 0 | 0 | 2018-02-28 04:00 | 4 | 4 | 86.8376 | 18.4096 | 2018-02-28 04:00 | 4 | 4 | 32.9983 | 6.9296
2018-02-28 05:00 | 5 | 4 | 0 | 0 | 2018-02-28 05:00 | 5 | 4 | 0 | 0 | 2018-02-28 05:00 | 5 | 4 | 87.0222 | 18.4487 | 2018-02-28 05:00 | 5 | 4 | 33.0684 | 6.9444
2018-02-28 06:00 | 6 | 4 | 0 | 0 | 2018-02-28 06:00 | 6 | 4 | 0 | 0 | 2018-02-28 06:00 | 6 | 4 | 86.9627 | 18.4361 | 2018-02-28 06:00 | 6 | 4 | 33.0458 | 6.9396
2018-02-28 07:00 | 7 | 4 | 0 | 0 | 2018-02-28 07:00 | 7 | 4 | 0 | 0 | 2018-02-28 07:00 | 7 | 4 | 87.1321 | 18.472 | 2018-02-28 07:00 | 7 | 4 | 33.1102 | 6.9531
2018-02-28 08:00 | 8 | 4 | 0 | 0 | 2018-02-28 08:00 | 8 | 4 | 0 | 0 | 2018-02-28 08:00 | 8 | 4 | 87.1931 | 18.4849 | 2018-02-28 08:00 | 8 | 4 | 33.1334 | 6.958
2018-02-28 09:00 | 9 | 4 | 0 | 0 | 2018-02-28 09:00 | 9 | 4 | 0 | 0 | 2018-02-28 09:00 | 9 | 4 | 86.7155 | 18.3837 | 2018-02-28 09:00 | 9 | 4 | 32.9519 | 6.9199
2018-02-28 10:00 | 10 | 4 | 0 | 0 | 2018-02-28 10:00 | 10 | 4 | 0 | 0 | 2018-02-28 10:00 | 10 | 4 | 86.6743 | 18.375 | 2018-02-28 10:00 | 10 | 4 | 32.9362 | 6.9166
2018-02-28 11:00 | 11 | 4 | 0 | 0 | 2018-02-28 11:00 | 11 | 4 | 0 | 0 | 2018-02-28 11:00 | 11 | 4 | 86.8956 | 18.4219 | 2018-02-28 11:00 | 11 | 4 | 33.0203 | 6.9343
2018-02-28 12:00 | 12 | 4 | 0 | 0 | 2018-02-28 12:00 | 12 | 4 | 0 | 0 | 2018-02-28 12:00 | 12 | 4 | 86.9276 | 18.4287 | 2018-02-28 12:00 | 12 | 4 | 33.0325 | 6.9368
2018-02-28 13:00 | 13 | 4 | 0 | 0 | 2018-02-28 13:00 | 13 | 4 | 0 | 0 | 2018-02-28 13:00 | 13 | 4 | 87.2541 | 18.4979 | 2018-02-28 13:00 | 13 | 4 | 33.1566 | 6.9629
2018-02-28 14:00 | 14 | 4 | 0 | 0 | 2018-02-28 14:00 | 14 | 4 | 0 | 0 | 2018-02-28 14:00 | 14 | 4 | 87.4037 | 18.5296 | 2018-02-28 14:00 | 14 | 4 | 33.2134 | 6.9748
2018-02-28 15:00 | 15 | 4 | 0 | 0 | 2018-02-28 15:00 | 15 | 4 | 0 | 0 | 2018-02-28 15:00 | 15 | 4 | 87.2129 | 18.4891 | 2018-02-28 15:00 | 15 | 4 | 33.1409 | 6.9596
2018-02-28 16:00 | 16 | 4 | 0 | 0 | 2018-02-28 16:00 | 16 | 4 | 0 | 0 | 2018-02-28 16:00 | 16 | 4 | 86.9718 | 18.438 | 2018-02-28 16:00 | 16 | 4 | 33.0493 | 6.9403
2018-02-28 17:00 | 17 | 4 | 0 | 0 | 2018-02-28 17:00 | 17 | 4 | 0 | 0 | 2018-02-28 17:00 | 17 | 4 | 87.1397 | 18.4736 | 2018-02-28 17:00 | 17 | 4 | 33.1131 | 6.9537
2018-02-28 18:00 | 18 | 4 | 0 | 0 | 2018-02-28 18:00 | 18 | 4 | 0 | 0 | 2018-02-28 18:00 | 18 | 4 | 87.2435 | 18.4956 | 2018-02-28 18:00 | 18 | 4 | 33.1525 | 6.962
2018-02-28 19:00 | 19 | 4 | 0 | 0 | 2018-02-28 19:00 | 19 | 4 | 0 | 0 | 2018-02-28 19:00 | 19 | 4 | 86.8894 | 18.4206 | 2018-02-28 19:00 | 19 | 4 | 33.018 | 6.9338
2018-02-28 20:00 | 20 | 4 | 0 | 0 | 2018-02-28 20:00 | 20 | 4 | 0 | 0 | 2018-02-28 20:00 | 20 | 4 | 87.1839 | 18.483 | 2018-02-28 20:00 | 20 | 4 | 33.1299 | 6.9573
2018-02-28 21:00 | 21 | 4 | 0 | 0 | 2018-02-28 21:00 | 21 | 4 | 0 | 0 | 2018-02-28 21:00 | 21 | 4 | 87.2419 | 18.4953 | 2018-02-28 21:00 | 21 | 4 | 33.1519 | 6.9619
2018-02-28 22:00 | 22 | 4 | 0 | 0 | 2018-02-28 22:00 | 22 | 4 | 0 | 0 | 2018-02-28 22:00 | 22 | 4 | 87.1733 | 18.4807 | 2018-02-28 22:00 | 22 | 4 | 33.1259 | 6.9564
2018-02-28 23:00 | 23 | 4 | 0 | 0 | 2018-02-28 23:00 | 23 | 4 | 0 | 0 | 2018-02-28 23:00 | 23 | 4 | 87.2557 | 18.4982 | 2018-02-28 23:00 | 23 | 4 | 33.1572 | 6.963
2018-03-01 | 0 | 5 | 86.5492 | 18.2619 | 2018-03-01 | 0 | 5 | 0 | 0 | 2018-03-01 | 0 | 5 | 0 | 0 | 2018-03-01 | 0 | 5 | 0 | 0
2018-03-01 01:00 | 1 | 5 | 86.7201 | 18.2979 | 2018-03-01 01:00 | 1 | 5 | 0 | 0 | 2018-03-01 01:00 | 1 | 5 | 0 | 0 | 2018-03-01 01:00 | 1 | 5 | 0 | 0
2018-03-01 02:00 | 2 | 5 | 86.5095 | 18.2535 | 2018-03-01 02:00 | 2 | 5 | 0 | 0 | 2018-03-01 02:00 | 2 | 5 | 0 | 0 | 2018-03-01 02:00 | 2 | 5 | 0 | 0
2018-03-01 03:00 | 3 | 5 | 86.4576 | 18.2426 | 2018-03-01 03:00 | 3 | 5 | 0 | 0 | 2018-03-01 03:00 | 3 | 5 | 0 | 0 | 2018-03-01 03:00 | 3 | 5 | 0 | 0
2018-03-01 04:00 | 4 | 5 | 86.6316 | 18.2793 | 2018-03-01 04:00 | 4 | 5 | 0 | 0 | 2018-03-01 04:00 | 4 | 5 | 0 | 0 | 2018-03-01 04:00 | 4 | 5 | 0 | 0
2018-03-01 05:00 | 5 | 5 | 86.569 | 18.2661 | 2018-03-01 05:00 | 5 | 5 | 0 | 0 | 2018-03-01 05:00 | 5 | 5 | 0 | 0 | 2018-03-01 05:00 | 5 | 5 | 0 | 0
2018-03-01 06:00 | 6 | 5 | 86.6468 | 18.2825 | 2018-03-01 06:00 | 6 | 5 | 0 | 0 | 2018-03-01 06:00 | 6 | 5 | 0 | 0 | 2018-03-01 06:00 | 6 | 5 | 0 | 0
2018-03-01 07:00 | 7 | 5 | 86.6361 | 18.2802 | 2018-03-01 07:00 | 7 | 5 | 0 | 0 | 2018-03-01 07:00 | 7 | 5 | 0 | 0 | 2018-03-01 07:00 | 7 | 5 | 0 | 0
2018-03-01 08:00 | 8 | 5 | 86.6819 | 18.2899 | 2018-03-01 08:00 | 8 | 5 | 0 | 0 | 2018-03-01 08:00 | 8 | 5 | 0 | 0 | 2018-03-01 08:00 | 8 | 5 | 0 | 0
2018-03-01 09:00 | 9 | 5 | 86.7094 | 18.2957 | 2018-03-01 09:00 | 9 | 5 | 0 | 0 | 2018-03-01 09:00 | 9 | 5 | 0 | 0 | 2018-03-01 09:00 | 9 | 5 | 0 | 0
2018-03-01 10:00 | 10 | 5 | 86.7933 | 18.3134 | 2018-03-01 10:00 | 10 | 5 | 0 | 0 | 2018-03-01 10:00 | 10 | 5 | 0 | 0 | 2018-03-01 10:00 | 10 | 5 | 0 | 0
2018-03-01 11:00 | 11 | 5 | 86.8009 | 18.315 | 2018-03-01 11:00 | 11 | 5 | 0 | 0 | 2018-03-01 11:00 | 11 | 5 | 0 | 0 | 2018-03-01 11:00 | 11 | 5 | 0 | 0
2018-03-01 12:00 | 12 | 5 | 86.6728 | 18.288 | 2018-03-01 12:00 | 12 | 5 | 0 | 0 | 2018-03-01 12:00 | 12 | 5 | 0 | 0 | 2018-03-01 12:00 | 12 | 5 | 0 | 0
2018-03-01 13:00 | 13 | 5 | 86.6316 | 18.2793 | 2018-03-01 13:00 | 13 | 5 | 0 | 0 | 2018-03-01 13:00 | 13 | 5 | 0 | 0 | 2018-03-01 13:00 | 13 | 5 | 0 | 0
2018-03-01 14:00 | 14 | 5 | 86.6316 | 18.2793 | 2018-03-01 14:00 | 14 | 5 | 0 | 0 | 2018-03-01 14:00 | 14 | 5 | 0 | 0 | 2018-03-01 14:00 | 14 | 5 | 0 | 0
2018-03-01 15:00 | 15 | 5 | 86.6636 | 18.286 | 2018-03-01 15:00 | 15 | 5 | 0 | 0 | 2018-03-01 15:00 | 15 | 5 | 0 | 0 | 2018-03-01 15:00 | 15 | 5 | 0 | 0
2018-03-01 16:00 | 16 | 5 | 86.5568 | 18.2635 | 2018-03-01 16:00 | 16 | 5 | 0 | 0 | 2018-03-01 16:00 | 16 | 5 | 0 | 0 | 2018-03-01 16:00 | 16 | 5 | 0 | 0
2018-03-01 17:00 | 17 | 5 | 86.6865 | 18.2909 | 2018-03-01 17:00 | 17 | 5 | 0 | 0 | 2018-03-01 17:00 | 17 | 5 | 0 | 0 | 2018-03-01 17:00 | 17 | 5 | 0 | 0
2018-03-01 18:00 | 18 | 5 | 86.7262 | 18.2992 | 2018-03-01 18:00 | 18 | 5 | 0 | 0 | 2018-03-01 18:00 | 18 | 5 | 0 | 0 | 2018-03-01 18:00 | 18 | 5 | 0 | 0
2018-03-01 19:00 | 19 | 5 | 86.5187 | 18.2554 | 2018-03-01 19:00 | 19 | 5 | 0 | 0 | 2018-03-01 19:00 | 19 | 5 | 0 | 0 | 2018-03-01 19:00 | 19 | 5 | 0 | 0
2018-03-01 20:00 | 20 | 5 | 86.5766 | 18.2677 | 2018-03-01 20:00 | 20 | 5 | 0 | 0 | 2018-03-01 20:00 | 20 | 5 | 0 | 0 | 2018-03-01 20:00 | 20 | 5 | 0 | 0
2018-03-01 21:00 | 21 | 5 | 86.6194 | 18.2767 | 2018-03-01 21:00 | 21 | 5 | 0 | 0 | 2018-03-01 21:00 | 21 | 5 | 0 | 0 | 2018-03-01 21:00 | 21 | 5 | 0 | 0
2018-03-01 22:00 | 22 | 5 | 86.6743 | 18.2883 | 2018-03-01 22:00 | 22 | 5 | 0 | 0 | 2018-03-01 22:00 | 22 | 5 | 0 | 0 | 2018-03-01 22:00 | 22 | 5 | 0 | 0
2018-03-01 23:00 | 23 | 5 | 86.5644 | 18.2651 | 2018-03-01 23:00 | 23 | 5 | 0 | 0 | 2018-03-01 23:00 | 23 | 5 | 0 | 0 | 2018-03-01 23:00 | 23 | 5 | 0 | 0
2018-03-02 | 0 | 6 | 86.2226 | 18.193 | 2018-03-02 | 0 | 6 | 86.688 | 17.6583 | 2018-03-02 | 0 | 6 | 0 | 0 | 2018-03-02 | 0 | 6 | 32.9414 | 6.9177
2018-03-02 01:00 | 1 | 6 | 86.1128 | 18.1698 | 2018-03-02 01:00 | 1 | 6 | 86.5232 | 17.6248 | 2018-03-02 01:00 | 1 | 6 | 0 | 0 | 2018-03-02 01:00 | 1 | 6 | 32.8788 | 6.9046
2018-03-02 02:00 | 2 | 6 | 86.2791 | 18.2049 | 2018-03-02 02:00 | 2 | 6 | 86.6896 | 17.6587 | 2018-03-02 02:00 | 2 | 6 | 0 | 0 | 2018-03-02 02:00 | 2 | 6 | 32.942 | 6.9178
2018-03-02 03:00 | 3 | 6 | 86.0014 | 18.1463 | 2018-03-02 03:00 | 3 | 6 | 86.4485 | 17.6096 | 2018-03-02 03:00 | 3 | 6 | 0 | 0 | 2018-03-02 03:00 | 3 | 6 | 32.8504 | 6.8986
2018-03-02 04:00 | 4 | 6 | 86.0533 | 18.1572 | 2018-03-02 04:00 | 4 | 6 | 86.4347 | 17.6067 | 2018-03-02 04:00 | 4 | 6 | 0 | 0 | 2018-03-02 04:00 | 4 | 6 | 32.8452 | 6.8975
2018-03-02 05:00 | 5 | 6 | 86.2257 | 18.1936 | 2018-03-02 05:00 | 5 | 6 | 86.6117 | 17.6428 | 2018-03-02 05:00 | 5 | 6 | 0 | 0 | 2018-03-02 05:00 | 5 | 6 | 32.9124 | 6.9116
2018-03-02 06:00 | 6 | 6 | 86.4332 | 18.2374 | 2018-03-02 06:00 | 6 | 6 | 86.9352 | 17.7087 | 2018-03-02 06:00 | 6 | 6 | 0 | 0 | 2018-03-02 06:00 | 6 | 6 | 33.0354 | 6.9374
2018-03-02 07:00 | 7 | 6 | 86.5873 | 18.2699 | 2018-03-02 07:00 | 7 | 6 | 87.0619 | 17.7345 | 2018-03-02 07:00 | 7 | 6 | 0 | 0 | 2018-03-02 07:00 | 7 | 6 | 33.0835 | 6.9475
2018-03-02 08:00 | 8 | 6 | 86.3691 | 18.2239 | 2018-03-02 08:00 | 8 | 6 | 86.7811 | 17.6773 | 2018-03-02 08:00 | 8 | 6 | 0 | 0 | 2018-03-02 08:00 | 8 | 6 | 32.9768 | 6.9251
2018-03-02 09:00 | 9 | 6 | 86.334 | 18.2165 | 2018-03-02 09:00 | 9 | 6 | 86.7399 | 17.6689 | 2018-03-02 09:00 | 9 | 6 | 0 | 0 | 2018-03-02 09:00 | 9 | 6 | 32.9612 | 6.9218
2018-03-02 10:00 | 10 | 6 | 86.5126 | 18.2542 | 2018-03-02 10:00 | 10 | 6 | 86.862 | 17.6938 | 2018-03-02 10:00 | 10 | 6 | 0 | 0 | 2018-03-02 10:00 | 10 | 6 | 33.0076 | 6.9316
2018-03-02 11:00 | 11 | 6 | 86.5003 | 18.2516 | 2018-03-02 11:00 | 11 | 6 | 86.9306 | 17.7078 | 2018-03-02 11:00 | 11 | 6 | 0 | 0 | 2018-03-02 11:00 | 11 | 6 | 33.0336 | 6.9371
2018-03-02 12:00 | 12 | 6 | 86.7002 | 18.2937 | 2018-03-02 12:00 | 12 | 6 | 87.1412 | 17.7507 | 2018-03-02 12:00 | 12 | 6 | 0 | 0 | 2018-03-02 12:00 | 12 | 6 | 33.1137 | 6.9539
2018-03-02 13:00 | 13 | 6 | 86.363 | 18.2226 | 2018-03-02 13:00 | 13 | 6 | 86.8009 | 17.6813 | 2018-03-02 13:00 | 13 | 6 | 0 | 0 | 2018-03-02 13:00 | 13 | 6 | 32.9843 | 6.9267
2018-03-02 14:00 | 14 | 6 | 86.4408 | 18.239 | 2018-03-02 14:00 | 14 | 6 | 86.8635 | 17.6941 | 2018-03-02 14:00 | 14 | 6 | 0 | 0 | 2018-03-02 14:00 | 14 | 6 | 33.0081 | 6.9317
2018-03-02 15:00 | 15 | 6 | 86.2943 | 18.2081 | 2018-03-02 15:00 | 15 | 6 | 86.6743 | 17.6556 | 2018-03-02 15:00 | 15 | 6 | 0 | 0 | 2018-03-02 15:00 | 15 | 6 | 32.9362 | 6.9166
2018-03-02 16:00 | 16 | 6 | 86.3706 | 18.2242 | 2018-03-02 16:00 | 16 | 6 | 86.7491 | 17.6708 | 2018-03-02 16:00 | 16 | 6 | 0 | 0 | 2018-03-02 16:00 | 16 | 6 | 32.9647 | 6.9226
2018-03-02 17:00 | 17 | 6 | 86.2882 | 18.2068 | 2018-03-02 17:00 | 17 | 6 | 86.7445 | 17.6699 | 2018-03-02 17:00 | 17 | 6 | 0 | 0 | 2018-03-02 17:00 | 17 | 6 | 32.9629 | 6.9222
2018-03-02 18:00 | 18 | 6 | 86.1875 | 18.1856 | 2018-03-02 18:00 | 18 | 6 | 86.6667 | 17.654 | 2018-03-02 18:00 | 18 | 6 | 0 | 0 | 2018-03-02 18:00 | 18 | 6 | 32.9333 | 6.916
2018-03-02 19:00 | 19 | 6 | 86.099 | 18.1669 | 2018-03-02 19:00 | 19 | 6 | 86.5431 | 17.6288 | 2018-03-02 19:00 | 19 | 6 | 0 | 0 | 2018-03-02 19:00 | 19 | 6 | 32.8864 | 6.9061
2018-03-02 20:00 | 20 | 6 | 86.1997 | 18.1881 | 2018-03-02 20:00 | 20 | 6 | 86.5187 | 17.6239 | 2018-03-02 20:00 | 20 | 6 | 0 | 0 | 2018-03-02 20:00 | 20 | 6 | 32.8771 | 6.9042
2018-03-02 21:00 | 21 | 6 | 86.3767 | 18.2255 | 2018-03-02 21:00 | 21 | 6 | 86.7247 | 17.6658 | 2018-03-02 21:00 | 21 | 6 | 0 | 0 | 2018-03-02 21:00 | 21 | 6 | 32.9554 | 6.9206
2018-03-02 22:00 | 22 | 6 | 86.3691 | 18.2239 | 2018-03-02 22:00 | 22 | 6 | 86.7659 | 17.6742 | 2018-03-02 22:00 | 22 | 6 | 0 | 0 | 2018-03-02 22:00 | 22 | 6 | 32.971 | 6.9239
2018-03-02 23:00 | 23 | 6 | 86.4012 | 18.2307 | 2018-03-02 23:00 | 23 | 6 | 86.7918 | 17.6795 | 2018-03-02 23:00 | 23 | 6 | 0 | 0 | 2018-03-02 23:00 | 23 | 6 | 32.9809 | 6.926
2018-03-03 | 0 | 7 | 86.0121 | 18.1486 | 2018-03-03 | 0 | 7 | 0 | 0 | 2018-03-03 | 0 | 7 | 86.5507 | 18.3487 | 2018-03-03 | 0 | 7 | 32.8893 | 6.9067
2018-03-03 01:00 | 1 | 7 | 85.919 | 18.1289 | 2018-03-03 01:00 | 1 | 7 | 0 | 0 | 2018-03-03 01:00 | 1 | 7 | 86.5324 | 18.3449 | 2018-03-03 01:00 | 1 | 7 | 32.8823 | 6.9053
2018-03-03 02:00 | 2 | 7 | 86.0533 | 18.1572 | 2018-03-03 02:00 | 2 | 7 | 0 | 0 | 2018-03-03 02:00 | 2 | 7 | 86.6453 | 18.3688 | 2018-03-03 02:00 | 2 | 7 | 32.9252 | 6.9143
2018-03-03 03:00 | 3 | 7 | 86.1677 | 18.1814 | 2018-03-03 03:00 | 3 | 7 | 0 | 0 | 2018-03-03 03:00 | 3 | 7 | 86.7002 | 18.3804 | 2018-03-03 03:00 | 3 | 7 | 32.9461 | 6.9187
2018-03-03 04:00 | 4 | 7 | 86.3081 | 18.211 | 2018-03-03 04:00 | 4 | 7 | 0 | 0 | 2018-03-03 04:00 | 4 | 7 | 86.8513 | 18.4125 | 2018-03-03 04:00 | 4 | 7 | 33.0035 | 6.9307
2018-03-03 05:00 | 5 | 7 | 86.2562 | 18.2001 | 2018-03-03 05:00 | 5 | 7 | 0 | 0 | 2018-03-03 05:00 | 5 | 7 | 86.8605 | 18.4144 | 2018-03-03 05:00 | 5 | 7 | 33.007 | 6.9315
2018-03-03 06:00 | 6 | 7 | 86.1234 | 18.172 | 2018-03-03 06:00 | 6 | 7 | 0 | 0 | 2018-03-03 06:00 | 6 | 7 | 86.6682 | 18.3737 | 2018-03-03 06:00 | 6 | 7 | 32.9339 | 6.9161
2018-03-03 07:00 | 7 | 7 | 86.1906 | 18.1862 | 2018-03-03 07:00 | 7 | 7 | 0 | 0 | 2018-03-03 07:00 | 7 | 7 | 86.7247 | 18.3856 | 2018-03-03 07:00 | 7 | 7 | 32.9554 | 6.9206
2018-03-03 08:00 | 8 | 7 | 86.36 | 18.222 | 2018-03-03 08:00 | 8 | 7 | 0 | 0 | 2018-03-03 08:00 | 8 | 7 | 86.952 | 18.4338 | 2018-03-03 08:00 | 8 | 7 | 33.0418 | 6.9388
2018-03-03 09:00 | 9 | 7 | 86.4912 | 18.2496 | 2018-03-03 09:00 | 9 | 7 | 0 | 0 | 2018-03-03 09:00 | 9 | 7 | 87.0588 | 18.4565 | 2018-03-03 09:00 | 9 | 7 | 33.0823 | 6.9473
2018-03-03 10:00 | 10 | 7 | 86.1982 | 18.1878 | 2018-03-03 10:00 | 10 | 7 | 0 | 0 | 2018-03-03 10:00 | 10 | 7 | 86.6392 | 18.3675 | 2018-03-03 10:00 | 10 | 7 | 32.9229 | 6.9138
2018-03-03 11:00 | 11 | 7 | 86.1707 | 18.182 | 2018-03-03 11:00 | 11 | 7 | 0 | 0 | 2018-03-03 11:00 | 11 | 7 | 86.8849 | 18.4196 | 2018-03-03 11:00 | 11 | 7 | 33.0163 | 6.9334
2018-03-03 12:00 | 12 | 7 | 86.5019 | 18.2519 | 2018-03-03 12:00 | 12 | 7 | 0 | 0 | 2018-03-03 12:00 | 12 | 7 | 87.1504 | 18.4759 | 2018-03-03 12:00 | 12 | 7 | 33.1172 | 6.9546
2018-03-03 13:00 | 13 | 7 | 86.6148 | 18.2757 | 2018-03-03 13:00 | 13 | 7 | 0 | 0 | 2018-03-03 13:00 | 13 | 7 | 87.3167 | 18.5111 | 2018-03-03 13:00 | 13 | 7 | 33.1803 | 6.9679
2018-03-03 14:00 | 14 | 7 | 86.4439 | 18.2397 | 2018-03-03 14:00 | 14 | 7 | 0 | 0 | 2018-03-03 14:00 | 14 | 7 | 87.0832 | 18.4616 | 2018-03-03 14:00 | 14 | 7 | 33.0916 | 6.9492
2018-03-03 15:00 | 15 | 7 | 86.5522 | 18.2625 | 2018-03-03 15:00 | 15 | 7 | 0 | 0 | 2018-03-03 15:00 | 15 | 7 | 87.2938 | 18.5063 | 2018-03-03 15:00 | 15 | 7 | 33.1716 | 6.966
2018-03-03 16:00 | 16 | 7 | 86.5644 | 18.2651 | 2018-03-03 16:00 | 16 | 7 | 0 | 0 | 2018-03-03 16:00 | 16 | 7 | 87.3579 | 18.5199 | 2018-03-03 16:00 | 16 | 7 | 33.196 | 6.9712
2018-03-03 17:00 | 17 | 7 | 86.7445 | 18.3031 | 2018-03-03 17:00 | 17 | 7 | 0 | 0 | 2018-03-03 17:00 | 17 | 7 | 87.57 | 18.5648 | 2018-03-03 17:00 | 17 | 7 | 33.2766 | 6.9881
2018-03-03 18:00 | 18 | 7 | 86.4668 | 18.2445 | 2018-03-03 18:00 | 18 | 7 | 0 | 0 | 2018-03-03 18:00 | 18 | 7 | 87.3014 | 18.5079 | 2018-03-03 18:00 | 18 | 7 | 33.1745 | 6.9667
2018-03-03 19:00 | 19 | 7 | 86.3661 | 18.2232 | 2018-03-03 19:00 | 19 | 7 | 0 | 0 | 2018-03-03 19:00 | 19 | 7 | 87.0954 | 18.4642 | 2018-03-03 19:00 | 19 | 7 | 33.0963 | 6.9502
2018-03-03 20:00 | 20 | 7 | 86.1173 | 18.1708 | 2018-03-03 20:00 | 20 | 7 | 0 | 0 | 2018-03-03 20:00 | 20 | 7 | 86.891 | 18.4209 | 2018-03-03 20:00 | 20 | 7 | 33.0186 | 6.9339
2018-03-03 21:00 | 21 | 7 | 86.1555 | 18.1788 | 2018-03-03 21:00 | 21 | 7 | 0 | 0 | 2018-03-03 21:00 | 21 | 7 | 86.9245 | 18.428 | 2018-03-03 21:00 | 21 | 7 | 33.0313 | 6.9366
2018-03-03 22:00 | 22 | 7 | 86.2211 | 18.1927 | 2018-03-03 22:00 | 22 | 7 | 0 | 0 | 2018-03-03 22:00 | 22 | 7 | 87.0054 | 18.4451 | 2018-03-03 22:00 | 22 | 7 | 33.0621 | 6.943
2018-03-03 23:00 | 23 | 7 | 86.2226 | 18.193 | 2018-03-03 23:00 | 23 | 7 | 0 | 0 | 2018-03-03 23:00 | 23 | 7 | 87.0787 | 18.4607 | 2018-03-03 23:00 | 23 | 7 | 33.0899 | 6.9489
2018-03-04 | 0 | 1 | 86.2364 | 18.1959 | 2018-03-04 | 0 | 1 | 86.7994 | 17.681 | 2018-03-04 | 0 | 1 | 0 | 0 | 2018-03-04 | 0 | 1 | 32.9838 | 6.9266
2018-03-04 01:00 | 1 | 1 | 86.3188 | 18.2133 | 2018-03-04 01:00 | 1 | 1 | 86.952 | 17.7121 | 2018-03-04 01:00 | 1 | 1 | 0 | 0 | 2018-03-04 01:00 | 1 | 1 | 33.0418 | 6.9388
2018-03-04 02:00 | 2 | 1 | 86.2119 | 18.1907 | 2018-03-04 02:00 | 2 | 1 | 86.8177 | 17.6848 | 2018-03-04 02:00 | 2 | 1 | 0 | 0 | 2018-03-04 02:00 | 2 | 1 | 32.9907 | 6.9281
2018-03-04 03:00 | 3 | 1 | 86.1845 | 18.1849 | 2018-03-04 03:00 | 3 | 1 | 86.7857 | 17.6782 | 2018-03-04 03:00 | 3 | 1 | 0 | 0 | 2018-03-04 03:00 | 3 | 1 | 32.9786 | 6.9255
2018-03-04 04:00 | 4 | 1 | 86.2455 | 18.1978 | 2018-03-04 04:00 | 4 | 1 | 86.833 | 17.6879 | 2018-03-04 04:00 | 4 | 1 | 0 | 0 | 2018-03-04 04:00 | 4 | 1 | 32.9965 | 6.9293
2018-03-04 05:00 | 5 | 1 | 86.2333 | 18.1952 | 2018-03-04 05:00 | 5 | 1 | 86.833 | 17.6879 | 2018-03-04 05:00 | 5 | 1 | 0 | 0 | 2018-03-04 05:00 | 5 | 1 | 32.9965 | 6.9293
2018-03-04 06:00 | 6 | 1 | 86.2776 | 18.2046 | 2018-03-04 06:00 | 6 | 1 | 86.8528 | 17.6919 | 2018-03-04 06:00 | 6 | 1 | 0 | 0 | 2018-03-04 06:00 | 6 | 1 | 33.0041 | 6.9309
2018-03-04 07:00 | 7 | 1 | 86.2867 | 18.2065 | 2018-03-04 07:00 | 7 | 1 | 86.8452 | 17.6904 | 2018-03-04 07:00 | 7 | 1 | 0 | 0 | 2018-03-04 07:00 | 7 | 1 | 33.0012 | 6.9302
2018-03-04 08:00 | 8 | 1 | 86.2989 | 18.2091 | 2018-03-04 08:00 | 8 | 1 | 86.9032 | 17.7022 | 2018-03-04 08:00 | 8 | 1 | 0 | 0 | 2018-03-04 08:00 | 8 | 1 | 33.0232 | 6.9349
2018-03-04 09:00 | 9 | 1 | 86.2867 | 18.2065 | 2018-03-04 09:00 | 9 | 1 | 86.8162 | 17.6845 | 2018-03-04 09:00 | 9 | 1 | 0 | 0 | 2018-03-04 09:00 | 9 | 1 | 32.9902 | 6.9279
2018-03-04 10:00 | 10 | 1 | 86.2882 | 18.2068 | 2018-03-04 10:00 | 10 | 1 | 86.8528 | 17.6919 | 2018-03-04 10:00 | 10 | 1 | 0 | 0 | 2018-03-04 10:00 | 10 | 1 | 33.0041 | 6.9309
2018-03-04 11:00 | 11 | 1 | 86.1845 | 18.1849 | 2018-03-04 11:00 | 11 | 1 | 86.743 | 17.6695 | 2018-03-04 11:00 | 11 | 1 | 0 | 0 | 2018-03-04 11:00 | 11 | 1 | 32.9623 | 6.9221
2018-03-04 12:00 | 12 | 1 | 86.1418 | 18.1759 | 2018-03-04 12:00 | 12 | 1 | 86.714 | 17.6636 | 2018-03-04 12:00 | 12 | 1 | 0 | 0 | 2018-03-04 12:00 | 12 | 1 | 32.9513 | 6.9198
2018-03-04 13:00 | 13 | 1 | 86.1479 | 18.1772 | 2018-03-04 13:00 | 13 | 1 | 86.7659 | 17.6742 | 2018-03-04 13:00 | 13 | 1 | 0 | 0 | 2018-03-04 13:00 | 13 | 1 | 32.971 | 6.9239
2018-03-04 14:00 | 14 | 1 | 86.1112 | 18.1695 | 2018-03-04 14:00 | 14 | 1 | 86.7018 | 17.6612 | 2018-03-04 14:00 | 14 | 1 | 0 | 0 | 2018-03-04 14:00 | 14 | 1 | 32.9467 | 6.9188
2018-03-04 15:00 | 15 | 1 | 86.2455 | 18.1978 | 2018-03-04 15:00 | 15 | 1 | 86.8482 | 17.691 | 2018-03-04 15:00 | 15 | 1 | 0 | 0 | 2018-03-04 15:00 | 15 | 1 | 33.0023 | 6.9305
2018-03-04 16:00 | 16 | 1 | 86.3447 | 18.2187 | 2018-03-04 16:00 | 16 | 1 | 86.9398 | 17.7096 | 2018-03-04 16:00 | 16 | 1 | 0 | 0 | 2018-03-04 16:00 | 16 | 1 | 33.0371 | 6.9378
2018-03-04 17:00 | 17 | 1 | 86.4805 | 18.2474 | 2018-03-04 17:00 | 17 | 1 | 86.9856 | 17.719 | 2018-03-04 17:00 | 17 | 1 | 0 | 0 | 2018-03-04 17:00 | 17 | 1 | 33.0545 | 6.9415
2018-03-04 18:00 | 18 | 1 | 86.4332 | 18.2374 | 2018-03-04 18:00 | 18 | 1 | 86.92 | 17.7056 | 2018-03-04 18:00 | 18 | 1 | 0 | 0 | 2018-03-04 18:00 | 18 | 1 | 33.0296 | 6.9362
2018-03-04 19:00 | 19 | 1 | 85.6794 | 18.0784 | 2018-03-04 19:00 | 19 | 1 | 85.9266 | 17.5032 | 2018-03-04 19:00 | 19 | 1 | 0 | 0 | 2018-03-04 19:00 | 19 | 1 | 32.6521 | 6.8569
2018-03-04 20:00 | 20 | 1 | 86.3294 | 18.2155 | 2018-03-04 20:00 | 20 | 1 | 86.5888 | 17.6381 | 2018-03-04 20:00 | 20 | 1 | 0 | 0 | 2018-03-04 20:00 | 20 | 1 | 32.9037 | 6.9098
2018-03-04 21:00 | 21 | 1 | 86.3569 | 18.2213 | 2018-03-04 21:00 | 21 | 1 | 86.6728 | 17.6552 | 2018-03-04 21:00 | 21 | 1 | 0 | 0 | 2018-03-04 21:00 | 21 | 1 | 32.9357 | 6.9165
2018-03-04 22:00 | 22 | 1 | 86.4881 | 18.249 | 2018-03-04 22:00 | 22 | 1 | 86.8086 | 17.6829 | 2018-03-04 22:00 | 22 | 1 | 0 | 0 | 2018-03-04 22:00 | 22 | 1 | 32.9873 | 6.9273
2018-03-04 23:00 | 23 | 1 | 86.4332 | 18.2374 | 2018-03-04 23:00 | 23 | 1 | 86.7353 | 17.668 | 2018-03-04 23:00 | 23 | 1 | 0 | 0 | 2018-03-04 23:00 | 23 | 1 | 32.9594 | 6.9215
2018-03-05 | 0 | 2 | 86.4088 | 18.2323 | 2018-03-05 | 0 | 2 | 86.7002 | 17.6608 | 2018-03-05 | 0 | 2 | 86.9352 | 18.4303 | 2018-03-05 | 0 | 2 | 65.9815 | 13.8561
2018-03-05 01:00 | 1 | 2 | 86.0426 | 18.155 | 2018-03-05 01:00 | 1 | 2 | 86.3127 | 17.5819 | 2018-03-05 01:00 | 1 | 2 | 86.5278 | 18.3439 | 2018-03-05 01:00 | 1 | 2 | 65.6794 | 13.7927
2018-03-05 02:00 | 2 | 2 | 86.392 | 18.2287 | 2018-03-05 02:00 | 2 | 2 | 86.6392 | 17.6484 | 2018-03-05 02:00 | 2 | 2 | 86.8421 | 18.4105 | 2018-03-05 02:00 | 2 | 2 | 65.9229 | 13.8438
2018-03-05 03:00 | 3 | 2 | 86.2776 | 18.2046 | 2018-03-05 03:00 | 3 | 2 | 86.5766 | 17.6357 | 2018-03-05 03:00 | 3 | 2 | 86.7536 | 18.3918 | 2018-03-05 03:00 | 3 | 2 | 65.8655 | 13.8317
2018-03-05 04:00 | 4 | 2 | 86.5034 | 18.2522 | 2018-03-05 04:00 | 4 | 2 | 86.8849 | 17.6985 | 2018-03-05 04:00 | 4 | 2 | 87.0283 | 18.45 | 2018-03-05 04:00 | 4 | 2 | 66.087 | 13.8783
2018-03-05 05:00 | 5 | 2 | 86.3661 | 18.2232 | 2018-03-05 05:00 | 5 | 2 | 86.772 | 17.6755 | 2018-03-05 05:00 | 5 | 2 | 87.0054 | 18.4451 | 2018-03-05 05:00 | 5 | 2 | 66.0354 | 13.8674
2018-03-05 06:00 | 6 | 2 | 86.2898 | 18.2071 | 2018-03-05 06:00 | 6 | 2 | 86.6499 | 17.6506 | 2018-03-05 06:00 | 6 | 2 | 86.8147 | 18.4047 | 2018-03-05 06:00 | 6 | 2 | 65.9165 | 13.8425
2018-03-05 07:00 | 7 | 2 | 86.2043 | 18.1891 | 2018-03-05 07:00 | 7 | 2 | 86.5278 | 17.6257 | 2018-03-05 07:00 | 7 | 2 | 86.7079 | 18.3821 | 2018-03-05 07:00 | 7 | 2 | 65.8296 | 13.8242
2018-03-05 08:00 | 8 | 2 | 86.3355 | 18.2168 | 2018-03-05 08:00 | 8 | 2 | 86.5461 | 17.6294 | 2018-03-05 08:00 | 8 | 2 | 86.8025 | 18.4021 | 2018-03-05 08:00 | 8 | 2 | 65.8725 | 13.8332
2018-03-05 09:00 | 9 | 2 | 86.3798 | 18.2261 | 2018-03-05 09:00 | 9 | 2 | 86.7262 | 17.6661 | 2018-03-05 09:00 | 9 | 2 | 86.8711 | 18.4167 | 2018-03-05 09:00 | 9 | 2 | 65.967 | 13.8531
2018-03-05 10:00 | 10 | 2 | 86.2272 | 18.1939 | 2018-03-05 10:00 | 10 | 2 | 86.5156 | 17.6232 | 2018-03-05 10:00 | 10 | 2 | 86.714 | 18.3834 | 2018-03-05 10:00 | 10 | 2 | 65.8272 | 13.8237
2018-03-05 11:00 | 11 | 2 | 86.2119 | 18.1907 | 2018-03-05 11:00 | 11 | 2 | 86.5141 | 17.6229 | 2018-03-05 11:00 | 11 | 2 | 86.7201 | 18.3847 | 2018-03-05 11:00 | 11 | 2 | 65.829 | 13.8241
2018-03-05 12:00 | 12 | 2 | 86.389 | 18.2281 | 2018-03-05 12:00 | 12 | 2 | 86.6835 | 17.6574 | 2018-03-05 12:00 | 12 | 2 | 86.8574 | 18.4138 | 2018-03-05 12:00 | 12 | 2 | 65.9455 | 13.8486
2018-03-05 13:00 | 13 | 2 | 86.4027 | 18.231 | 2018-03-05 13:00 | 13 | 2 | 86.6224 | 17.645 | 2018-03-05 13:00 | 13 | 2 | 86.7475 | 18.3905 | 2018-03-05 13:00 | 13 | 2 | 65.8806 | 13.8349
2018-03-05 14:00 | 14 | 2 | 86.3783 | 18.2258 | 2018-03-05 14:00 | 14 | 2 | 86.6606 | 17.6528 | 2018-03-05 14:00 | 14 | 2 | 86.7903 | 18.3995 | 2018-03-05 14:00 | 14 | 2 | 65.9113 | 13.8414
2018-03-05 15:00 | 15 | 2 | 86.3355 | 18.2168 | 2018-03-05 15:00 | 15 | 2 | 86.5248 | 17.6251 | 2018-03-05 15:00 | 15 | 2 | 86.7384 | 18.3885 | 2018-03-05 15:00 | 15 | 2 | 65.84 | 13.8264
2018-03-05 16:00 | 16 | 2 | 86.3493 | 18.2197 | 2018-03-05 16:00 | 16 | 2 | 86.4912 | 17.6183 | 2018-03-05 16:00 | 16 | 2 | 86.685 | 18.3772 | 2018-03-05 16:00 | 16 | 2 | 65.807 | 13.8195
2018-03-05 17:00 | 17 | 2 | 86.244 | 18.1975 | 2018-03-05 17:00 | 17 | 2 | 86.4683 | 17.6136 | 2018-03-05 17:00 | 17 | 2 | 86.6743 | 18.375 | 2018-03-05 17:00 | 17 | 2 | 65.7942 | 13.8168
2018-03-05 18:00 | 18 | 2 | 86.3142 | 18.2123 | 2018-03-05 18:00 | 18 | 2 | 86.4378 | 17.6074 | 2018-03-05 18:00 | 18 | 2 | 86.5934 | 18.3578 | 2018-03-05 18:00 | 18 | 2 | 65.7519 | 13.8079
2018-03-05 19:00 | 19 | 2 | 86.2089 | 18.1901 | 2018-03-05 19:00 | 19 | 2 | 86.3508 | 17.5897 | 2018-03-05 19:00 | 19 | 2 | 86.5583 | 18.3504 | 2018-03-05 19:00 | 19 | 2 | 65.7055 | 13.7981
2018-03-05 20:00 | 20 | 2 | 86.2181 | 18.192 | 2018-03-05 20:00 | 20 | 2 | 86.4836 | 17.6167 | 2018-03-05 20:00 | 20 | 2 | 86.6896 | 18.3782 | 2018-03-05 20:00 | 20 | 2 | 65.8058 | 13.8192
2018-03-05 21:00 | 21 | 2 | 86.1494 | 18.1775 | 2018-03-05 21:00 | 21 | 2 | 86.4759 | 17.6151 | 2018-03-05 21:00 | 21 | 2 | 86.63 | 18.3656 | 2018-03-05 21:00 | 21 | 2 | 65.7802 | 13.8139
2018-03-05 22:00 | 22 | 2 | 86.2593 | 18.2007 | 2018-03-05 22:00 | 22 | 2 | 86.5522 | 17.6307 | 2018-03-05 22:00 | 22 | 2 | 86.6468 | 18.3691 | 2018-03-05 22:00 | 22 | 2 | 65.8156 | 13.8213
2018-03-05 23:00 | 23 | 2 | 86.4424 | 18.2393 | 2018-03-05 23:00 | 23 | 2 | 86.8055 | 17.6823 | 2018-03-05 23:00 | 23 | 2 | 86.8864 | 18.4199 | 2018-03-05 23:00 | 23 | 2 | 66.0029 | 13.8606
2018-03-06 | 0 | 3 | 86.4637 | 18.2438 | 2018-03-06 | 0 | 3 | 0 | 0 | 2018-03-06 | 0 | 3 | 0 | 0 | 2018-03-06 | 0 | 3 | 0 | 0
2018-03-06 01:00 | 1 | 3 | 86.5629 | 18.2648 | 2018-03-06 01:00 | 1 | 3 | 0 | 0 | 2018-03-06 01:00 | 1 | 3 | 0 | 0 | 2018-03-06 01:00 | 1 | 3 | 0 | 0
2018-03-06 02:00 | 2 | 3 | 86.3706 | 18.2242 | 2018-03-06 02:00 | 2 | 3 | 0 | 0 | 2018-03-06 02:00 | 2 | 3 | 0 | 0 | 2018-03-06 02:00 | 2 | 3 | 0 | 0
2018-03-06 03:00 | 3 | 3 | 86.3523 | 18.2203 | 2018-03-06 03:00 | 3 | 3 | 0 | 0 | 2018-03-06 03:00 | 3 | 3 | 0 | 0 | 2018-03-06 03:00 | 3 | 3 | 0 | 0
2018-03-06 04:00 | 4 | 3 | 86.3676 | 18.2236 | 2018-03-06 04:00 | 4 | 3 | 0 | 0 | 2018-03-06 04:00 | 4 | 3 | 0 | 0 | 2018-03-06 04:00 | 4 | 3 | 0 | 0
2018-03-06 05:00 | 5 | 3 | 86.4027 | 18.231 | 2018-03-06 05:00 | 5 | 3 | 0 | 0 | 2018-03-06 05:00 | 5 | 3 | 0 | 0 | 2018-03-06 05:00 | 5 | 3 | 0 | 0
2018-03-06 06:00 | 6 | 3 | 86.4652 | 18.2442 | 2018-03-06 06:00 | 6 | 3 | 0 | 0 | 2018-03-06 06:00 | 6 | 3 | 0 | 0 | 2018-03-06 06:00 | 6 | 3 | 0 | 0
2018-03-06 07:00 | 7 | 3 | 86.4012 | 18.2307 | 2018-03-06 07:00 | 7 | 3 | 0 | 0 | 2018-03-06 07:00 | 7 | 3 | 0 | 0 | 2018-03-06 07:00 | 7 | 3 | 0 | 0
2018-03-06 08:00 | 8 | 3 | 86.4515 | 18.2413 | 2018-03-06 08:00 | 8 | 3 | 0 | 0 | 2018-03-06 08:00 | 8 | 3 | 0 | 0 | 2018-03-06 08:00 | 8 | 3 | 0 | 0
2018-03-06 09:00 | 9 | 3 | 86.2028 | 18.1888 | 2018-03-06 09:00 | 9 | 3 | 0 | 0 | 2018-03-06 09:00 | 9 | 3 | 0 | 0 | 2018-03-06 09:00 | 9 | 3 | 0 | 0
2018-03-06 10:00 | 10 | 3 | 86.2715 | 18.2033 | 2018-03-06 10:00 | 10 | 3 | 0 | 0 | 2018-03-06 10:00 | 10 | 3 | 0 | 0 | 2018-03-06 10:00 | 10 | 3 | 0 | 0
2018-03-06 11:00 | 11 | 3 | 86.7567 | 18.3057 | 2018-03-06 11:00 | 11 | 3 | 0 | 0 | 2018-03-06 11:00 | 11 | 3 | 0 | 0 | 2018-03-06 11:00 | 11 | 3 | 0 | 0
2018-03-06 12:00 | 12 | 3 | 86.6194 | 18.2767 | 2018-03-06 12:00 | 12 | 3 | 0 | 0 | 2018-03-06 12:00 | 12 | 3 | 0 | 0 | 2018-03-06 12:00 | 12 | 3 | 0 | 0
2018-03-06 13:00 | 13 | 3 | 86.6377 | 18.2806 | 2018-03-06 13:00 | 13 | 3 | 0 | 0 | 2018-03-06 13:00 | 13 | 3 | 0 | 0 | 2018-03-06 13:00 | 13 | 3 | 0 | 0
2018-03-06 14:00 | 14 | 3 | 86.8757 | 18.3308 | 2018-03-06 14:00 | 14 | 3 | 0 | 0 | 2018-03-06 14:00 | 14 | 3 | 0 | 0 | 2018-03-06 14:00 | 14 | 3 | 0 | 0
2018-03-06 15:00 | 15 | 3 | 86.7994 | 18.3147 | 2018-03-06 15:00 | 15 | 3 | 0 | 0 | 2018-03-06 15:00 | 15 | 3 | 0 | 0 | 2018-03-06 15:00 | 15 | 3 | 0 | 0
2018-03-06 16:00 | 16 | 3 | 86.7674 | 18.3079 | 2018-03-06 16:00 | 16 | 3 | 0 | 0 | 2018-03-06 16:00 | 16 | 3 | 0 | 0 | 2018-03-06 16:00 | 16 | 3 | 0 | 0
2018-03-06 17:00 | 17 | 3 | 86.7384 | 18.3018 | 2018-03-06 17:00 | 17 | 3 | 0 | 0 | 2018-03-06 17:00 | 17 | 3 | 0 | 0 | 2018-03-06 17:00 | 17 | 3 | 0 | 0
2018-03-06 18:00 | 18 | 3 | 86.7124 | 18.2963 | 2018-03-06 18:00 | 18 | 3 | 0 | 0 | 2018-03-06 18:00 | 18 | 3 | 0 | 0 | 2018-03-06 18:00 | 18 | 3 | 0 | 0
2018-03-06 19:00 | 19 | 3 | 86.8376 | 18.3227 | 2018-03-06 19:00 | 19 | 3 | 0 | 0 | 2018-03-06 19:00 | 19 | 3 | 0 | 0 | 2018-03-06 19:00 | 19 | 3 | 0 | 0
2018-03-06 20:00 | 20 | 3 | 86.627 | 18.2783 | 2018-03-06 20:00 | 20 | 3 | 0 | 0 | 2018-03-06 20:00 | 20 | 3 | 0 | 0 | 2018-03-06 20:00 | 20 | 3 | 0 | 0
2018-03-06 21:00 | 21 | 3 | 86.6239 | 18.2776 | 2018-03-06 21:00 | 21 | 3 | 0 | 0 | 2018-03-06 21:00 | 21 | 3 | 0 | 0 | 2018-03-06 21:00 | 21 | 3 | 0 | 0
2018-03-06 22:00 | 22 | 3 | 86.714 | 18.2967 | 2018-03-06 22:00 | 22 | 3 | 0 | 0 | 2018-03-06 22:00 | 22 | 3 | 0 | 0 | 2018-03-06 22:00 | 22 | 3 | 0 | 0
2018-03-06 23:00 | 23 | 3 | 86.8971 | 18.3353 | 2018-03-06 23:00 | 23 | 3 | 0 | 0 | 2018-03-06 23:00 | 23 | 3 | 0 | 0 | 2018-03-06 23:00 | 23 | 3 | 0 | 0
2018-03-07 | 0 | 4 | 0 | 0 | 2018-03-07 | 0 | 4 | 0 | 0 | 2018-03-07 | 0 | 4 | 86.6712 | 18.3743 | 2018-03-07 | 0 | 4 | 32.9351 | 6.9164
2018-03-07 01:00 | 1 | 4 | 0 | 0 | 2018-03-07 01:00 | 1 | 4 | 0 | 0 | 2018-03-07 01:00 | 1 | 4 | 86.511 | 18.3403 | 2018-03-07 01:00 | 1 | 4 | 32.8742 | 6.9036
2018-03-07 02:00 | 2 | 4 | 0 | 0 | 2018-03-07 02:00 | 2 | 4 | 0 | 0 | 2018-03-07 02:00 | 2 | 4 | 86.7628 | 18.3937 | 2018-03-07 02:00 | 2 | 4 | 32.9699 | 6.9237
2018-03-07 03:00 | 3 | 4 | 0 | 0 | 2018-03-07 03:00 | 3 | 4 | 0 | 0 | 2018-03-07 03:00 | 3 | 4 | 86.7384 | 18.3885 | 2018-03-07 03:00 | 3 | 4 | 32.9606 | 6.9217
2018-03-07 04:00 | 4 | 4 | 0 | 0 | 2018-03-07 04:00 | 4 | 4 | 0 | 0 | 2018-03-07 04:00 | 4 | 4 | 86.8376 | 18.4096 | 2018-03-07 04:00 | 4 | 4 | 32.9983 | 6.9296
2018-03-07 05:00 | 5 | 4 | 0 | 0 | 2018-03-07 05:00 | 5 | 4 | 0 | 0 | 2018-03-07 05:00 | 5 | 4 | 87.0222 | 18.4487 | 2018-03-07 05:00 | 5 | 4 | 33.0684 | 6.9444
2018-03-07 06:00 | 6 | 4 | 0 | 0 | 2018-03-07 06:00 | 6 | 4 | 0 | 0 | 2018-03-07 06:00 | 6 | 4 | 86.9627 | 18.4361 | 2018-03-07 06:00 | 6 | 4 | 33.0458 | 6.9396
2018-03-07 07:00 | 7 | 4 | 0 | 0 | 2018-03-07 07:00 | 7 | 4 | 0 | 0 | 2018-03-07 07:00 | 7 | 4 | 87.1321 | 18.472 | 2018-03-07 07:00 | 7 | 4 | 33.1102 | 6.9531
2018-03-07 08:00 | 8 | 4 | 0 | 0 | 2018-03-07 08:00 | 8 | 4 | 0 | 0 | 2018-03-07 08:00 | 8 | 4 | 87.1931 | 18.4849 | 2018-03-07 08:00 | 8 | 4 | 33.1334 | 6.958
2018-03-07 09:00 | 9 | 4 | 0 | 0 | 2018-03-07 09:00 | 9 | 4 | 0 | 0 | 2018-03-07 09:00 | 9 | 4 | 86.7155 | 18.3837 | 2018-03-07 09:00 | 9 | 4 | 32.9519 | 6.9199
2018-03-07 10:00 | 10 | 4 | 0 | 0 | 2018-03-07 10:00 | 10 | 4 | 0 | 0 | 2018-03-07 10:00 | 10 | 4 | 86.6743 | 18.375 | 2018-03-07 10:00 | 10 | 4 | 32.9362 | 6.9166
2018-03-07 11:00 | 11 | 4 | 0 | 0 | 2018-03-07 11:00 | 11 | 4 | 0 | 0 | 2018-03-07 11:00 | 11 | 4 | 86.8956 | 18.4219 | 2018-03-07 11:00 | 11 | 4 | 33.0203 | 6.9343
2018-03-07 12:00 | 12 | 4 | 0 | 0 | 2018-03-07 12:00 | 12 | 4 | 0 | 0 | 2018-03-07 12:00 | 12 | 4 | 86.9276 | 18.4287 | 2018-03-07 12:00 | 12 | 4 | 33.0325 | 6.9368
2018-03-07 13:00 | 13 | 4 | 0 | 0 | 2018-03-07 13:00 | 13 | 4 | 0 | 0 | 2018-03-07 13:00 | 13 | 4 | 87.2541 | 18.4979 | 2018-03-07 13:00 | 13 | 4 | 33.1566 | 6.9629
2018-03-07 14:00 | 14 | 4 | 0 | 0 | 2018-03-07 14:00 | 14 | 4 | 0 | 0 | 2018-03-07 14:00 | 14 | 4 | 87.4037 | 18.5296 | 2018-03-07 14:00 | 14 | 4 | 33.2134 | 6.9748
2018-03-07 15:00 | 15 | 4 | 0 | 0 | 2018-03-07 15:00 | 15 | 4 | 0 | 0 | 2018-03-07 15:00 | 15 | 4 | 87.2129 | 18.4891 | 2018-03-07 15:00 | 15 | 4 | 33.1409 | 6.9596
2018-03-07 16:00 | 16 | 4 | 0 | 0 | 2018-03-07 16:00 | 16 | 4 | 0 | 0 | 2018-03-07 16:00 | 16 | 4 | 86.9718 | 18.438 | 2018-03-07 16:00 | 16 | 4 | 33.0493 | 6.9403
2018-03-07 17:00 | 17 | 4 | 0 | 0 | 2018-03-07 17:00 | 17 | 4 | 0 | 0 | 2018-03-07 17:00 | 17 | 4 | 87.1397 | 18.4736 | 2018-03-07 17:00 | 17 | 4 | 33.1131 | 6.9537
2018-03-07 18:00 | 18 | 4 | 0 | 0 | 2018-03-07 18:00 | 18 | 4 | 0 | 0 | 2018-03-07 18:00 | 18 | 4 | 87.2435 | 18.4956 | 2018-03-07 18:00 | 18 | 4 | 33.1525 | 6.962
2018-03-07 19:00 | 19 | 4 | 0 | 0 | 2018-03-07 19:00 | 19 | 4 | 0 | 0 | 2018-03-07 19:00 | 19 | 4 | 86.8894 | 18.4206 | 2018-03-07 19:00 | 19 | 4 | 33.018 | 6.9338
2018-03-07 20:00 | 20 | 4 | 0 | 0 | 2018-03-07 20:00 | 20 | 4 | 0 | 0 | 2018-03-07 20:00 | 20 | 4 | 87.1839 | 18.483 | 2018-03-07 20:00 | 20 | 4 | 33.1299 | 6.9573
2018-03-07 21:00 | 21 | 4 | 0 | 0 | 2018-03-07 21:00 | 21 | 4 | 0 | 0 | 2018-03-07 21:00 | 21 | 4 | 87.2419 | 18.4953 | 2018-03-07 21:00 | 21 | 4 | 33.1519 | 6.9619
2018-03-07 22:00 | 22 | 4 | 0 | 0 | 2018-03-07 22:00 | 22 | 4 | 0 | 0 | 2018-03-07 22:00 | 22 | 4 | 87.1733 | 18.4807 | 2018-03-07 22:00 | 22 | 4 | 33.1259 | 6.9564
2018-03-07 23:00 | 23 | 4 | 0 | 0 | 2018-03-07 23:00 | 23 | 4 | 0 | 0 | 2018-03-07 23:00 | 23 | 4 | 87.2557 | 18.4982 | 2018-03-07 23:00 | 23 | 4 | 33.1572 | 6.963
2018-03-08 | 0 | 5 | 86.5492 | 18.2619 | 2018-03-08 | 0 | 5 | 0 | 0 | 2018-03-08 | 0 | 5 | 0 | 0 | 2018-03-08 | 0 | 5 | 0 | 0
2018-03-08 01:00 | 1 | 5 | 86.7201 | 18.2979 | 2018-03-08 01:00 | 1 | 5 | 0 | 0 | 2018-03-08 01:00 | 1 | 5 | 0 | 0 | 2018-03-08 01:00 | 1 | 5 | 0 | 0
2018-03-08 02:00 | 2 | 5 | 86.5095 | 18.2535 | 2018-03-08 02:00 | 2 | 5 | 0 | 0 | 2018-03-08 02:00 | 2 | 5 | 0 | 0 | 2018-03-08 02:00 | 2 | 5 | 0 | 0
2018-03-08 03:00 | 3 | 5 | 86.4576 | 18.2426 | 2018-03-08 03:00 | 3 | 5 | 0 | 0 | 2018-03-08 03:00 | 3 | 5 | 0 | 0 | 2018-03-08 03:00 | 3 | 5 | 0 | 0
2018-03-08 04:00 | 4 | 5 | 86.6316 | 18.2793 | 2018-03-08 04:00 | 4 | 5 | 0 | 0 | 2018-03-08 04:00 | 4 | 5 | 0 | 0 | 2018-03-08 04:00 | 4 | 5 | 0 | 0
2018-03-08 05:00 | 5 | 5 | 86.569 | 18.2661 | 2018-03-08 05:00 | 5 | 5 | 0 | 0 | 2018-03-08 05:00 | 5 | 5 | 0 | 0 | 2018-03-08 05:00 | 5 | 5 | 0 | 0
2018-03-08 06:00 | 6 | 5 | 86.6468 | 18.2825 | 2018-03-08 06:00 | 6 | 5 | 0 | 0 | 2018-03-08 06:00 | 6 | 5 | 0 | 0 | 2018-03-08 06:00 | 6 | 5 | 0 | 0
2018-03-08 07:00 | 7 | 5 | 86.6361 | 18.2802 | 2018-03-08 07:00 | 7 | 5 | 0 | 0 | 2018-03-08 07:00 | 7 | 5 | 0 | 0 | 2018-03-08 07:00 | 7 | 5 | 0 | 0
2018-03-08 08:00 | 8 | 5 | 86.6819 | 18.2899 | 2018-03-08 08:00 | 8 | 5 | 0 | 0 | 2018-03-08 08:00 | 8 | 5 | 0 | 0 | 2018-03-08 08:00 | 8 | 5 | 0 | 0
2018-03-08 09:00 | 9 | 5 | 86.7094 | 18.2957 | 2018-03-08 09:00 | 9 | 5 | 0 | 0 | 2018-03-08 09:00 | 9 | 5 | 0 | 0 | 2018-03-08 09:00 | 9 | 5 | 0 | 0
2018-03-08 10:00 | 10 | 5 | 86.7933 | 18.3134 | 2018-03-08 10:00 | 10 | 5 | 0 | 0 | 2018-03-08 10:00 | 10 | 5 | 0 | 0 | 2018-03-08 10:00 | 10 | 5 | 0 | 0
2018-03-08 11:00 | 11 | 5 | 86.8009 | 18.315 | 2018-03-08 11:00 | 11 | 5 | 0 | 0 | 2018-03-08 11:00 | 11 | 5 | 0 | 0 | 2018-03-08 11:00 | 11 | 5 | 0 | 0
2018-03-08 12:00 | 12 | 5 | 86.6728 | 18.288 | 2018-03-08 12:00 | 12 | 5 | 0 | 0 | 2018-03-08 12:00 | 12 | 5 | 0 | 0 | 2018-03-08 12:00 | 12 | 5 | 0 | 0
2018-03-08 13:00 | 13 | 5 | 86.6316 | 18.2793 | 2018-03-08 13:00 | 13 | 5 | 0 | 0 | 2018-03-08 13:00 | 13 | 5 | 0 | 0 | 2018-03-08 13:00 | 13 | 5 | 0 | 0
2018-03-08 14:00 | 14 | 5 | 86.6316 | 18.2793 | 2018-03-08 14:00 | 14 | 5 | 0 | 0 | 2018-03-08 14:00 | 14 | 5 | 0 | 0 | 2018-03-08 14:00 | 14 | 5 | 0 | 0
2018-03-08 15:00 | 15 | 5 | 86.6636 | 18.286 | 2018-03-08 15:00 | 15 | 5 | 0 | 0 | 2018-03-08 15:00 | 15 | 5 | 0 | 0 | 2018-03-08 15:00 | 15 | 5 | 0 | 0
2018-03-08 16:00 | 16 | 5 | 86.5568 | 18.2635 | 2018-03-08 16:00 | 16 | 5 | 0 | 0 | 2018-03-08 16:00 | 16 | 5 | 0 | 0 | 2018-03-08 16:00 | 16 | 5 | 0 | 0
2018-03-08 17:00 | 17 | 5 | 86.6865 | 18.2909 | 2018-03-08 17:00 | 17 | 5 | 0 | 0 | 2018-03-08 17:00 | 17 | 5 | 0 | 0 | 2018-03-08 17:00 | 17 | 5 | 0 | 0
2018-03-08 18:00 | 18 | 5 | 86.7262 | 18.2992 | 2018-03-08 18:00 | 18 | 5 | 0 | 0 | 2018-03-08 18:00 | 18 | 5 | 0 | 0 | 2018-03-08 18:00 | 18 | 5 | 0 | 0
2018-03-08 19:00 | 19 | 5 | 86.5187 | 18.2554 | 2018-03-08 19:00 | 19 | 5 | 0 | 0 | 2018-03-08 19:00 | 19 | 5 | 0 | 0 | 2018-03-08 19:00 | 19 | 5 | 0 | 0
2018-03-08 20:00 | 20 | 5 | 86.5766 | 18.2677 | 2018-03-08 20:00 | 20 | 5 | 0 | 0 | 2018-03-08 20:00 | 20 | 5 | 0 | 0 | 2018-03-08 20:00 | 20 | 5 | 0 | 0
2018-03-08 21:00 | 21 | 5 | 86.6194 | 18.2767 | 2018-03-08 21:00 | 21 | 5 | 0 | 0 | 2018-03-08 21:00 | 21 | 5 | 0 | 0 | 2018-03-08 21:00 | 21 | 5 | 0 | 0
2018-03-08 22:00 | 22 | 5 | 86.6743 | 18.2883 | 2018-03-08 22:00 | 22 | 5 | 0 | 0 | 2018-03-08 22:00 | 22 | 5 | 0 | 0 | 2018-03-08 22:00 | 22 | 5 | 0 | 0
2018-03-08 23:00 | 23 | 5 | 86.5644 | 18.2651 | 2018-03-08 23:00 | 23 | 5 | 0 | 0 | 2018-03-08 23:00 | 23 | 5 | 0 | 0 | 2018-03-08 23:00 | 23 | 5 | 0 | 0
2018-03-09 | 0 | 6 | 86.2226 | 18.193 | 2018-03-09 | 0 | 6 | 86.688 | 17.6583 | 2018-03-09 | 0 | 6 | 0 | 0 | 2018-03-09 | 0 | 6 | 32.9414 | 6.9177
2018-03-09 01:00 | 1 | 6 | 86.1128 | 18.1698 | 2018-03-09 01:00 | 1 | 6 | 86.5232 | 17.6248 | 2018-03-09 01:00 | 1 | 6 | 0 | 0 | 2018-03-09 01:00 | 1 | 6 | 32.8788 | 6.9046
2018-03-09 02:00 | 2 | 6 | 86.2791 | 18.2049 | 2018-03-09 02:00 | 2 | 6 | 86.6896 | 17.6587 | 2018-03-09 02:00 | 2 | 6 | 0 | 0 | 2018-03-09 02:00 | 2 | 6 | 32.942 | 6.9178
2018-03-09 03:00 | 3 | 6 | 86.0014 | 18.1463 | 2018-03-09 03:00 | 3 | 6 | 86.4485 | 17.6096 | 2018-03-09 03:00 | 3 | 6 | 0 | 0 | 2018-03-09 03:00 | 3 | 6 | 32.8504 | 6.8986
2018-03-09 04:00 | 4 | 6 | 86.0533 | 18.1572 | 2018-03-09 04:00 | 4 | 6 | 86.4347 | 17.6067 | 2018-03-09 04:00 | 4 | 6 | 0 | 0 | 2018-03-09 04:00 | 4 | 6 | 32.8452 | 6.8975
2018-03-09 05:00 | 5 | 6 | 86.2257 | 18.1936 | 2018-03-09 05:00 | 5 | 6 | 86.6117 | 17.6428 | 2018-03-09 05:00 | 5 | 6 | 0 | 0 | 2018-03-09 05:00 | 5 | 6 | 32.9124 | 6.9116
2018-03-09 06:00 | 6 | 6 | 86.4332 | 18.2374 | 2018-03-09 06:00 | 6 | 6 | 86.9352 | 17.7087 | 2018-03-09 06:00 | 6 | 6 | 0 | 0 | 2018-03-09 06:00 | 6 | 6 | 33.0354 | 6.9374
2018-03-09 07:00 | 7 | 6 | 86.5873 | 18.2699 | 2018-03-09 07:00 | 7 | 6 | 87.0619 | 17.7345 | 2018-03-09 07:00 | 7 | 6 | 0 | 0 | 2018-03-09 07:00 | 7 | 6 | 33.0835 | 6.9475
2018-03-09 08:00 | 8 | 6 | 86.3691 | 18.2239 | 2018-03-09 08:00 | 8 | 6 | 86.7811 | 17.6773 | 2018-03-09 08:00 | 8 | 6 | 0 | 0 | 2018-03-09 08:00 | 8 | 6 | 32.9768 | 6.9251
2018-03-09 09:00 | 9 | 6 | 86.334 | 18.2165 | 2018-03-09 09:00 | 9 | 6 | 86.7399 | 17.6689 | 2018-03-09 09:00 | 9 | 6 | 0 | 0 | 2018-03-09 09:00 | 9 | 6 | 32.9612 | 6.9218
2018-03-09 10:00 | 10 | 6 | 86.5126 | 18.2542 | 2018-03-09 10:00 | 10 | 6 | 86.862 | 17.6938 | 2018-03-09 10:00 | 10 | 6 | 0 | 0 | 2018-03-09 10:00 | 10 | 6 | 33.0076 | 6.9316
2018-03-09 11:00 | 11 | 6 | 86.5003 | 18.2516 | 2018-03-09 11:00 | 11 | 6 | 86.9306 | 17.7078 | 2018-03-09 11:00 | 11 | 6 | 0 | 0 | 2018-03-09 11:00 | 11 | 6 | 33.0336 | 6.9371
2018-03-09 12:00 | 12 | 6 | 86.7002 | 18.2937 | 2018-03-09 12:00 | 12 | 6 | 87.1412 | 17.7507 | 2018-03-09 12:00 | 12 | 6 | 0 | 0 | 2018-03-09 12:00 | 12 | 6 | 33.1137 | 6.9539
2018-03-09 13:00 | 13 | 6 | 86.363 | 18.2226 | 2018-03-09 13:00 | 13 | 6 | 86.8009 | 17.6813 | 2018-03-09 13:00 | 13 | 6 | 0 | 0 | 2018-03-09 13:00 | 13 | 6 | 32.9843 | 6.9267
2018-03-09 14:00 | 14 | 6 | 86.4408 | 18.239 | 2018-03-09 14:00 | 14 | 6 | 86.8635 | 17.6941 | 2018-03-09 14:00 | 14 | 6 | 0 | 0 | 2018-03-09 14:00 | 14 | 6 | 33.0081 | 6.9317
2018-03-09 15:00 | 15 | 6 | 86.2943 | 18.2081 | 2018-03-09 15:00 | 15 | 6 | 86.6743 | 17.6556 | 2018-03-09 15:00 | 15 | 6 | 0 | 0 | 2018-03-09 15:00 | 15 | 6 | 32.9362 | 6.9166
2018-03-09 16:00 | 16 | 6 | 86.3706 | 18.2242 | 2018-03-09 16:00 | 16 | 6 | 86.7491 | 17.6708 | 2018-03-09 16:00 | 16 | 6 | 0 | 0 | 2018-03-09 16:00 | 16 | 6 | 32.9647 | 6.9226
2018-03-09 17:00 | 17 | 6 | 86.2882 | 18.2068 | 2018-03-09 17:00 | 17 | 6 | 86.7445 | 17.6699 | 2018-03-09 17:00 | 17 | 6 | 0 | 0 | 2018-03-09 17:00 | 17 | 6 | 32.9629 | 6.9222
2018-03-09 18:00 | 18 | 6 | 86.1875 | 18.1856 | 2018-03-09 18:00 | 18 | 6 | 86.6667 | 17.654 | 2018-03-09 18:00 | 18 | 6 | 0 | 0 | 2018-03-09 18:00 | 18 | 6 | 32.9333 | 6.916
2018-03-09 19:00 | 19 | 6 | 86.099 | 18.1669 | 2018-03-09 19:00 | 19 | 6 | 86.5431 | 17.6288 | 2018-03-09 19:00 | 19 | 6 | 0 | 0 | 2018-03-09 19:00 | 19 | 6 | 32.8864 | 6.9061
2018-03-09 20:00 | 20 | 6 | 86.1997 | 18.1881 | 2018-03-09 20:00 | 20 | 6 | 86.5187 | 17.6239 | 2018-03-09 20:00 | 20 | 6 | 0 | 0 | 2018-03-09 20:00 | 20 | 6 | 32.8771 | 6.9042
2018-03-09 21:00 | 21 | 6 | 86.3767 | 18.2255 | 2018-03-09 21:00 | 21 | 6 | 86.7247 | 17.6658 | 2018-03-09 21:00 | 21 | 6 | 0 | 0 | 2018-03-09 21:00 | 21 | 6 | 32.9554 | 6.9206
2018-03-09 22:00 | 22 | 6 | 86.3691 | 18.2239 | 2018-03-09 22:00 | 22 | 6 | 86.7659 | 17.6742 | 2018-03-09 22:00 | 22 | 6 | 0 | 0 | 2018-03-09 22:00 | 22 | 6 | 32.971 | 6.9239
2018-03-09 23:00 | 23 | 6 | 86.4012 | 18.2307 | 2018-03-09 23:00 | 23 | 6 | 86.7918 | 17.6795 | 2018-03-09 23:00 | 23 | 6 | 0 | 0 | 2018-03-09 23:00 | 23 | 6 | 32.9809 | 6.926
2018-03-10 | 0 | 7 | 86.0121 | 18.1486 | 2018-03-10 | 0 | 7 | 0 | 0 | 2018-03-10 | 0 | 7 | 86.5507 | 18.3487 | 2018-03-10 | 0 | 7 | 32.8893 | 6.9067
2018-03-10 01:00 | 1 | 7 | 85.919 | 18.1289 | 2018-03-10 01:00 | 1 | 7 | 0 | 0 | 2018-03-10 01:00 | 1 | 7 | 86.5324 | 18.3449 | 2018-03-10 01:00 | 1 | 7 | 32.8823 | 6.9053
2018-03-10 02:00 | 2 | 7 | 86.0533 | 18.1572 | 2018-03-10 02:00 | 2 | 7 | 0 | 0 | 2018-03-10 02:00 | 2 | 7 | 86.6453 | 18.3688 | 2018-03-10 02:00 | 2 | 7 | 32.9252 | 6.9143
2018-03-10 03:00 | 3 | 7 | 86.1677 | 18.1814 | 2018-03-10 03:00 | 3 | 7 | 0 | 0 | 2018-03-10 03:00 | 3 | 7 | 86.7002 | 18.3804 | 2018-03-10 03:00 | 3 | 7 | 32.9461 | 6.9187
2018-03-10 04:00 | 4 | 7 | 86.3081 | 18.211 | 2018-03-10 04:00 | 4 | 7 | 0 | 0 | 2018-03-10 04:00 | 4 | 7 | 86.8513 | 18.4125 | 2018-03-10 04:00 | 4 | 7 | 33.0035 | 6.9307
2018-03-10 05:00 | 5 | 7 | 86.2562 | 18.2001 | 2018-03-10 05:00 | 5 | 7 | 0 | 0 | 2018-03-10 05:00 | 5 | 7 | 86.8605 | 18.4144 | 2018-03-10 05:00 | 5 | 7 | 33.007 | 6.9315
2018-03-10 06:00 | 6 | 7 | 86.1234 | 18.172 | 2018-03-10 06:00 | 6 | 7 | 0 | 0 | 2018-03-10 06:00 | 6 | 7 | 86.6682 | 18.3737 | 2018-03-10 06:00 | 6 | 7 | 32.9339 | 6.9161
2018-03-10 07:00 | 7 | 7 | 86.1906 | 18.1862 | 2018-03-10 07:00 | 7 | 7 | 0 | 0 | 2018-03-10 07:00 | 7 | 7 | 86.7247 | 18.3856 | 2018-03-10 07:00 | 7 | 7 | 32.9554 | 6.9206
2018-03-10 08:00 | 8 | 7 | 86.36 | 18.222 | 2018-03-10 08:00 | 8 | 7 | 0 | 0 | 2018-03-10 08:00 | 8 | 7 | 86.952 | 18.4338 | 2018-03-10 08:00 | 8 | 7 | 33.0418 | 6.9388
2018-03-10 09:00 | 9 | 7 | 86.4912 | 18.2496 | 2018-03-10 09:00 | 9 | 7 | 0 | 0 | 2018-03-10 09:00 | 9 | 7 | 87.0588 | 18.4565 | 2018-03-10 09:00 | 9 | 7 | 33.0823 | 6.9473
2018-03-10 10:00 | 10 | 7 | 86.1982 | 18.1878 | 2018-03-10 10:00 | 10 | 7 | 0 | 0 | 2018-03-10 10:00 | 10 | 7 | 86.6392 | 18.3675 | 2018-03-10 10:00 | 10 | 7 | 32.9229 | 6.9138
2018-03-10 11:00 | 11 | 7 | 86.1707 | 18.182 | 2018-03-10 11:00 | 11 | 7 | 0 | 0 | 2018-03-10 11:00 | 11 | 7 | 86.8849 | 18.4196 | 2018-03-10 11:00 | 11 | 7 | 33.0163 | 6.9334
2018-03-10 12:00 | 12 | 7 | 86.5019 | 18.2519 | 2018-03-10 12:00 | 12 | 7 | 0 | 0 | 2018-03-10 12:00 | 12 | 7 | 87.1504 | 18.4759 | 2018-03-10 12:00 | 12 | 7 | 33.1172 | 6.9546
2018-03-10 13:00 | 13 | 7 | 86.6148 | 18.2757 | 2018-03-10 13:00 | 13 | 7 | 0 | 0 | 2018-03-10 13:00 | 13 | 7 | 87.3167 | 18.5111 | 2018-03-10 13:00 | 13 | 7 | 33.1803 | 6.9679
2018-03-10 14:00 | 14 | 7 | 86.4439 | 18.2397 | 2018-03-10 14:00 | 14 | 7 | 0 | 0 | 2018-03-10 14:00 | 14 | 7 | 87.0832 | 18.4616 | 2018-03-10 14:00 | 14 | 7 | 33.0916 | 6.9492
2018-03-10 15:00 | 15 | 7 | 86.5522 | 18.2625 | 2018-03-10 15:00 | 15 | 7 | 0 | 0 | 2018-03-10 15:00 | 15 | 7 | 87.2938 | 18.5063 | 2018-03-10 15:00 | 15 | 7 | 33.1716 | 6.966
2018-03-10 16:00 | 16 | 7 | 86.5644 | 18.2651 | 2018-03-10 16:00 | 16 | 7 | 0 | 0 | 2018-03-10 16:00 | 16 | 7 | 87.3579 | 18.5199 | 2018-03-10 16:00 | 16 | 7 | 33.196 | 6.9712
2018-03-10 17:00 | 17 | 7 | 86.7445 | 18.3031 | 2018-03-10 17:00 | 17 | 7 | 0 | 0 | 2018-03-10 17:00 | 17 | 7 | 87.57 | 18.5648 | 2018-03-10 17:00 | 17 | 7 | 33.2766 | 6.9881
2018-03-10 18:00 | 18 | 7 | 86.4668 | 18.2445 | 2018-03-10 18:00 | 18 | 7 | 0 | 0 | 2018-03-10 18:00 | 18 | 7 | 87.3014 | 18.5079 | 2018-03-10 18:00 | 18 | 7 | 33.1745 | 6.9667
2018-03-10 19:00 | 19 | 7 | 86.3661 | 18.2232 | 2018-03-10 19:00 | 19 | 7 | 0 | 0 | 2018-03-10 19:00 | 19 | 7 | 87.0954 | 18.4642 | 2018-03-10 19:00 | 19 | 7 | 33.0963 | 6.9502
2018-03-10 20:00 | 20 | 7 | 86.1173 | 18.1708 | 2018-03-10 20:00 | 20 | 7 | 0 | 0 | 2018-03-10 20:00 | 20 | 7 | 86.891 | 18.4209 | 2018-03-10 20:00 | 20 | 7 | 33.0186 | 6.9339
2018-03-10 21:00 | 21 | 7 | 86.1555 | 18.1788 | 2018-03-10 21:00 | 21 | 7 | 0 | 0 | 2018-03-10 21:00 | 21 | 7 | 86.9245 | 18.428 | 2018-03-10 21:00 | 21 | 7 | 33.0313 | 6.9366
2018-03-10 22:00 | 22 | 7 | 86.2211 | 18.1927 | 2018-03-10 22:00 | 22 | 7 | 0 | 0 | 2018-03-10 22:00 | 22 | 7 | 87.0054 | 18.4451 | 2018-03-10 22:00 | 22 | 7 | 33.0621 | 6.943
2018-03-10 23:00 | 23 | 7 | 86.2226 | 18.193 | 2018-03-10 23:00 | 23 | 7 | 0 | 0 | 2018-03-10 23:00 | 23 | 7 | 87.0787 | 18.4607 | 2018-03-10 23:00 | 23 | 7 | 33.0899 | 6.9489
2018-03-11 | 0 | 1 | 86.2364 | 18.1959 | 2018-03-11 | 0 | 1 | 86.7994 | 17.681 | 2018-03-11 | 0 | 1 | 0 | 0 | 2018-03-11 | 0 | 1 | 32.9838 | 6.9266
2018-03-11 01:00 | 1 | 1 | 86.3188 | 18.2133 | 2018-03-11 01:00 | 1 | 1 | 86.952 | 17.7121 | 2018-03-11 01:00 | 1 | 1 | 0 | 0 | 2018-03-11 01:00 | 1 | 1 | 33.0418 | 6.9388
2018-03-11 02:00 | 2 | 1 | 86.2119 | 18.1907 | 2018-03-11 02:00 | 2 | 1 | 86.8177 | 17.6848 | 2018-03-11 02:00 | 2 | 1 | 0 | 0 | 2018-03-11 02:00 | 2 | 1 | 32.9907 | 6.9281
2018-03-11 03:00 | 3 | 1 | 86.1845 | 18.1849 | 2018-03-11 03:00 | 3 | 1 | 86.7857 | 17.6782 | 2018-03-11 03:00 | 3 | 1 | 0 | 0 | 2018-03-11 03:00 | 3 | 1 | 32.9786 | 6.9255
2018-03-11 04:00 | 4 | 1 | 86.2455 | 18.1978 | 2018-03-11 04:00 | 4 | 1 | 86.833 | 17.6879 | 2018-03-11 04:00 | 4 | 1 | 0 | 0 | 2018-03-11 04:00 | 4 | 1 | 32.9965 | 6.9293
2018-03-11 05:00 | 5 | 1 | 86.2333 | 18.1952 | 2018-03-11 05:00 | 5 | 1 | 86.833 | 17.6879 | 2018-03-11 05:00 | 5 | 1 | 0 | 0 | 2018-03-11 05:00 | 5 | 1 | 32.9965 | 6.9293
2018-03-11 06:00 | 6 | 1 | 86.2776 | 18.2046 | 2018-03-11 06:00 | 6 | 1 | 86.8528 | 17.6919 | 2018-03-11 06:00 | 6 | 1 | 0 | 0 | 2018-03-11 06:00 | 6 | 1 | 33.0041 | 6.9309
2018-03-11 07:00 | 7 | 1 | 86.2867 | 18.2065 | 2018-03-11 07:00 | 7 | 1 | 86.8452 | 17.6904 | 2018-03-11 07:00 | 7 | 1 | 0 | 0 | 2018-03-11 07:00 | 7 | 1 | 33.0012 | 6.9302
2018-03-11 08:00 | 8 | 1 | 86.2989 | 18.2091 | 2018-03-11 08:00 | 8 | 1 | 86.9032 | 17.7022 | 2018-03-11 08:00 | 8 | 1 | 0 | 0 | 2018-03-11 08:00 | 8 | 1 | 33.0232 | 6.9349
2018-03-11 09:00 | 9 | 1 | 86.2867 | 18.2065 | 2018-03-11 09:00 | 9 | 1 | 86.8162 | 17.6845 | 2018-03-11 09:00 | 9 | 1 | 0 | 0 | 2018-03-11 09:00 | 9 | 1 | 32.9902 | 6.9279
2018-03-11 10:00 | 10 | 1 | 86.2882 | 18.2068 | 2018-03-11 10:00 | 10 | 1 | 86.8528 | 17.6919 | 2018-03-11 10:00 | 10 | 1 | 0 | 0 | 2018-03-11 10:00 | 10 | 1 | 33.0041 | 6.9309
2018-03-11 11:00 | 11 | 1 | 86.1845 | 18.1849 | 2018-03-11 11:00 | 11 | 1 | 86.743 | 17.6695 | 2018-03-11 11:00 | 11 | 1 | 0 | 0 | 2018-03-11 11:00 | 11 | 1 | 32.9623 | 6.9221
2018-03-11 12:00 | 12 | 1 | 86.1418 | 18.1759 | 2018-03-11 12:00 | 12 | 1 | 86.714 | 17.6636 | 2018-03-11 12:00 | 12 | 1 | 0 | 0 | 2018-03-11 12:00 | 12 | 1 | 32.9513 | 6.9198
2018-03-11 13:00 | 13 | 1 | 86.1479 | 18.1772 | 2018-03-11 13:00 | 13 | 1 | 86.7659 | 17.6742 | 2018-03-11 13:00 | 13 | 1 | 0 | 0 | 2018-03-11 13:00 | 13 | 1 | 32.971 | 6.9239
2018-03-11 14:00 | 14 | 1 | 86.1112 | 18.1695 | 2018-03-11 14:00 | 14 | 1 | 86.7018 | 17.6612 | 2018-03-11 14:00 | 14 | 1 | 0 | 0 | 2018-03-11 14:00 | 14 | 1 | 32.9467 | 6.9188
2018-03-11 15:00 | 15 | 1 | 86.2455 | 18.1978 | 2018-03-11 15:00 | 15 | 1 | 86.8482 | 17.691 | 2018-03-11 15:00 | 15 | 1 | 0 | 0 | 2018-03-11 15:00 | 15 | 1 | 33.0023 | 6.9305
2018-03-11 16:00 | 16 | 1 | 86.3447 | 18.2187 | 2018-03-11 16:00 | 16 | 1 | 86.9398 | 17.7096 | 2018-03-11 16:00 | 16 | 1 | 0 | 0 | 2018-03-11 16:00 | 16 | 1 | 33.0371 | 6.9378
2018-03-11 17:00 | 17 | 1 | 86.4805 | 18.2474 | 2018-03-11 17:00 | 17 | 1 | 86.9856 | 17.719 | 2018-03-11 17:00 | 17 | 1 | 0 | 0 | 2018-03-11 17:00 | 17 | 1 | 33.0545 | 6.9415
2018-03-11 18:00 | 18 | 1 | 86.4332 | 18.2374 | 2018-03-11 18:00 | 18 | 1 | 86.92 | 17.7056 | 2018-03-11 18:00 | 18 | 1 | 0 | 0 | 2018-03-11 18:00 | 18 | 1 | 33.0296 | 6.9362
2018-03-11 19:00 | 19 | 1 | 85.6794 | 18.0784 | 2018-03-11 19:00 | 19 | 1 | 85.9266 | 17.5032 | 2018-03-11 19:00 | 19 | 1 | 0 | 0 | 2018-03-11 19:00 | 19 | 1 | 32.6521 | 6.8569
2018-03-11 20:00 | 20 | 1 | 86.3294 | 18.2155 | 2018-03-11 20:00 | 20 | 1 | 86.5888 | 17.6381 | 2018-03-11 20:00 | 20 | 1 | 0 | 0 | 2018-03-11 20:00 | 20 | 1 | 32.9037 | 6.9098
2018-03-11 21:00 | 21 | 1 | 86.3569 | 18.2213 | 2018-03-11 21:00 | 21 | 1 | 86.6728 | 17.6552 | 2018-03-11 21:00 | 21 | 1 | 0 | 0 | 2018-03-11 21:00 | 21 | 1 | 32.9357 | 6.9165
2018-03-11 22:00 | 22 | 1 | 86.4881 | 18.249 | 2018-03-11 22:00 | 22 | 1 | 86.8086 | 17.6829 | 2018-03-11 22:00 | 22 | 1 | 0 | 0 | 2018-03-11 22:00 | 22 | 1 | 32.9873 | 6.9273
2018-03-11 23:00 | 23 | 1 | 86.4332 | 18.2374 | 2018-03-11 23:00 | 23 | 1 | 86.7353 | 17.668 | 2018-03-11 23:00 | 23 | 1 | 0 | 0 | 2018-03-11 23:00 | 23 | 1 | 32.9594 | 6.9215
2018-03-12 | 0 | 2 | 86.4088 | 18.2323 | 2018-03-12 | 0 | 2 | 86.7002 | 17.6608 | 2018-03-12 | 0 | 2 | 86.9352 | 18.4303 | 2018-03-12 | 0 | 2 | 65.9815 | 13.8561
2018-03-12 01:00 | 1 | 2 | 86.0426 | 18.155 | 2018-03-12 01:00 | 1 | 2 | 86.3127 | 17.5819 | 2018-03-12 01:00 | 1 | 2 | 86.5278 | 18.3439 | 2018-03-12 01:00 | 1 | 2 | 65.6794 | 13.7927
2018-03-12 02:00 | 2 | 2 | 86.392 | 18.2287 | 2018-03-12 02:00 | 2 | 2 | 86.6392 | 17.6484 | 2018-03-12 02:00 | 2 | 2 | 86.8421 | 18.4105 | 2018-03-12 02:00 | 2 | 2 | 65.9229 | 13.8438
2018-03-12 03:00 | 3 | 2 | 86.2776 | 18.2046 | 2018-03-12 03:00 | 3 | 2 | 86.5766 | 17.6357 | 2018-03-12 03:00 | 3 | 2 | 86.7536 | 18.3918 | 2018-03-12 03:00 | 3 | 2 | 65.8655 | 13.8317
2018-03-12 04:00 | 4 | 2 | 86.5034 | 18.2522 | 2018-03-12 04:00 | 4 | 2 | 86.8849 | 17.6985 | 2018-03-12 04:00 | 4 | 2 | 87.0283 | 18.45 | 2018-03-12 04:00 | 4 | 2 | 66.087 | 13.8783
2018-03-12 05:00 | 5 | 2 | 86.3661 | 18.2232 | 2018-03-12 05:00 | 5 | 2 | 86.772 | 17.6755 | 2018-03-12 05:00 | 5 | 2 | 87.0054 | 18.4451 | 2018-03-12 05:00 | 5 | 2 | 66.0354 | 13.8674
2018-03-12 06:00 | 6 | 2 | 86.2898 | 18.2071 | 2018-03-12 06:00 | 6 | 2 | 86.6499 | 17.6506 | 2018-03-12 06:00 | 6 | 2 | 86.8147 | 18.4047 | 2018-03-12 06:00 | 6 | 2 | 65.9165 | 13.8425
2018-03-12 07:00 | 7 | 2 | 86.2043 | 18.1891 | 2018-03-12 07:00 | 7 | 2 | 86.5278 | 17.6257 | 2018-03-12 07:00 | 7 | 2 | 86.7079 | 18.3821 | 2018-03-12 07:00 | 7 | 2 | 65.8296 | 13.8242
2018-03-12 08:00 | 8 | 2 | 86.3355 | 18.2168 | 2018-03-12 08:00 | 8 | 2 | 86.5461 | 17.6294 | 2018-03-12 08:00 | 8 | 2 | 86.8025 | 18.4021 | 2018-03-12 08:00 | 8 | 2 | 65.8725 | 13.8332
2018-03-12 09:00 | 9 | 2 | 86.3798 | 18.2261 | 2018-03-12 09:00 | 9 | 2 | 86.7262 | 17.6661 | 2018-03-12 09:00 | 9 | 2 | 86.8711 | 18.4167 | 2018-03-12 09:00 | 9 | 2 | 65.967 | 13.8531
2018-03-12 10:00 | 10 | 2 | 86.2272 | 18.1939 | 2018-03-12 10:00 | 10 | 2 | 86.5156 | 17.6232 | 2018-03-12 10:00 | 10 | 2 | 86.714 | 18.3834 | 2018-03-12 10:00 | 10 | 2 | 65.8272 | 13.8237
2018-03-12 11:00 | 11 | 2 | 86.2119 | 18.1907 | 2018-03-12 11:00 | 11 | 2 | 86.5141 | 17.6229 | 2018-03-12 11:00 | 11 | 2 | 86.7201 | 18.3847 | 2018-03-12 11:00 | 11 | 2 | 65.829 | 13.8241
2018-03-12 12:00 | 12 | 2 | 86.389 | 18.2281 | 2018-03-12 12:00 | 12 | 2 | 86.6835 | 17.6574 | 2018-03-12 12:00 | 12 | 2 | 86.8574 | 18.4138 | 2018-03-12 12:00 | 12 | 2 | 65.9455 | 13.8486
2018-03-12 13:00 | 13 | 2 | 86.4027 | 18.231 | 2018-03-12 13:00 | 13 | 2 | 86.6224 | 17.645 | 2018-03-12 13:00 | 13 | 2 | 86.7475 | 18.3905 | 2018-03-12 13:00 | 13 | 2 | 65.8806 | 13.8349
2018-03-12 14:00 | 14 | 2 | 86.3783 | 18.2258 | 2018-03-12 14:00 | 14 | 2 | 86.6606 | 17.6528 | 2018-03-12 14:00 | 14 | 2 | 86.7903 | 18.3995 | 2018-03-12 14:00 | 14 | 2 | 65.9113 | 13.8414
2018-03-12 15:00 | 15 | 2 | 86.3355 | 18.2168 | 2018-03-12 15:00 | 15 | 2 | 86.5248 | 17.6251 | 2018-03-12 15:00 | 15 | 2 | 86.7384 | 18.3885 | 2018-03-12 15:00 | 15 | 2 | 65.84 | 13.8264
2018-03-12 16:00 | 16 | 2 | 86.3493 | 18.2197 | 2018-03-12 16:00 | 16 | 2 | 86.4912 | 17.6183 | 2018-03-12 16:00 | 16 | 2 | 86.685 | 18.3772 | 2018-03-12 16:00 | 16 | 2 | 65.807 | 13.8195
2018-03-12 17:00 | 17 | 2 | 86.244 | 18.1975 | 2018-03-12 17:00 | 17 | 2 | 86.4683 | 17.6136 | 2018-03-12 17:00 | 17 | 2 | 86.6743 | 18.375 | 2018-03-12 17:00 | 17 | 2 | 65.7942 | 13.8168
2018-03-12 18:00 | 18 | 2 | 86.3142 | 18.2123 | 2018-03-12 18:00 | 18 | 2 | 86.4378 | 17.6074 | 2018-03-12 18:00 | 18 | 2 | 86.5934 | 18.3578 | 2018-03-12 18:00 | 18 | 2 | 65.7519 | 13.8079
2018-03-12 19:00 | 19 | 2 | 86.2089 | 18.1901 | 2018-03-12 19:00 | 19 | 2 | 86.3508 | 17.5897 | 2018-03-12 19:00 | 19 | 2 | 86.5583 | 18.3504 | 2018-03-12 19:00 | 19 | 2 | 65.7055 | 13.7981
2018-03-12 20:00 | 20 | 2 | 86.2181 | 18.192 | 2018-03-12 20:00 | 20 | 2 | 86.4836 | 17.6167 | 2018-03-12 20:00 | 20 | 2 | 86.6896 | 18.3782 | 2018-03-12 20:00 | 20 | 2 | 65.8058 | 13.8192
2018-03-12 21:00 | 21 | 2 | 86.1494 | 18.1775 | 2018-03-12 21:00 | 21 | 2 | 86.4759 | 17.6151 | 2018-03-12 21:00 | 21 | 2 | 86.63 | 18.3656 | 2018-03-12 21:00 | 21 | 2 | 65.7802 | 13.8139
2018-03-12 22:00 | 22 | 2 | 86.2593 | 18.2007 | 2018-03-12 22:00 | 22 | 2 | 86.5522 | 17.6307 | 2018-03-12 22:00 | 22 | 2 | 86.6468 | 18.3691 | 2018-03-12 22:00 | 22 | 2 | 65.8156 | 13.8213
2018-03-12 23:00 | 23 | 2 | 86.4424 | 18.2393 | 2018-03-12 23:00 | 23 | 2 | 86.8055 | 17.6823 | 2018-03-12 23:00 | 23 | 2 | 86.8864 | 18.4199 | 2018-03-12 23:00 | 23 | 2 | 66.0029 | 13.8606
2018-03-13 | 0 | 3 | 86.4637 | 18.2438 | 2018-03-13 | 0 | 3 | 0 | 0 | 2018-03-13 | 0 | 3 | 0 | 0 | 2018-03-13 | 0 | 3 | 0 | 0
2018-03-13 01:00 | 1 | 3 | 86.5629 | 18.2648 | 2018-03-13 01:00 | 1 | 3 | 0 | 0 | 2018-03-13 01:00 | 1 | 3 | 0 | 0 | 2018-03-13 01:00 | 1 | 3 | 0 | 0
2018-03-13 02:00 | 2 | 3 | 86.3706 | 18.2242 | 2018-03-13 02:00 | 2 | 3 | 0 | 0 | 2018-03-13 02:00 | 2 | 3 | 0 | 0 | 2018-03-13 02:00 | 2 | 3 | 0 | 0
2018-03-13 03:00 | 3 | 3 | 86.3523 | 18.2203 | 2018-03-13 03:00 | 3 | 3 | 0 | 0 | 2018-03-13 03:00 | 3 | 3 | 0 | 0 | 2018-03-13 03:00 | 3 | 3 | 0 | 0
2018-03-13 04:00 | 4 | 3 | 86.3676 | 18.2236 | 2018-03-13 04:00 | 4 | 3 | 0 | 0 | 2018-03-13 04:00 | 4 | 3 | 0 | 0 | 2018-03-13 04:00 | 4 | 3 | 0 | 0
2018-03-13 05:00 | 5 | 3 | 86.4027 | 18.231 | 2018-03-13 05:00 | 5 | 3 | 0 | 0 | 2018-03-13 05:00 | 5 | 3 | 0 | 0 | 2018-03-13 05:00 | 5 | 3 | 0 | 0
2018-03-13 06:00 | 6 | 3 | 86.4652 | 18.2442 | 2018-03-13 06:00 | 6 | 3 | 0 | 0 | 2018-03-13 06:00 | 6 | 3 | 0 | 0 | 2018-03-13 06:00 | 6 | 3 | 0 | 0
2018-03-13 07:00 | 7 | 3 | 86.4012 | 18.2307 | 2018-03-13 07:00 | 7 | 3 | 0 | 0 | 2018-03-13 07:00 | 7 | 3 | 0 | 0 | 2018-03-13 07:00 | 7 | 3 | 0 | 0
2018-03-13 08:00 | 8 | 3 | 86.4515 | 18.2413 | 2018-03-13 08:00 | 8 | 3 | 0 | 0 | 2018-03-13 08:00 | 8 | 3 | 0 | 0 | 2018-03-13 08:00 | 8 | 3 | 0 | 0
2018-03-13 09:00 | 9 | 3 | 86.2028 | 18.1888 | 2018-03-13 09:00 | 9 | 3 | 0 | 0 | 2018-03-13 09:00 | 9 | 3 | 0 | 0 | 2018-03-13 09:00 | 9 | 3 | 0 | 0
2018-03-13 10:00 | 10 | 3 | 86.2715 | 18.2033 | 2018-03-13 10:00 | 10 | 3 | 0 | 0 | 2018-03-13 10:00 | 10 | 3 | 0 | 0 | 2018-03-13 10:00 | 10 | 3 | 0 | 0
2018-03-13 11:00 | 11 | 3 | 86.7567 | 18.3057 | 2018-03-13 11:00 | 11 | 3 | 0 | 0 | 2018-03-13 11:00 | 11 | 3 | 0 | 0 | 2018-03-13 11:00 | 11 | 3 | 0 | 0
2018-03-13 12:00 | 12 | 3 | 86.6194 | 18.2767 | 2018-03-13 12:00 | 12 | 3 | 0 | 0 | 2018-03-13 12:00 | 12 | 3 | 0 | 0 | 2018-03-13 12:00 | 12 | 3 | 0 | 0
2018-03-13 13:00 | 13 | 3 | 86.6377 | 18.2806 | 2018-03-13 13:00 | 13 | 3 | 0 | 0 | 2018-03-13 13:00 | 13 | 3 | 0 | 0 | 2018-03-13 13:00 | 13 | 3 | 0 | 0
2018-03-13 14:00 | 14 | 3 | 86.8757 | 18.3308 | 2018-03-13 14:00 | 14 | 3 | 0 | 0 | 2018-03-13 14:00 | 14 | 3 | 0 | 0 | 2018-03-13 14:00 | 14 | 3 | 0 | 0
2018-03-13 15:00 | 15 | 3 | 86.7994 | 18.3147 | 2018-03-13 15:00 | 15 | 3 | 0 | 0 | 2018-03-13 15:00 | 15 | 3 | 0 | 0 | 2018-03-13 15:00 | 15 | 3 | 0 | 0
2018-03-13 16:00 | 16 | 3 | 86.7674 | 18.3079 | 2018-03-13 16:00 | 16 | 3 | 0 | 0 | 2018-03-13 16:00 | 16 | 3 | 0 | 0 | 2018-03-13 16:00 | 16 | 3 | 0 | 0
2018-03-13 17:00 | 17 | 3 | 86.7384 | 18.3018 | 2018-03-13 17:00 | 17 | 3 | 0 | 0 | 2018-03-13 17:00 | 17 | 3 | 0 | 0 | 2018-03-13 17:00 | 17 | 3 | 0 | 0
2018-03-13 18:00 | 18 | 3 | 86.7124 | 18.2963 | 2018-03-13 18:00 | 18 | 3 | 0 | 0 | 2018-03-13 18:00 | 18 | 3 | 0 | 0 | 2018-03-13 18:00 | 18 | 3 | 0 | 0
2018-03-13 19:00 | 19 | 3 | 86.8376 | 18.3227 | 2018-03-13 19:00 | 19 | 3 | 0 | 0 | 2018-03-13 19:00 | 19 | 3 | 0 | 0 | 2018-03-13 19:00 | 19 | 3 | 0 | 0
2018-03-13 20:00 | 20 | 3 | 86.627 | 18.2783 | 2018-03-13 20:00 | 20 | 3 | 0 | 0 | 2018-03-13 20:00 | 20 | 3 | 0 | 0 | 2018-03-13 20:00 | 20 | 3 | 0 | 0
2018-03-13 21:00 | 21 | 3 | 86.6239 | 18.2776 | 2018-03-13 21:00 | 21 | 3 | 0 | 0 | 2018-03-13 21:00 | 21 | 3 | 0 | 0 | 2018-03-13 21:00 | 21 | 3 | 0 | 0
2018-03-13 22:00 | 22 | 3 | 86.714 | 18.2967 | 2018-03-13 22:00 | 22 | 3 | 0 | 0 | 2018-03-13 22:00 | 22 | 3 | 0 | 0 | 2018-03-13 22:00 | 22 | 3 | 0 | 0
2018-03-13 23:00 | 23 | 3 | 86.8971 | 18.3353 | 2018-03-13 23:00 | 23 | 3 | 0 | 0 | 2018-03-13 23:00 | 23 | 3 | 0 | 0 | 2018-03-13 23:00 | 23 | 3 | 0 | 0
2018-03-14 | 0 | 4 | 0 | 0 | 2018-03-14 | 0 | 4 | 0 | 0 | 2018-03-14 | 0 | 4 | 86.6712 | 18.3743 | 2018-03-14 | 0 | 4 | 32.9351 | 6.9164
2018-03-14 01:00 | 1 | 4 | 0 | 0 | 2018-03-14 01:00 | 1 | 4 | 0 | 0 | 2018-03-14 01:00 | 1 | 4 | 86.511 | 18.3403 | 2018-03-14 01:00 | 1 | 4 | 32.8742 | 6.9036
2018-03-14 02:00 | 2 | 4 | 0 | 0 | 2018-03-14 02:00 | 2 | 4 | 0 | 0 | 2018-03-14 02:00 | 2 | 4 | 86.7628 | 18.3937 | 2018-03-14 02:00 | 2 | 4 | 32.9699 | 6.9237
2018-03-14 03:00 | 3 | 4 | 0 | 0 | 2018-03-14 03:00 | 3 | 4 | 0 | 0 | 2018-03-14 03:00 | 3 | 4 | 86.7384 | 18.3885 | 2018-03-14 03:00 | 3 | 4 | 32.9606 | 6.9217
2018-03-14 04:00 | 4 | 4 | 0 | 0 | 2018-03-14 04:00 | 4 | 4 | 0 | 0 | 2018-03-14 04:00 | 4 | 4 | 86.8376 | 18.4096 | 2018-03-14 04:00 | 4 | 4 | 32.9983 | 6.9296
2018-03-14 05:00 | 5 | 4 | 0 | 0 | 2018-03-14 05:00 | 5 | 4 | 0 | 0 | 2018-03-14 05:00 | 5 | 4 | 87.0222 | 18.4487 | 2018-03-14 05:00 | 5 | 4 | 33.0684 | 6.9444
2018-03-14 06:00 | 6 | 4 | 0 | 0 | 2018-03-14 06:00 | 6 | 4 | 0 | 0 | 2018-03-14 06:00 | 6 | 4 | 86.9627 | 18.4361 | 2018-03-14 06:00 | 6 | 4 | 33.0458 | 6.9396
2018-03-14 07:00 | 7 | 4 | 0 | 0 | 2018-03-14 07:00 | 7 | 4 | 0 | 0 | 2018-03-14 07:00 | 7 | 4 | 87.1321 | 18.472 | 2018-03-14 07:00 | 7 | 4 | 33.1102 | 6.9531
2018-03-14 08:00 | 8 | 4 | 0 | 0 | 2018-03-14 08:00 | 8 | 4 | 0 | 0 | 2018-03-14 08:00 | 8 | 4 | 87.1931 | 18.4849 | 2018-03-14 08:00 | 8 | 4 | 33.1334 | 6.958
2018-03-14 09:00 | 9 | 4 | 0 | 0 | 2018-03-14 09:00 | 9 | 4 | 0 | 0 | 2018-03-14 09:00 | 9 | 4 | 86.7155 | 18.3837 | 2018-03-14 09:00 | 9 | 4 | 32.9519 | 6.9199
2018-03-14 10:00 | 10 | 4 | 0 | 0 | 2018-03-14 10:00 | 10 | 4 | 0 | 0 | 2018-03-14 10:00 | 10 | 4 | 86.6743 | 18.375 | 2018-03-14 10:00 | 10 | 4 | 32.9362 | 6.9166
2018-03-14 11:00 | 11 | 4 | 0 | 0 | 2018-03-14 11:00 | 11 | 4 | 0 | 0 | 2018-03-14 11:00 | 11 | 4 | 86.8956 | 18.4219 | 2018-03-14 11:00 | 11 | 4 | 33.0203 | 6.9343
2018-03-14 12:00 | 12 | 4 | 0 | 0 | 2018-03-14 12:00 | 12 | 4 | 0 | 0 | 2018-03-14 12:00 | 12 | 4 | 86.9276 | 18.4287 | 2018-03-14 12:00 | 12 | 4 | 33.0325 | 6.9368
2018-03-14 13:00 | 13 | 4 | 0 | 0 | 2018-03-14 13:00 | 13 | 4 | 0 | 0 | 2018-03-14 13:00 | 13 | 4 | 87.2541 | 18.4979 | 2018-03-14 13:00 | 13 | 4 | 33.1566 | 6.9629
2018-03-14 14:00 | 14 | 4 | 0 | 0 | 2018-03-14 14:00 | 14 | 4 | 0 | 0 | 2018-03-14 14:00 | 14 | 4 | 87.4037 | 18.5296 | 2018-03-14 14:00 | 14 | 4 | 33.2134 | 6.9748
2018-03-14 15:00 | 15 | 4 | 0 | 0 | 2018-03-14 15:00 | 15 | 4 | 0 | 0 | 2018-03-14 15:00 | 15 | 4 | 87.2129 | 18.4891 | 2018-03-14 15:00 | 15 | 4 | 33.1409 | 6.9596
2018-03-14 16:00 | 16 | 4 | 0 | 0 | 2018-03-14 16:00 | 16 | 4 | 0 | 0 | 2018-03-14 16:00 | 16 | 4 | 86.9718 | 18.438 | 2018-03-14 16:00 | 16 | 4 | 33.0493 | 6.9403
2018-03-14 17:00 | 17 | 4 | 0 | 0 | 2018-03-14 17:00 | 17 | 4 | 0 | 0 | 2018-03-14 17:00 | 17 | 4 | 87.1397 | 18.4736 | 2018-03-14 17:00 | 17 | 4 | 33.1131 | 6.9537
2018-03-14 18:00 | 18 | 4 | 0 | 0 | 2018-03-14 18:00 | 18 | 4 | 0 | 0 | 2018-03-14 18:00 | 18 | 4 | 87.2435 | 18.4956 | 2018-03-14 18:00 | 18 | 4 | 33.1525 | 6.962
2018-03-14 19:00 | 19 | 4 | 0 | 0 | 2018-03-14 19:00 | 19 | 4 | 0 | 0 | 2018-03-14 19:00 | 19 | 4 | 86.8894 | 18.4206 | 2018-03-14 19:00 | 19 | 4 | 33.018 | 6.9338
2018-03-14 20:00 | 20 | 4 | 0 | 0 | 2018-03-14 20:00 | 20 | 4 | 0 | 0 | 2018-03-14 20:00 | 20 | 4 | 87.1839 | 18.483 | 2018-03-14 20:00 | 20 | 4 | 33.1299 | 6.9573
2018-03-14 21:00 | 21 | 4 | 0 | 0 | 2018-03-14 21:00 | 21 | 4 | 0 | 0 | 2018-03-14 21:00 | 21 | 4 | 87.2419 | 18.4953 | 2018-03-14 21:00 | 21 | 4 | 33.1519 | 6.9619
2018-03-14 22:00 | 22 | 4 | 0 | 0 | 2018-03-14 22:00 | 22 | 4 | 0 | 0 | 2018-03-14 22:00 | 22 | 4 | 87.1733 | 18.4807 | 2018-03-14 22:00 | 22 | 4 | 33.1259 | 6.9564
2018-03-14 23:00 | 23 | 4 | 0 | 0 | 2018-03-14 23:00 | 23 | 4 | 0 | 0 | 2018-03-14 23:00 | 23 | 4 | 87.2557 | 18.4982 | 2018-03-14 23:00 | 23 | 4 | 33.1572 | 6.963
2018-03-15 | 0 | 5 | 86.5492 | 18.2619 | 2018-03-15 | 0 | 5 | 0 | 0 | 2018-03-15 | 0 | 5 | 0 | 0 | 2018-03-15 | 0 | 5 | 0 | 0
2018-03-15 01:00 | 1 | 5 | 86.7201 | 18.2979 | 2018-03-15 01:00 | 1 | 5 | 0 | 0 | 2018-03-15 01:00 | 1 | 5 | 0 | 0 | 2018-03-15 01:00 | 1 | 5 | 0 | 0
2018-03-15 02:00 | 2 | 5 | 86.5095 | 18.2535 | 2018-03-15 02:00 | 2 | 5 | 0 | 0 | 2018-03-15 02:00 | 2 | 5 | 0 | 0 | 2018-03-15 02:00 | 2 | 5 | 0 | 0
2018-03-15 03:00 | 3 | 5 | 86.4576 | 18.2426 | 2018-03-15 03:00 | 3 | 5 | 0 | 0 | 2018-03-15 03:00 | 3 | 5 | 0 | 0 | 2018-03-15 03:00 | 3 | 5 | 0 | 0
2018-03-15 04:00 | 4 | 5 | 86.6316 | 18.2793 | 2018-03-15 04:00 | 4 | 5 | 0 | 0 | 2018-03-15 04:00 | 4 | 5 | 0 | 0 | 2018-03-15 04:00 | 4 | 5 | 0 | 0
2018-03-15 05:00 | 5 | 5 | 86.569 | 18.2661 | 2018-03-15 05:00 | 5 | 5 | 0 | 0 | 2018-03-15 05:00 | 5 | 5 | 0 | 0 | 2018-03-15 05:00 | 5 | 5 | 0 | 0
2018-03-15 06:00 | 6 | 5 | 86.6468 | 18.2825 | 2018-03-15 06:00 | 6 | 5 | 0 | 0 | 2018-03-15 06:00 | 6 | 5 | 0 | 0 | 2018-03-15 06:00 | 6 | 5 | 0 | 0
2018-03-15 07:00 | 7 | 5 | 86.6361 | 18.2802 | 2018-03-15 07:00 | 7 | 5 | 0 | 0 | 2018-03-15 07:00 | 7 | 5 | 0 | 0 | 2018-03-15 07:00 | 7 | 5 | 0 | 0
2018-03-15 08:00 | 8 | 5 | 86.6819 | 18.2899 | 2018-03-15 08:00 | 8 | 5 | 0 | 0 | 2018-03-15 08:00 | 8 | 5 | 0 | 0 | 2018-03-15 08:00 | 8 | 5 | 0 | 0
2018-03-15 09:00 | 9 | 5 | 86.7094 | 18.2957 | 2018-03-15 09:00 | 9 | 5 | 0 | 0 | 2018-03-15 09:00 | 9 | 5 | 0 | 0 | 2018-03-15 09:00 | 9 | 5 | 0 | 0
2018-03-15 10:00 | 10 | 5 | 86.7933 | 18.3134 | 2018-03-15 10:00 | 10 | 5 | 0 | 0 | 2018-03-15 10:00 | 10 | 5 | 0 | 0 | 2018-03-15 10:00 | 10 | 5 | 0 | 0
2018-03-15 11:00 | 11 | 5 | 86.8009 | 18.315 | 2018-03-15 11:00 | 11 | 5 | 0 | 0 | 2018-03-15 11:00 | 11 | 5 | 0 | 0 | 2018-03-15 11:00 | 11 | 5 | 0 | 0
2018-03-15 12:00 | 12 | 5 | 86.6728 | 18.288 | 2018-03-15 12:00 | 12 | 5 | 0 | 0 | 2018-03-15 12:00 | 12 | 5 | 0 | 0 | 2018-03-15 12:00 | 12 | 5 | 0 | 0
2018-03-15 13:00 | 13 | 5 | 86.6316 | 18.2793 | 2018-03-15 13:00 | 13 | 5 | 0 | 0 | 2018-03-15 13:00 | 13 | 5 | 0 | 0 | 2018-03-15 13:00 | 13 | 5 | 0 | 0
2018-03-15 14:00 | 14 | 5 | 86.6316 | 18.2793 | 2018-03-15 14:00 | 14 | 5 | 0 | 0 | 2018-03-15 14:00 | 14 | 5 | 0 | 0 | 2018-03-15 14:00 | 14 | 5 | 0 | 0
2018-03-15 15:00 | 15 | 5 | 86.6636 | 18.286 | 2018-03-15 15:00 | 15 | 5 | 0 | 0 | 2018-03-15 15:00 | 15 | 5 | 0 | 0 | 2018-03-15 15:00 | 15 | 5 | 0 | 0
2018-03-15 16:00 | 16 | 5 | 86.5568 | 18.2635 | 2018-03-15 16:00 | 16 | 5 | 0 | 0 | 2018-03-15 16:00 | 16 | 5 | 0 | 0 | 2018-03-15 16:00 | 16 | 5 | 0 | 0
2018-03-15 17:00 | 17 | 5 | 86.6865 | 18.2909 | 2018-03-15 17:00 | 17 | 5 | 0 | 0 | 2018-03-15 17:00 | 17 | 5 | 0 | 0 | 2018-03-15 17:00 | 17 | 5 | 0 | 0
2018-03-15 18:00 | 18 | 5 | 86.7262 | 18.2992 | 2018-03-15 18:00 | 18 | 5 | 0 | 0 | 2018-03-15 18:00 | 18 | 5 | 0 | 0 | 2018-03-15 18:00 | 18 | 5 | 0 | 0
2018-03-15 19:00 | 19 | 5 | 86.5187 | 18.2554 | 2018-03-15 19:00 | 19 | 5 | 0 | 0 | 2018-03-15 19:00 | 19 | 5 | 0 | 0 | 2018-03-15 19:00 | 19 | 5 | 0 | 0
2018-03-15 20:00 | 20 | 5 | 86.5766 | 18.2677 | 2018-03-15 20:00 | 20 | 5 | 0 | 0 | 2018-03-15 20:00 | 20 | 5 | 0 | 0 | 2018-03-15 20:00 | 20 | 5 | 0 | 0
2018-03-15 21:00 | 21 | 5 | 86.6194 | 18.2767 | 2018-03-15 21:00 | 21 | 5 | 0 | 0 | 2018-03-15 21:00 | 21 | 5 | 0 | 0 | 2018-03-15 21:00 | 21 | 5 | 0 | 0
2018-03-15 22:00 | 22 | 5 | 86.6743 | 18.2883 | 2018-03-15 22:00 | 22 | 5 | 0 | 0 | 2018-03-15 22:00 | 22 | 5 | 0 | 0 | 2018-03-15 22:00 | 22 | 5 | 0 | 0
2018-03-15 23:00 | 23 | 5 | 86.5644 | 18.2651 | 2018-03-15 23:00 | 23 | 5 | 0 | 0 | 2018-03-15 23:00 | 23 | 5 | 0 | 0 | 2018-03-15 23:00 | 23 | 5 | 0 | 0
2018-03-16 | 0 | 6 | 86.2226 | 18.193 | 2018-03-16 | 0 | 6 | 86.688 | 17.6583 | 2018-03-16 | 0 | 6 | 0 | 0 | 2018-03-16 | 0 | 6 | 32.9414 | 6.9177
2018-03-16 01:00 | 1 | 6 | 86.1128 | 18.1698 | 2018-03-16 01:00 | 1 | 6 | 86.5232 | 17.6248 | 2018-03-16 01:00 | 1 | 6 | 0 | 0 | 2018-03-16 01:00 | 1 | 6 | 32.8788 | 6.9046
2018-03-16 02:00 | 2 | 6 | 86.2791 | 18.2049 | 2018-03-16 02:00 | 2 | 6 | 86.6896 | 17.6587 | 2018-03-16 02:00 | 2 | 6 | 0 | 0 | 2018-03-16 02:00 | 2 | 6 | 32.942 | 6.9178
2018-03-16 03:00 | 3 | 6 | 86.0014 | 18.1463 | 2018-03-16 03:00 | 3 | 6 | 86.4485 | 17.6096 | 2018-03-16 03:00 | 3 | 6 | 0 | 0 | 2018-03-16 03:00 | 3 | 6 | 32.8504 | 6.8986
2018-03-16 04:00 | 4 | 6 | 86.0533 | 18.1572 | 2018-03-16 04:00 | 4 | 6 | 86.4347 | 17.6067 | 2018-03-16 04:00 | 4 | 6 | 0 | 0 | 2018-03-16 04:00 | 4 | 6 | 32.8452 | 6.8975
2018-03-16 05:00 | 5 | 6 | 86.2257 | 18.1936 | 2018-03-16 05:00 | 5 | 6 | 86.6117 | 17.6428 | 2018-03-16 05:00 | 5 | 6 | 0 | 0 | 2018-03-16 05:00 | 5 | 6 | 32.9124 | 6.9116
2018-03-16 06:00 | 6 | 6 | 86.4332 | 18.2374 | 2018-03-16 06:00 | 6 | 6 | 86.9352 | 17.7087 | 2018-03-16 06:00 | 6 | 6 | 0 | 0 | 2018-03-16 06:00 | 6 | 6 | 33.0354 | 6.9374
2018-03-16 07:00 | 7 | 6 | 86.5873 | 18.2699 | 2018-03-16 07:00 | 7 | 6 | 87.0619 | 17.7345 | 2018-03-16 07:00 | 7 | 6 | 0 | 0 | 2018-03-16 07:00 | 7 | 6 | 33.0835 | 6.9475
2018-03-16 08:00 | 8 | 6 | 86.3691 | 18.2239 | 2018-03-16 08:00 | 8 | 6 | 86.7811 | 17.6773 | 2018-03-16 08:00 | 8 | 6 | 0 | 0 | 2018-03-16 08:00 | 8 | 6 | 32.9768 | 6.9251
2018-03-16 09:00 | 9 | 6 | 86.334 | 18.2165 | 2018-03-16 09:00 | 9 | 6 | 86.7399 | 17.6689 | 2018-03-16 09:00 | 9 | 6 | 0 | 0 | 2018-03-16 09:00 | 9 | 6 | 32.9612 | 6.9218
2018-03-16 10:00 | 10 | 6 | 86.5126 | 18.2542 | 2018-03-16 10:00 | 10 | 6 | 86.862 | 17.6938 | 2018-03-16 10:00 | 10 | 6 | 0 | 0 | 2018-03-16 10:00 | 10 | 6 | 33.0076 | 6.9316
2018-03-16 11:00 | 11 | 6 | 86.5003 | 18.2516 | 2018-03-16 11:00 | 11 | 6 | 86.9306 | 17.7078 | 2018-03-16 11:00 | 11 | 6 | 0 | 0 | 2018-03-16 11:00 | 11 | 6 | 33.0336 | 6.9371
2018-03-16 12:00 | 12 | 6 | 86.7002 | 18.2937 | 2018-03-16 12:00 | 12 | 6 | 87.1412 | 17.7507 | 2018-03-16 12:00 | 12 | 6 | 0 | 0 | 2018-03-16 12:00 | 12 | 6 | 33.1137 | 6.9539
2018-03-16 13:00 | 13 | 6 | 86.363 | 18.2226 | 2018-03-16 13:00 | 13 | 6 | 86.8009 | 17.6813 | 2018-03-16 13:00 | 13 | 6 | 0 | 0 | 2018-03-16 13:00 | 13 | 6 | 32.9843 | 6.9267
2018-03-16 14:00 | 14 | 6 | 86.4408 | 18.239 | 2018-03-16 14:00 | 14 | 6 | 86.8635 | 17.6941 | 2018-03-16 14:00 | 14 | 6 | 0 | 0 | 2018-03-16 14:00 | 14 | 6 | 33.0081 | 6.9317
2018-03-16 15:00 | 15 | 6 | 86.2943 | 18.2081 | 2018-03-16 15:00 | 15 | 6 | 86.6743 | 17.6556 | 2018-03-16 15:00 | 15 | 6 | 0 | 0 | 2018-03-16 15:00 | 15 | 6 | 32.9362 | 6.9166
2018-03-16 16:00 | 16 | 6 | 86.3706 | 18.2242 | 2018-03-16 16:00 | 16 | 6 | 86.7491 | 17.6708 | 2018-03-16 16:00 | 16 | 6 | 0 | 0 | 2018-03-16 16:00 | 16 | 6 | 32.9647 | 6.9226
2018-03-16 17:00 | 17 | 6 | 86.2882 | 18.2068 | 2018-03-16 17:00 | 17 | 6 | 86.7445 | 17.6699 | 2018-03-16 17:00 | 17 | 6 | 0 | 0 | 2018-03-16 17:00 | 17 | 6 | 32.9629 | 6.9222
2018-03-16 18:00 | 18 | 6 | 86.1875 | 18.1856 | 2018-03-16 18:00 | 18 | 6 | 86.6667 | 17.654 | 2018-03-16 18:00 | 18 | 6 | 0 | 0 | 2018-03-16 18:00 | 18 | 6 | 32.9333 | 6.916
2018-03-16 19:00 | 19 | 6 | 86.099 | 18.1669 | 2018-03-16 19:00 | 19 | 6 | 86.5431 | 17.6288 | 2018-03-16 19:00 | 19 | 6 | 0 | 0 | 2018-03-16 19:00 | 19 | 6 | 32.8864 | 6.9061
2018-03-16 20:00 | 20 | 6 | 86.1997 | 18.1881 | 2018-03-16 20:00 | 20 | 6 | 86.5187 | 17.6239 | 2018-03-16 20:00 | 20 | 6 | 0 | 0 | 2018-03-16 20:00 | 20 | 6 | 32.8771 | 6.9042
2018-03-16 21:00 | 21 | 6 | 86.3767 | 18.2255 | 2018-03-16 21:00 | 21 | 6 | 86.7247 | 17.6658 | 2018-03-16 21:00 | 21 | 6 | 0 | 0 | 2018-03-16 21:00 | 21 | 6 | 32.9554 | 6.9206
2018-03-16 22:00 | 22 | 6 | 86.3691 | 18.2239 | 2018-03-16 22:00 | 22 | 6 | 86.7659 | 17.6742 | 2018-03-16 22:00 | 22 | 6 | 0 | 0 | 2018-03-16 22:00 | 22 | 6 | 32.971 | 6.9239
2018-03-16 23:00 | 23 | 6 | 86.4012 | 18.2307 | 2018-03-16 23:00 | 23 | 6 | 86.7918 | 17.6795 | 2018-03-16 23:00 | 23 | 6 | 0 | 0 | 2018-03-16 23:00 | 23 | 6 | 32.9809 | 6.926
2018-03-17 | 0 | 7 | 86.0121 | 18.1486 | 2018-03-17 | 0 | 7 | 0 | 0 | 2018-03-17 | 0 | 7 | 86.5507 | 18.3487 | 2018-03-17 | 0 | 7 | 32.8893 | 6.9067
2018-03-17 01:00 | 1 | 7 | 85.919 | 18.1289 | 2018-03-17 01:00 | 1 | 7 | 0 | 0 | 2018-03-17 01:00 | 1 | 7 | 86.5324 | 18.3449 | 2018-03-17 01:00 | 1 | 7 | 32.8823 | 6.9053
2018-03-17 02:00 | 2 | 7 | 86.0533 | 18.1572 | 2018-03-17 02:00 | 2 | 7 | 0 | 0 | 2018-03-17 02:00 | 2 | 7 | 86.6453 | 18.3688 | 2018-03-17 02:00 | 2 | 7 | 32.9252 | 6.9143
2018-03-17 03:00 | 3 | 7 | 86.1677 | 18.1814 | 2018-03-17 03:00 | 3 | 7 | 0 | 0 | 2018-03-17 03:00 | 3 | 7 | 86.7002 | 18.3804 | 2018-03-17 03:00 | 3 | 7 | 32.9461 | 6.9187
2018-03-17 04:00 | 4 | 7 | 86.3081 | 18.211 | 2018-03-17 04:00 | 4 | 7 | 0 | 0 | 2018-03-17 04:00 | 4 | 7 | 86.8513 | 18.4125 | 2018-03-17 04:00 | 4 | 7 | 33.0035 | 6.9307
2018-03-17 05:00 | 5 | 7 | 86.2562 | 18.2001 | 2018-03-17 05:00 | 5 | 7 | 0 | 0 | 2018-03-17 05:00 | 5 | 7 | 86.8605 | 18.4144 | 2018-03-17 05:00 | 5 | 7 | 33.007 | 6.9315
2018-03-17 06:00 | 6 | 7 | 86.1234 | 18.172 | 2018-03-17 06:00 | 6 | 7 | 0 | 0 | 2018-03-17 06:00 | 6 | 7 | 86.6682 | 18.3737 | 2018-03-17 06:00 | 6 | 7 | 32.9339 | 6.9161
2018-03-17 07:00 | 7 | 7 | 86.1906 | 18.1862 | 2018-03-17 07:00 | 7 | 7 | 0 | 0 | 2018-03-17 07:00 | 7 | 7 | 86.7247 | 18.3856 | 2018-03-17 07:00 | 7 | 7 | 32.9554 | 6.9206
2018-03-17 08:00 | 8 | 7 | 86.36 | 18.222 | 2018-03-17 08:00 | 8 | 7 | 0 | 0 | 2018-03-17 08:00 | 8 | 7 | 86.952 | 18.4338 | 2018-03-17 08:00 | 8 | 7 | 33.0418 | 6.9388
2018-03-17 09:00 | 9 | 7 | 86.4912 | 18.2496 | 2018-03-17 09:00 | 9 | 7 | 0 | 0 | 2018-03-17 09:00 | 9 | 7 | 87.0588 | 18.4565 | 2018-03-17 09:00 | 9 | 7 | 33.0823 | 6.9473
2018-03-17 10:00 | 10 | 7 | 86.1982 | 18.1878 | 2018-03-17 10:00 | 10 | 7 | 0 | 0 | 2018-03-17 10:00 | 10 | 7 | 86.6392 | 18.3675 | 2018-03-17 10:00 | 10 | 7 | 32.9229 | 6.9138
2018-03-17 11:00 | 11 | 7 | 86.1707 | 18.182 | 2018-03-17 11:00 | 11 | 7 | 0 | 0 | 2018-03-17 11:00 | 11 | 7 | 86.8849 | 18.4196 | 2018-03-17 11:00 | 11 | 7 | 33.0163 | 6.9334
2018-03-17 12:00 | 12 | 7 | 86.5019 | 18.2519 | 2018-03-17 12:00 | 12 | 7 | 0 | 0 | 2018-03-17 12:00 | 12 | 7 | 87.1504 | 18.4759 | 2018-03-17 12:00 | 12 | 7 | 33.1172 | 6.9546
2018-03-17 13:00 | 13 | 7 | 86.6148 | 18.2757 | 2018-03-17 13:00 | 13 | 7 | 0 | 0 | 2018-03-17 13:00 | 13 | 7 | 87.3167 | 18.5111 | 2018-03-17 13:00 | 13 | 7 | 33.1803 | 6.9679
2018-03-17 14:00 | 14 | 7 | 86.4439 | 18.2397 | 2018-03-17 14:00 | 14 | 7 | 0 | 0 | 2018-03-17 14:00 | 14 | 7 | 87.0832 | 18.4616 | 2018-03-17 14:00 | 14 | 7 | 33.0916 | 6.9492
2018-03-17 15:00 | 15 | 7 | 86.5522 | 18.2625 | 2018-03-17 15:00 | 15 | 7 | 0 | 0 | 2018-03-17 15:00 | 15 | 7 | 87.2938 | 18.5063 | 2018-03-17 15:00 | 15 | 7 | 33.1716 | 6.966
2018-03-17 16:00 | 16 | 7 | 86.5644 | 18.2651 | 2018-03-17 16:00 | 16 | 7 | 0 | 0 | 2018-03-17 16:00 | 16 | 7 | 87.3579 | 18.5199 | 2018-03-17 16:00 | 16 | 7 | 33.196 | 6.9712
2018-03-17 17:00 | 17 | 7 | 86.7445 | 18.3031 | 2018-03-17 17:00 | 17 | 7 | 0 | 0 | 2018-03-17 17:00 | 17 | 7 | 87.57 | 18.5648 | 2018-03-17 17:00 | 17 | 7 | 33.2766 | 6.9881
2018-03-17 18:00 | 18 | 7 | 86.4668 | 18.2445 | 2018-03-17 18:00 | 18 | 7 | 0 | 0 | 2018-03-17 18:00 | 18 | 7 | 87.3014 | 18.5079 | 2018-03-17 18:00 | 18 | 7 | 33.1745 | 6.9667
2018-03-17 19:00 | 19 | 7 | 86.3661 | 18.2232 | 2018-03-17 19:00 | 19 | 7 | 0 | 0 | 2018-03-17 19:00 | 19 | 7 | 87.0954 | 18.4642 | 2018-03-17 19:00 | 19 | 7 | 33.0963 | 6.9502
2018-03-17 20:00 | 20 | 7 | 86.1173 | 18.1708 | 2018-03-17 20:00 | 20 | 7 | 0 | 0 | 2018-03-17 20:00 | 20 | 7 | 86.891 | 18.4209 | 2018-03-17 20:00 | 20 | 7 | 33.0186 | 6.9339
2018-03-17 21:00 | 21 | 7 | 86.1555 | 18.1788 | 2018-03-17 21:00 | 21 | 7 | 0 | 0 | 2018-03-17 21:00 | 21 | 7 | 86.9245 | 18.428 | 2018-03-17 21:00 | 21 | 7 | 33.0313 | 6.9366
2018-03-17 22:00 | 22 | 7 | 86.2211 | 18.1927 | 2018-03-17 22:00 | 22 | 7 | 0 | 0 | 2018-03-17 22:00 | 22 | 7 | 87.0054 | 18.4451 | 2018-03-17 22:00 | 22 | 7 | 33.0621 | 6.943
2018-03-17 23:00 | 23 | 7 | 86.2226 | 18.193 | 2018-03-17 23:00 | 23 | 7 | 0 | 0 | 2018-03-17 23:00 | 23 | 7 | 87.0787 | 18.4607 | 2018-03-17 23:00 | 23 | 7 | 33.0899 | 6.9489
2018-03-18 | 0 | 1 | 86.2364 | 18.1959 | 2018-03-18 | 0 | 1 | 86.7994 | 17.681 | 2018-03-18 | 0 | 1 | 0 | 0 | 2018-03-18 | 0 | 1 | 32.9838 | 6.9266
2018-03-18 01:00 | 1 | 1 | 86.3188 | 18.2133 | 2018-03-18 01:00 | 1 | 1 | 86.952 | 17.7121 | 2018-03-18 01:00 | 1 | 1 | 0 | 0 | 2018-03-18 01:00 | 1 | 1 | 33.0418 | 6.9388
2018-03-18 02:00 | 2 | 1 | 86.2119 | 18.1907 | 2018-03-18 02:00 | 2 | 1 | 86.8177 | 17.6848 | 2018-03-18 02:00 | 2 | 1 | 0 | 0 | 2018-03-18 02:00 | 2 | 1 | 32.9907 | 6.9281
2018-03-18 03:00 | 3 | 1 | 86.1845 | 18.1849 | 2018-03-18 03:00 | 3 | 1 | 86.7857 | 17.6782 | 2018-03-18 03:00 | 3 | 1 | 0 | 0 | 2018-03-18 03:00 | 3 | 1 | 32.9786 | 6.9255
2018-03-18 04:00 | 4 | 1 | 86.2455 | 18.1978 | 2018-03-18 04:00 | 4 | 1 | 86.833 | 17.6879 | 2018-03-18 04:00 | 4 | 1 | 0 | 0 | 2018-03-18 04:00 | 4 | 1 | 32.9965 | 6.9293
2018-03-18 05:00 | 5 | 1 | 86.2333 | 18.1952 | 2018-03-18 05:00 | 5 | 1 | 86.833 | 17.6879 | 2018-03-18 05:00 | 5 | 1 | 0 | 0 | 2018-03-18 05:00 | 5 | 1 | 32.9965 | 6.9293
2018-03-18 06:00 | 6 | 1 | 86.2776 | 18.2046 | 2018-03-18 06:00 | 6 | 1 | 86.8528 | 17.6919 | 2018-03-18 06:00 | 6 | 1 | 0 | 0 | 2018-03-18 06:00 | 6 | 1 | 33.0041 | 6.9309
2018-03-18 07:00 | 7 | 1 | 86.2867 | 18.2065 | 2018-03-18 07:00 | 7 | 1 | 86.8452 | 17.6904 | 2018-03-18 07:00 | 7 | 1 | 0 | 0 | 2018-03-18 07:00 | 7 | 1 | 33.0012 | 6.9302
2018-03-18 08:00 | 8 | 1 | 86.2989 | 18.2091 | 2018-03-18 08:00 | 8 | 1 | 86.9032 | 17.7022 | 2018-03-18 08:00 | 8 | 1 | 0 | 0 | 2018-03-18 08:00 | 8 | 1 | 33.0232 | 6.9349
2018-03-18 09:00 | 9 | 1 | 86.2867 | 18.2065 | 2018-03-18 09:00 | 9 | 1 | 86.8162 | 17.6845 | 2018-03-18 09:00 | 9 | 1 | 0 | 0 | 2018-03-18 09:00 | 9 | 1 | 32.9902 | 6.9279
2018-03-18 10:00 | 10 | 1 | 86.2882 | 18.2068 | 2018-03-18 10:00 | 10 | 1 | 86.8528 | 17.6919 | 2018-03-18 10:00 | 10 | 1 | 0 | 0 | 2018-03-18 10:00 | 10 | 1 | 33.0041 | 6.9309
2018-03-18 11:00 | 11 | 1 | 86.1845 | 18.1849 | 2018-03-18 11:00 | 11 | 1 | 86.743 | 17.6695 | 2018-03-18 11:00 | 11 | 1 | 0 | 0 | 2018-03-18 11:00 | 11 | 1 | 32.9623 | 6.9221
2018-03-18 12:00 | 12 | 1 | 86.1418 | 18.1759 | 2018-03-18 12:00 | 12 | 1 | 86.714 | 17.6636 | 2018-03-18 12:00 | 12 | 1 | 0 | 0 | 2018-03-18 12:00 | 12 | 1 | 32.9513 | 6.9198
2018-03-18 13:00 | 13 | 1 | 86.1479 | 18.1772 | 2018-03-18 13:00 | 13 | 1 | 86.7659 | 17.6742 | 2018-03-18 13:00 | 13 | 1 | 0 | 0 | 2018-03-18 13:00 | 13 | 1 | 32.971 | 6.9239
2018-03-18 14:00 | 14 | 1 | 86.1112 | 18.1695 | 2018-03-18 14:00 | 14 | 1 | 86.7018 | 17.6612 | 2018-03-18 14:00 | 14 | 1 | 0 | 0 | 2018-03-18 14:00 | 14 | 1 | 32.9467 | 6.9188
2018-03-18 15:00 | 15 | 1 | 86.2455 | 18.1978 | 2018-03-18 15:00 | 15 | 1 | 86.8482 | 17.691 | 2018-03-18 15:00 | 15 | 1 | 0 | 0 | 2018-03-18 15:00 | 15 | 1 | 33.0023 | 6.9305
2018-03-18 16:00 | 16 | 1 | 86.3447 | 18.2187 | 2018-03-18 16:00 | 16 | 1 | 86.9398 | 17.7096 | 2018-03-18 16:00 | 16 | 1 | 0 | 0 | 2018-03-18 16:00 | 16 | 1 | 33.0371 | 6.9378
2018-03-18 17:00 | 17 | 1 | 86.4805 | 18.2474 | 2018-03-18 17:00 | 17 | 1 | 86.9856 | 17.719 | 2018-03-18 17:00 | 17 | 1 | 0 | 0 | 2018-03-18 17:00 | 17 | 1 | 33.0545 | 6.9415
2018-03-18 18:00 | 18 | 1 | 86.4332 | 18.2374 | 2018-03-18 18:00 | 18 | 1 | 86.92 | 17.7056 | 2018-03-18 18:00 | 18 | 1 | 0 | 0 | 2018-03-18 18:00 | 18 | 1 | 33.0296 | 6.9362
2018-03-18 19:00 | 19 | 1 | 85.6794 | 18.0784 | 2018-03-18 19:00 | 19 | 1 | 85.9266 | 17.5032 | 2018-03-18 19:00 | 19 | 1 | 0 | 0 | 2018-03-18 19:00 | 19 | 1 | 32.6521 | 6.8569
2018-03-18 20:00 | 20 | 1 | 86.3294 | 18.2155 | 2018-03-18 20:00 | 20 | 1 | 86.5888 | 17.6381 | 2018-03-18 20:00 | 20 | 1 | 0 | 0 | 2018-03-18 20:00 | 20 | 1 | 32.9037 | 6.9098
2018-03-18 21:00 | 21 | 1 | 86.3569 | 18.2213 | 2018-03-18 21:00 | 21 | 1 | 86.6728 | 17.6552 | 2018-03-18 21:00 | 21 | 1 | 0 | 0 | 2018-03-18 21:00 | 21 | 1 | 32.9357 | 6.9165
2018-03-18 22:00 | 22 | 1 | 86.4881 | 18.249 | 2018-03-18 22:00 | 22 | 1 | 86.8086 | 17.6829 | 2018-03-18 22:00 | 22 | 1 | 0 | 0 | 2018-03-18 22:00 | 22 | 1 | 32.9873 | 6.9273
2018-03-18 23:00 | 23 | 1 | 86.4332 | 18.2374 | 2018-03-18 23:00 | 23 | 1 | 86.7353 | 17.668 | 2018-03-18 23:00 | 23 | 1 | 0 | 0 | 2018-03-18 23:00 | 23 | 1 | 32.9594 | 6.9215
2018-03-19 | 0 | 2 | 86.4088 | 18.2323 | 2018-03-19 | 0 | 2 | 86.7002 | 17.6608 | 2018-03-19 | 0 | 2 | 86.9352 | 18.4303 | 2018-03-19 | 0 | 2 | 65.9815 | 13.8561
2018-03-19 01:00 | 1 | 2 | 86.0426 | 18.155 | 2018-03-19 01:00 | 1 | 2 | 86.3127 | 17.5819 | 2018-03-19 01:00 | 1 | 2 | 86.5278 | 18.3439 | 2018-03-19 01:00 | 1 | 2 | 65.6794 | 13.7927
2018-03-19 02:00 | 2 | 2 | 86.392 | 18.2287 | 2018-03-19 02:00 | 2 | 2 | 86.6392 | 17.6484 | 2018-03-19 02:00 | 2 | 2 | 86.8421 | 18.4105 | 2018-03-19 02:00 | 2 | 2 | 65.9229 | 13.8438
2018-03-19 03:00 | 3 | 2 | 86.2776 | 18.2046 | 2018-03-19 03:00 | 3 | 2 | 86.5766 | 17.6357 | 2018-03-19 03:00 | 3 | 2 | 86.7536 | 18.3918 | 2018-03-19 03:00 | 3 | 2 | 65.8655 | 13.8317
2018-03-19 04:00 | 4 | 2 | 86.5034 | 18.2522 | 2018-03-19 04:00 | 4 | 2 | 86.8849 | 17.6985 | 2018-03-19 04:00 | 4 | 2 | 87.0283 | 18.45 | 2018-03-19 04:00 | 4 | 2 | 66.087 | 13.8783
2018-03-19 05:00 | 5 | 2 | 86.3661 | 18.2232 | 2018-03-19 05:00 | 5 | 2 | 86.772 | 17.6755 | 2018-03-19 05:00 | 5 | 2 | 87.0054 | 18.4451 | 2018-03-19 05:00 | 5 | 2 | 66.0354 | 13.8674
2018-03-19 06:00 | 6 | 2 | 86.2898 | 18.2071 | 2018-03-19 06:00 | 6 | 2 | 86.6499 | 17.6506 | 2018-03-19 06:00 | 6 | 2 | 86.8147 | 18.4047 | 2018-03-19 06:00 | 6 | 2 | 65.9165 | 13.8425
2018-03-19 07:00 | 7 | 2 | 86.2043 | 18.1891 | 2018-03-19 07:00 | 7 | 2 | 86.5278 | 17.6257 | 2018-03-19 07:00 | 7 | 2 | 86.7079 | 18.3821 | 2018-03-19 07:00 | 7 | 2 | 65.8296 | 13.8242
2018-03-19 08:00 | 8 | 2 | 86.3355 | 18.2168 | 2018-03-19 08:00 | 8 | 2 | 86.5461 | 17.6294 | 2018-03-19 08:00 | 8 | 2 | 86.8025 | 18.4021 | 2018-03-19 08:00 | 8 | 2 | 65.8725 | 13.8332
2018-03-19 09:00 | 9 | 2 | 86.3798 | 18.2261 | 2018-03-19 09:00 | 9 | 2 | 86.7262 | 17.6661 | 2018-03-19 09:00 | 9 | 2 | 86.8711 | 18.4167 | 2018-03-19 09:00 | 9 | 2 | 65.967 | 13.8531
2018-03-19 10:00 | 10 | 2 | 86.2272 | 18.1939 | 2018-03-19 10:00 | 10 | 2 | 86.5156 | 17.6232 | 2018-03-19 10:00 | 10 | 2 | 86.714 | 18.3834 | 2018-03-19 10:00 | 10 | 2 | 65.8272 | 13.8237
2018-03-19 11:00 | 11 | 2 | 86.2119 | 18.1907 | 2018-03-19 11:00 | 11 | 2 | 86.5141 | 17.6229 | 2018-03-19 11:00 | 11 | 2 | 86.7201 | 18.3847 | 2018-03-19 11:00 | 11 | 2 | 65.829 | 13.8241
2018-03-19 12:00 | 12 | 2 | 86.389 | 18.2281 | 2018-03-19 12:00 | 12 | 2 | 86.6835 | 17.6574 | 2018-03-19 12:00 | 12 | 2 | 86.8574 | 18.4138 | 2018-03-19 12:00 | 12 | 2 | 65.9455 | 13.8486
2018-03-19 13:00 | 13 | 2 | 86.4027 | 18.231 | 2018-03-19 13:00 | 13 | 2 | 86.6224 | 17.645 | 2018-03-19 13:00 | 13 | 2 | 86.7475 | 18.3905 | 2018-03-19 13:00 | 13 | 2 | 65.8806 | 13.8349
2018-03-19 14:00 | 14 | 2 | 86.3783 | 18.2258 | 2018-03-19 14:00 | 14 | 2 | 86.6606 | 17.6528 | 2018-03-19 14:00 | 14 | 2 | 86.7903 | 18.3995 | 2018-03-19 14:00 | 14 | 2 | 65.9113 | 13.8414
2018-03-19 15:00 | 15 | 2 | 86.3355 | 18.2168 | 2018-03-19 15:00 | 15 | 2 | 86.5248 | 17.6251 | 2018-03-19 15:00 | 15 | 2 | 86.7384 | 18.3885 | 2018-03-19 15:00 | 15 | 2 | 65.84 | 13.8264
2018-03-19 16:00 | 16 | 2 | 86.3493 | 18.2197 | 2018-03-19 16:00 | 16 | 2 | 86.4912 | 17.6183 | 2018-03-19 16:00 | 16 | 2 | 86.685 | 18.3772 | 2018-03-19 16:00 | 16 | 2 | 65.807 | 13.8195
2018-03-19 17:00 | 17 | 2 | 86.244 | 18.1975 | 2018-03-19 17:00 | 17 | 2 | 86.4683 | 17.6136 | 2018-03-19 17:00 | 17 | 2 | 86.6743 | 18.375 | 2018-03-19 17:00 | 17 | 2 | 65.7942 | 13.8168
2018-03-19 18:00 | 18 | 2 | 86.3142 | 18.2123 | 2018-03-19 18:00 | 18 | 2 | 86.4378 | 17.6074 | 2018-03-19 18:00 | 18 | 2 | 86.5934 | 18.3578 | 2018-03-19 18:00 | 18 | 2 | 65.7519 | 13.8079
2018-03-19 19:00 | 19 | 2 | 86.2089 | 18.1901 | 2018-03-19 19:00 | 19 | 2 | 86.3508 | 17.5897 | 2018-03-19 19:00 | 19 | 2 | 86.5583 | 18.3504 | 2018-03-19 19:00 | 19 | 2 | 65.7055 | 13.7981
2018-03-19 20:00 | 20 | 2 | 86.2181 | 18.192 | 2018-03-19 20:00 | 20 | 2 | 86.4836 | 17.6167 | 2018-03-19 20:00 | 20 | 2 | 86.6896 | 18.3782 | 2018-03-19 20:00 | 20 | 2 | 65.8058 | 13.8192
2018-03-19 21:00 | 21 | 2 | 86.1494 | 18.1775 | 2018-03-19 21:00 | 21 | 2 | 86.4759 | 17.6151 | 2018-03-19 21:00 | 21 | 2 | 86.63 | 18.3656 | 2018-03-19 21:00 | 21 | 2 | 65.7802 | 13.8139
2018-03-19 22:00 | 22 | 2 | 86.2593 | 18.2007 | 2018-03-19 22:00 | 22 | 2 | 86.5522 | 17.6307 | 2018-03-19 22:00 | 22 | 2 | 86.6468 | 18.3691 | 2018-03-19 22:00 | 22 | 2 | 65.8156 | 13.8213
2018-03-19 23:00 | 23 | 2 | 86.4424 | 18.2393 | 2018-03-19 23:00 | 23 | 2 | 86.8055 | 17.6823 | 2018-03-19 23:00 | 23 | 2 | 86.8864 | 18.4199 | 2018-03-19 23:00 | 23 | 2 | 66.0029 | 13.8606
2018-03-20 | 0 | 3 | 86.4637 | 18.2438 | 2018-03-20 | 0 | 3 | 0 | 0 | 2018-03-20 | 0 | 3 | 0 | 0 | 2018-03-20 | 0 | 3 | 0 | 0
2018-03-20 01:00 | 1 | 3 | 86.5629 | 18.2648 | 2018-03-20 01:00 | 1 | 3 | 0 | 0 | 2018-03-20 01:00 | 1 | 3 | 0 | 0 | 2018-03-20 01:00 | 1 | 3 | 0 | 0
2018-03-20 02:00 | 2 | 3 | 86.3706 | 18.2242 | 2018-03-20 02:00 | 2 | 3 | 0 | 0 | 2018-03-20 02:00 | 2 | 3 | 0 | 0 | 2018-03-20 02:00 | 2 | 3 | 0 | 0
2018-03-20 03:00 | 3 | 3 | 86.3523 | 18.2203 | 2018-03-20 03:00 | 3 | 3 | 0 | 0 | 2018-03-20 03:00 | 3 | 3 | 0 | 0 | 2018-03-20 03:00 | 3 | 3 | 0 | 0
2018-03-20 04:00 | 4 | 3 | 86.3676 | 18.2236 | 2018-03-20 04:00 | 4 | 3 | 0 | 0 | 2018-03-20 04:00 | 4 | 3 | 0 | 0 | 2018-03-20 04:00 | 4 | 3 | 0 | 0
2018-03-20 05:00 | 5 | 3 | 86.4027 | 18.231 | 2018-03-20 05:00 | 5 | 3 | 0 | 0 | 2018-03-20 05:00 | 5 | 3 | 0 | 0 | 2018-03-20 05:00 | 5 | 3 | 0 | 0
2018-03-20 06:00 | 6 | 3 | 86.4652 | 18.2442 | 2018-03-20 06:00 | 6 | 3 | 0 | 0 | 2018-03-20 06:00 | 6 | 3 | 0 | 0 | 2018-03-20 06:00 | 6 | 3 | 0 | 0
2018-03-20 07:00 | 7 | 3 | 86.4012 | 18.2307 | 2018-03-20 07:00 | 7 | 3 | 0 | 0 | 2018-03-20 07:00 | 7 | 3 | 0 | 0 | 2018-03-20 07:00 | 7 | 3 | 0 | 0
2018-03-20 08:00 | 8 | 3 | 86.4515 | 18.2413 | 2018-03-20 08:00 | 8 | 3 | 0 | 0 | 2018-03-20 08:00 | 8 | 3 | 0 | 0 | 2018-03-20 08:00 | 8 | 3 | 0 | 0
2018-03-20 09:00 | 9 | 3 | 86.2028 | 18.1888 | 2018-03-20 09:00 | 9 | 3 | 0 | 0 | 2018-03-20 09:00 | 9 | 3 | 0 | 0 | 2018-03-20 09:00 | 9 | 3 | 0 | 0
2018-03-20 10:00 | 10 | 3 | 86.2715 | 18.2033 | 2018-03-20 10:00 | 10 | 3 | 0 | 0 | 2018-03-20 10:00 | 10 | 3 | 0 | 0 | 2018-03-20 10:00 | 10 | 3 | 0 | 0
2018-03-20 11:00 | 11 | 3 | 86.7567 | 18.3057 | 2018-03-20 11:00 | 11 | 3 | 0 | 0 | 2018-03-20 11:00 | 11 | 3 | 0 | 0 | 2018-03-20 11:00 | 11 | 3 | 0 | 0
2018-03-20 12:00 | 12 | 3 | 86.6194 | 18.2767 | 2018-03-20 12:00 | 12 | 3 | 0 | 0 | 2018-03-20 12:00 | 12 | 3 | 0 | 0 | 2018-03-20 12:00 | 12 | 3 | 0 | 0
2018-03-20 13:00 | 13 | 3 | 86.6377 | 18.2806 | 2018-03-20 13:00 | 13 | 3 | 0 | 0 | 2018-03-20 13:00 | 13 | 3 | 0 | 0 | 2018-03-20 13:00 | 13 | 3 | 0 | 0
2018-03-20 14:00 | 14 | 3 | 86.8757 | 18.3308 | 2018-03-20 14:00 | 14 | 3 | 0 | 0 | 2018-03-20 14:00 | 14 | 3 | 0 | 0 | 2018-03-20 14:00 | 14 | 3 | 0 | 0
2018-03-20 15:00 | 15 | 3 | 86.7994 | 18.3147 | 2018-03-20 15:00 | 15 | 3 | 0 | 0 | 2018-03-20 15:00 | 15 | 3 | 0 | 0 | 2018-03-20 15:00 | 15 | 3 | 0 | 0
2018-03-20 16:00 | 16 | 3 | 86.7674 | 18.3079 | 2018-03-20 16:00 | 16 | 3 | 0 | 0 | 2018-03-20 16:00 | 16 | 3 | 0 | 0 | 2018-03-20 16:00 | 16 | 3 | 0 | 0
2018-03-20 17:00 | 17 | 3 | 86.7384 | 18.3018 | 2018-03-20 17:00 | 17 | 3 | 0 | 0 | 2018-03-20 17:00 | 17 | 3 | 0 | 0 | 2018-03-20 17:00 | 17 | 3 | 0 | 0
2018-03-20 18:00 | 18 | 3 | 86.7124 | 18.2963 | 2018-03-20 18:00 | 18 | 3 | 0 | 0 | 2018-03-20 18:00 | 18 | 3 | 0 | 0 | 2018-03-20 18:00 | 18 | 3 | 0 | 0
2018-03-20 19:00 | 19 | 3 | 86.8376 | 18.3227 | 2018-03-20 19:00 | 19 | 3 | 0 | 0 | 2018-03-20 19:00 | 19 | 3 | 0 | 0 | 2018-03-20 19:00 | 19 | 3 | 0 | 0
2018-03-20 20:00 | 20 | 3 | 86.627 | 18.2783 | 2018-03-20 20:00 | 20 | 3 | 0 | 0 | 2018-03-20 20:00 | 20 | 3 | 0 | 0 | 2018-03-20 20:00 | 20 | 3 | 0 | 0
2018-03-20 21:00 | 21 | 3 | 86.6239 | 18.2776 | 2018-03-20 21:00 | 21 | 3 | 0 | 0 | 2018-03-20 21:00 | 21 | 3 | 0 | 0 | 2018-03-20 21:00 | 21 | 3 | 0 | 0
2018-03-20 22:00 | 22 | 3 | 86.714 | 18.2967 | 2018-03-20 22:00 | 22 | 3 | 0 | 0 | 2018-03-20 22:00 | 22 | 3 | 0 | 0 | 2018-03-20 22:00 | 22 | 3 | 0 | 0
2018-03-20 23:00 | 23 | 3 | 86.8971 | 18.3353 | 2018-03-20 23:00 | 23 | 3 | 0 | 0 | 2018-03-20 23:00 | 23 | 3 | 0 | 0 | 2018-03-20 23:00 | 23 | 3 | 0 | 0
2018-03-21 | 0 | 4 | 0 | 0 | 2018-03-21 | 0 | 4 | 0 | 0 | 2018-03-21 | 0 | 4 | 86.6712 | 18.3743 | 2018-03-21 | 0 | 4 | 32.9351 | 6.9164
2018-03-21 01:00 | 1 | 4 | 0 | 0 | 2018-03-21 01:00 | 1 | 4 | 0 | 0 | 2018-03-21 01:00 | 1 | 4 | 86.511 | 18.3403 | 2018-03-21 01:00 | 1 | 4 | 32.8742 | 6.9036
2018-03-21 02:00 | 2 | 4 | 0 | 0 | 2018-03-21 02:00 | 2 | 4 | 0 | 0 | 2018-03-21 02:00 | 2 | 4 | 86.7628 | 18.3937 | 2018-03-21 02:00 | 2 | 4 | 32.9699 | 6.9237
2018-03-21 03:00 | 3 | 4 | 0 | 0 | 2018-03-21 03:00 | 3 | 4 | 0 | 0 | 2018-03-21 03:00 | 3 | 4 | 86.7384 | 18.3885 | 2018-03-21 03:00 | 3 | 4 | 32.9606 | 6.9217
2018-03-21 04:00 | 4 | 4 | 0 | 0 | 2018-03-21 04:00 | 4 | 4 | 0 | 0 | 2018-03-21 04:00 | 4 | 4 | 86.8376 | 18.4096 | 2018-03-21 04:00 | 4 | 4 | 32.9983 | 6.9296
2018-03-21 05:00 | 5 | 4 | 0 | 0 | 2018-03-21 05:00 | 5 | 4 | 0 | 0 | 2018-03-21 05:00 | 5 | 4 | 87.0222 | 18.4487 | 2018-03-21 05:00 | 5 | 4 | 33.0684 | 6.9444
2018-03-21 06:00 | 6 | 4 | 0 | 0 | 2018-03-21 06:00 | 6 | 4 | 0 | 0 | 2018-03-21 06:00 | 6 | 4 | 86.9627 | 18.4361 | 2018-03-21 06:00 | 6 | 4 | 33.0458 | 6.9396
2018-03-21 07:00 | 7 | 4 | 0 | 0 | 2018-03-21 07:00 | 7 | 4 | 0 | 0 | 2018-03-21 07:00 | 7 | 4 | 87.1321 | 18.472 | 2018-03-21 07:00 | 7 | 4 | 33.1102 | 6.9531
2018-03-21 08:00 | 8 | 4 | 0 | 0 | 2018-03-21 08:00 | 8 | 4 | 0 | 0 | 2018-03-21 08:00 | 8 | 4 | 87.1931 | 18.4849 | 2018-03-21 08:00 | 8 | 4 | 33.1334 | 6.958
2018-03-21 09:00 | 9 | 4 | 0 | 0 | 2018-03-21 09:00 | 9 | 4 | 0 | 0 | 2018-03-21 09:00 | 9 | 4 | 86.7155 | 18.3837 | 2018-03-21 09:00 | 9 | 4 | 32.9519 | 6.9199
2018-03-21 10:00 | 10 | 4 | 0 | 0 | 2018-03-21 10:00 | 10 | 4 | 0 | 0 | 2018-03-21 10:00 | 10 | 4 | 86.6743 | 18.375 | 2018-03-21 10:00 | 10 | 4 | 32.9362 | 6.9166
2018-03-21 11:00 | 11 | 4 | 0 | 0 | 2018-03-21 11:00 | 11 | 4 | 0 | 0 | 2018-03-21 11:00 | 11 | 4 | 86.8956 | 18.4219 | 2018-03-21 11:00 | 11 | 4 | 33.0203 | 6.9343
2018-03-21 12:00 | 12 | 4 | 0 | 0 | 2018-03-21 12:00 | 12 | 4 | 0 | 0 | 2018-03-21 12:00 | 12 | 4 | 86.9276 | 18.4287 | 2018-03-21 12:00 | 12 | 4 | 33.0325 | 6.9368
2018-03-21 13:00 | 13 | 4 | 0 | 0 | 2018-03-21 13:00 | 13 | 4 | 0 | 0 | 2018-03-21 13:00 | 13 | 4 | 87.2541 | 18.4979 | 2018-03-21 13:00 | 13 | 4 | 33.1566 | 6.9629
2018-03-21 14:00 | 14 | 4 | 0 | 0 | 2018-03-21 14:00 | 14 | 4 | 0 | 0 | 2018-03-21 14:00 | 14 | 4 | 87.4037 | 18.5296 | 2018-03-21 14:00 | 14 | 4 | 33.2134 | 6.9748
2018-03-21 15:00 | 15 | 4 | 0 | 0 | 2018-03-21 15:00 | 15 | 4 | 0 | 0 | 2018-03-21 15:00 | 15 | 4 | 87.2129 | 18.4891 | 2018-03-21 15:00 | 15 | 4 | 33.1409 | 6.9596
2018-03-21 16:00 | 16 | 4 | 0 | 0 | 2018-03-21 16:00 | 16 | 4 | 0 | 0 | 2018-03-21 16:00 | 16 | 4 | 86.9718 | 18.438 | 2018-03-21 16:00 | 16 | 4 | 33.0493 | 6.9403
2018-03-21 17:00 | 17 | 4 | 0 | 0 | 2018-03-21 17:00 | 17 | 4 | 0 | 0 | 2018-03-21 17:00 | 17 | 4 | 87.1397 | 18.4736 | 2018-03-21 17:00 | 17 | 4 | 33.1131 | 6.9537
2018-03-21 18:00 | 18 | 4 | 0 | 0 | 2018-03-21 18:00 | 18 | 4 | 0 | 0 | 2018-03-21 18:00 | 18 | 4 | 87.2435 | 18.4956 | 2018-03-21 18:00 | 18 | 4 | 33.1525 | 6.962
2018-03-21 19:00 | 19 | 4 | 0 | 0 | 2018-03-21 19:00 | 19 | 4 | 0 | 0 | 2018-03-21 19:00 | 19 | 4 | 86.8894 | 18.4206 | 2018-03-21 19:00 | 19 | 4 | 33.018 | 6.9338
2018-03-21 20:00 | 20 | 4 | 0 | 0 | 2018-03-21 20:00 | 20 | 4 | 0 | 0 | 2018-03-21 20:00 | 20 | 4 | 87.1839 | 18.483 | 2018-03-21 20:00 | 20 | 4 | 33.1299 | 6.9573
2018-03-21 21:00 | 21 | 4 | 0 | 0 | 2018-03-21 21:00 | 21 | 4 | 0 | 0 | 2018-03-21 21:00 | 21 | 4 | 87.2419 | 18.4953 | 2018-03-21 21:00 | 21 | 4 | 33.1519 | 6.9619
2018-03-21 22:00 | 22 | 4 | 0 | 0 | 2018-03-21 22:00 | 22 | 4 | 0 | 0 | 2018-03-21 22:00 | 22 | 4 | 87.1733 | 18.4807 | 2018-03-21 22:00 | 22 | 4 | 33.1259 | 6.9564
2018-03-21 23:00 | 23 | 4 | 0 | 0 | 2018-03-21 23:00 | 23 | 4 | 0 | 0 | 2018-03-21 23:00 | 23 | 4 | 87.2557 | 18.4982 | 2018-03-21 23:00 | 23 | 4 | 33.1572 | 6.963
2018-03-22 | 0 | 5 | 86.5492 | 18.2619 | 2018-03-22 | 0 | 5 | 0 | 0 | 2018-03-22 | 0 | 5 | 0 | 0 | 2018-03-22 | 0 | 5 | 0 | 0
2018-03-22 01:00 | 1 | 5 | 86.7201 | 18.2979 | 2018-03-22 01:00 | 1 | 5 | 0 | 0 | 2018-03-22 01:00 | 1 | 5 | 0 | 0 | 2018-03-22 01:00 | 1 | 5 | 0 | 0
2018-03-22 02:00 | 2 | 5 | 86.5095 | 18.2535 | 2018-03-22 02:00 | 2 | 5 | 0 | 0 | 2018-03-22 02:00 | 2 | 5 | 0 | 0 | 2018-03-22 02:00 | 2 | 5 | 0 | 0
2018-03-22 03:00 | 3 | 5 | 86.4576 | 18.2426 | 2018-03-22 03:00 | 3 | 5 | 0 | 0 | 2018-03-22 03:00 | 3 | 5 | 0 | 0 | 2018-03-22 03:00 | 3 | 5 | 0 | 0
2018-03-22 04:00 | 4 | 5 | 86.6316 | 18.2793 | 2018-03-22 04:00 | 4 | 5 | 0 | 0 | 2018-03-22 04:00 | 4 | 5 | 0 | 0 | 2018-03-22 04:00 | 4 | 5 | 0 | 0
2018-03-22 05:00 | 5 | 5 | 86.569 | 18.2661 | 2018-03-22 05:00 | 5 | 5 | 0 | 0 | 2018-03-22 05:00 | 5 | 5 | 0 | 0 | 2018-03-22 05:00 | 5 | 5 | 0 | 0
2018-03-22 06:00 | 6 | 5 | 86.6468 | 18.2825 | 2018-03-22 06:00 | 6 | 5 | 0 | 0 | 2018-03-22 06:00 | 6 | 5 | 0 | 0 | 2018-03-22 06:00 | 6 | 5 | 0 | 0
2018-03-22 07:00 | 7 | 5 | 86.6361 | 18.2802 | 2018-03-22 07:00 | 7 | 5 | 0 | 0 | 2018-03-22 07:00 | 7 | 5 | 0 | 0 | 2018-03-22 07:00 | 7 | 5 | 0 | 0
2018-03-22 08:00 | 8 | 5 | 86.6819 | 18.2899 | 2018-03-22 08:00 | 8 | 5 | 0 | 0 | 2018-03-22 08:00 | 8 | 5 | 0 | 0 | 2018-03-22 08:00 | 8 | 5 | 0 | 0
2018-03-22 09:00 | 9 | 5 | 86.7094 | 18.2957 | 2018-03-22 09:00 | 9 | 5 | 0 | 0 | 2018-03-22 09:00 | 9 | 5 | 0 | 0 | 2018-03-22 09:00 | 9 | 5 | 0 | 0
2018-03-22 10:00 | 10 | 5 | 86.7933 | 18.3134 | 2018-03-22 10:00 | 10 | 5 | 0 | 0 | 2018-03-22 10:00 | 10 | 5 | 0 | 0 | 2018-03-22 10:00 | 10 | 5 | 0 | 0
2018-03-22 11:00 | 11 | 5 | 86.8009 | 18.315 | 2018-03-22 11:00 | 11 | 5 | 0 | 0 | 2018-03-22 11:00 | 11 | 5 | 0 | 0 | 2018-03-22 11:00 | 11 | 5 | 0 | 0
2018-03-22 12:00 | 12 | 5 | 86.6728 | 18.288 | 2018-03-22 12:00 | 12 | 5 | 0 | 0 | 2018-03-22 12:00 | 12 | 5 | 0 | 0 | 2018-03-22 12:00 | 12 | 5 | 0 | 0
2018-03-22 13:00 | 13 | 5 | 86.6316 | 18.2793 | 2018-03-22 13:00 | 13 | 5 | 0 | 0 | 2018-03-22 13:00 | 13 | 5 | 0 | 0 | 2018-03-22 13:00 | 13 | 5 | 0 | 0
2018-03-22 14:00 | 14 | 5 | 86.6316 | 18.2793 | 2018-03-22 14:00 | 14 | 5 | 0 | 0 | 2018-03-22 14:00 | 14 | 5 | 0 | 0 | 2018-03-22 14:00 | 14 | 5 | 0 | 0
2018-03-22 15:00 | 15 | 5 | 86.6636 | 18.286 | 2018-03-22 15:00 | 15 | 5 | 0 | 0 | 2018-03-22 15:00 | 15 | 5 | 0 | 0 | 2018-03-22 15:00 | 15 | 5 | 0 | 0
2018-03-22 16:00 | 16 | 5 | 86.5568 | 18.2635 | 2018-03-22 16:00 | 16 | 5 | 0 | 0 | 2018-03-22 16:00 | 16 | 5 | 0 | 0 | 2018-03-22 16:00 | 16 | 5 | 0 | 0
2018-03-22 17:00 | 17 | 5 | 86.6865 | 18.2909 | 2018-03-22 17:00 | 17 | 5 | 0 | 0 | 2018-03-22 17:00 | 17 | 5 | 0 | 0 | 2018-03-22 17:00 | 17 | 5 | 0 | 0
2018-03-22 18:00 | 18 | 5 | 86.7262 | 18.2992 | 2018-03-22 18:00 | 18 | 5 | 0 | 0 | 2018-03-22 18:00 | 18 | 5 | 0 | 0 | 2018-03-22 18:00 | 18 | 5 | 0 | 0
2018-03-22 19:00 | 19 | 5 | 86.5187 | 18.2554 | 2018-03-22 19:00 | 19 | 5 | 0 | 0 | 2018-03-22 19:00 | 19 | 5 | 0 | 0 | 2018-03-22 19:00 | 19 | 5 | 0 | 0
2018-03-22 20:00 | 20 | 5 | 86.5766 | 18.2677 | 2018-03-22 20:00 | 20 | 5 | 0 | 0 | 2018-03-22 20:00 | 20 | 5 | 0 | 0 | 2018-03-22 20:00 | 20 | 5 | 0 | 0
2018-03-22 21:00 | 21 | 5 | 86.6194 | 18.2767 | 2018-03-22 21:00 | 21 | 5 | 0 | 0 | 2018-03-22 21:00 | 21 | 5 | 0 | 0 | 2018-03-22 21:00 | 21 | 5 | 0 | 0
2018-03-22 22:00 | 22 | 5 | 86.6743 | 18.2883 | 2018-03-22 22:00 | 22 | 5 | 0 | 0 | 2018-03-22 22:00 | 22 | 5 | 0 | 0 | 2018-03-22 22:00 | 22 | 5 | 0 | 0
2018-03-22 23:00 | 23 | 5 | 86.5644 | 18.2651 | 2018-03-22 23:00 | 23 | 5 | 0 | 0 | 2018-03-22 23:00 | 23 | 5 | 0 | 0 | 2018-03-22 23:00 | 23 | 5 | 0 | 0
2018-03-23 | 0 | 6 | 86.2226 | 18.193 | 2018-03-23 | 0 | 6 | 86.688 | 17.6583 | 2018-03-23 | 0 | 6 | 0 | 0 | 2018-03-23 | 0 | 6 | 32.9414 | 6.9177
2018-03-23 01:00 | 1 | 6 | 86.1128 | 18.1698 | 2018-03-23 01:00 | 1 | 6 | 86.5232 | 17.6248 | 2018-03-23 01:00 | 1 | 6 | 0 | 0 | 2018-03-23 01:00 | 1 | 6 | 32.8788 | 6.9046
2018-03-23 02:00 | 2 | 6 | 86.2791 | 18.2049 | 2018-03-23 02:00 | 2 | 6 | 86.6896 | 17.6587 | 2018-03-23 02:00 | 2 | 6 | 0 | 0 | 2018-03-23 02:00 | 2 | 6 | 32.942 | 6.9178
2018-03-23 03:00 | 3 | 6 | 86.0014 | 18.1463 | 2018-03-23 03:00 | 3 | 6 | 86.4485 | 17.6096 | 2018-03-23 03:00 | 3 | 6 | 0 | 0 | 2018-03-23 03:00 | 3 | 6 | 32.8504 | 6.8986
2018-03-23 04:00 | 4 | 6 | 86.0533 | 18.1572 | 2018-03-23 04:00 | 4 | 6 | 86.4347 | 17.6067 | 2018-03-23 04:00 | 4 | 6 | 0 | 0 | 2018-03-23 04:00 | 4 | 6 | 32.8452 | 6.8975
2018-03-23 05:00 | 5 | 6 | 86.2257 | 18.1936 | 2018-03-23 05:00 | 5 | 6 | 86.6117 | 17.6428 | 2018-03-23 05:00 | 5 | 6 | 0 | 0 | 2018-03-23 05:00 | 5 | 6 | 32.9124 | 6.9116
2018-03-23 06:00 | 6 | 6 | 86.4332 | 18.2374 | 2018-03-23 06:00 | 6 | 6 | 86.9352 | 17.7087 | 2018-03-23 06:00 | 6 | 6 | 0 | 0 | 2018-03-23 06:00 | 6 | 6 | 33.0354 | 6.9374
2018-03-23 07:00 | 7 | 6 | 86.5873 | 18.2699 | 2018-03-23 07:00 | 7 | 6 | 87.0619 | 17.7345 | 2018-03-23 07:00 | 7 | 6 | 0 | 0 | 2018-03-23 07:00 | 7 | 6 | 33.0835 | 6.9475
2018-03-23 08:00 | 8 | 6 | 86.3691 | 18.2239 | 2018-03-23 08:00 | 8 | 6 | 86.7811 | 17.6773 | 2018-03-23 08:00 | 8 | 6 | 0 | 0 | 2018-03-23 08:00 | 8 | 6 | 32.9768 | 6.9251
2018-03-23 09:00 | 9 | 6 | 86.334 | 18.2165 | 2018-03-23 09:00 | 9 | 6 | 86.7399 | 17.6689 | 2018-03-23 09:00 | 9 | 6 | 0 | 0 | 2018-03-23 09:00 | 9 | 6 | 32.9612 | 6.9218
2018-03-23 10:00 | 10 | 6 | 86.5126 | 18.2542 | 2018-03-23 10:00 | 10 | 6 | 86.862 | 17.6938 | 2018-03-23 10:00 | 10 | 6 | 0 | 0 | 2018-03-23 10:00 | 10 | 6 | 33.0076 | 6.9316
2018-03-23 11:00 | 11 | 6 | 86.5003 | 18.2516 | 2018-03-23 11:00 | 11 | 6 | 86.9306 | 17.7078 | 2018-03-23 11:00 | 11 | 6 | 0 | 0 | 2018-03-23 11:00 | 11 | 6 | 33.0336 | 6.9371
2018-03-23 12:00 | 12 | 6 | 86.7002 | 18.2937 | 2018-03-23 12:00 | 12 | 6 | 87.1412 | 17.7507 | 2018-03-23 12:00 | 12 | 6 | 0 | 0 | 2018-03-23 12:00 | 12 | 6 | 33.1137 | 6.9539
2018-03-23 13:00 | 13 | 6 | 86.363 | 18.2226 | 2018-03-23 13:00 | 13 | 6 | 86.8009 | 17.6813 | 2018-03-23 13:00 | 13 | 6 | 0 | 0 | 2018-03-23 13:00 | 13 | 6 | 32.9843 | 6.9267
2018-03-23 14:00 | 14 | 6 | 86.4408 | 18.239 | 2018-03-23 14:00 | 14 | 6 | 86.8635 | 17.6941 | 2018-03-23 14:00 | 14 | 6 | 0 | 0 | 2018-03-23 14:00 | 14 | 6 | 33.0081 | 6.9317
2018-03-23 15:00 | 15 | 6 | 86.2943 | 18.2081 | 2018-03-23 15:00 | 15 | 6 | 86.6743 | 17.6556 | 2018-03-23 15:00 | 15 | 6 | 0 | 0 | 2018-03-23 15:00 | 15 | 6 | 32.9362 | 6.9166
2018-03-23 16:00 | 16 | 6 | 86.3706 | 18.2242 | 2018-03-23 16:00 | 16 | 6 | 86.7491 | 17.6708 | 2018-03-23 16:00 | 16 | 6 | 0 | 0 | 2018-03-23 16:00 | 16 | 6 | 32.9647 | 6.9226
2018-03-23 17:00 | 17 | 6 | 86.2882 | 18.2068 | 2018-03-23 17:00 | 17 | 6 | 86.7445 | 17.6699 | 2018-03-23 17:00 | 17 | 6 | 0 | 0 | 2018-03-23 17:00 | 17 | 6 | 32.9629 | 6.9222
2018-03-23 18:00 | 18 | 6 | 86.1875 | 18.1856 | 2018-03-23 18:00 | 18 | 6 | 86.6667 | 17.654 | 2018-03-23 18:00 | 18 | 6 | 0 | 0 | 2018-03-23 18:00 | 18 | 6 | 32.9333 | 6.916
2018-03-23 19:00 | 19 | 6 | 86.099 | 18.1669 | 2018-03-23 19:00 | 19 | 6 | 86.5431 | 17.6288 | 2018-03-23 19:00 | 19 | 6 | 0 | 0 | 2018-03-23 19:00 | 19 | 6 | 32.8864 | 6.9061
2018-03-23 20:00 | 20 | 6 | 86.1997 | 18.1881 | 2018-03-23 20:00 | 20 | 6 | 86.5187 | 17.6239 | 2018-03-23 20:00 | 20 | 6 | 0 | 0 | 2018-03-23 20:00 | 20 | 6 | 32.8771 | 6.9042
2018-03-23 21:00 | 21 | 6 | 86.3767 | 18.2255 | 2018-03-23 21:00 | 21 | 6 | 86.7247 | 17.6658 | 2018-03-23 21:00 | 21 | 6 | 0 | 0 | 2018-03-23 21:00 | 21 | 6 | 32.9554 | 6.9206
2018-03-23 22:00 | 22 | 6 | 86.3691 | 18.2239 | 2018-03-23 22:00 | 22 | 6 | 86.7659 | 17.6742 | 2018-03-23 22:00 | 22 | 6 | 0 | 0 | 2018-03-23 22:00 | 22 | 6 | 32.971 | 6.9239
2018-03-23 23:00 | 23 | 6 | 86.4012 | 18.2307 | 2018-03-23 23:00 | 23 | 6 | 86.7918 | 17.6795 | 2018-03-23 23:00 | 23 | 6 | 0 | 0 | 2018-03-23 23:00 | 23 | 6 | 32.9809 | 6.926
2018-03-24 | 0 | 7 | 86.0121 | 18.1486 | 2018-03-24 | 0 | 7 | 0 | 0 | 2018-03-24 | 0 | 7 | 86.5507 | 18.3487 | 2018-03-24 | 0 | 7 | 32.8893 | 6.9067
2018-03-24 01:00 | 1 | 7 | 85.919 | 18.1289 | 2018-03-24 01:00 | 1 | 7 | 0 | 0 | 2018-03-24 01:00 | 1 | 7 | 86.5324 | 18.3449 | 2018-03-24 01:00 | 1 | 7 | 32.8823 | 6.9053
2018-03-24 02:00 | 2 | 7 | 86.0533 | 18.1572 | 2018-03-24 02:00 | 2 | 7 | 0 | 0 | 2018-03-24 02:00 | 2 | 7 | 86.6453 | 18.3688 | 2018-03-24 02:00 | 2 | 7 | 32.9252 | 6.9143
2018-03-24 03:00 | 3 | 7 | 86.1677 | 18.1814 | 2018-03-24 03:00 | 3 | 7 | 0 | 0 | 2018-03-24 03:00 | 3 | 7 | 86.7002 | 18.3804 | 2018-03-24 03:00 | 3 | 7 | 32.9461 | 6.9187
2018-03-24 04:00 | 4 | 7 | 86.3081 | 18.211 | 2018-03-24 04:00 | 4 | 7 | 0 | 0 | 2018-03-24 04:00 | 4 | 7 | 86.8513 | 18.4125 | 2018-03-24 04:00 | 4 | 7 | 33.0035 | 6.9307
2018-03-24 05:00 | 5 | 7 | 86.2562 | 18.2001 | 2018-03-24 05:00 | 5 | 7 | 0 | 0 | 2018-03-24 05:00 | 5 | 7 | 86.8605 | 18.4144 | 2018-03-24 05:00 | 5 | 7 | 33.007 | 6.9315
2018-03-24 06:00 | 6 | 7 | 86.1234 | 18.172 | 2018-03-24 06:00 | 6 | 7 | 0 | 0 | 2018-03-24 06:00 | 6 | 7 | 86.6682 | 18.3737 | 2018-03-24 06:00 | 6 | 7 | 32.9339 | 6.9161
2018-03-24 07:00 | 7 | 7 | 86.1906 | 18.1862 | 2018-03-24 07:00 | 7 | 7 | 0 | 0 | 2018-03-24 07:00 | 7 | 7 | 86.7247 | 18.3856 | 2018-03-24 07:00 | 7 | 7 | 32.9554 | 6.9206
2018-03-24 08:00 | 8 | 7 | 86.36 | 18.222 | 2018-03-24 08:00 | 8 | 7 | 0 | 0 | 2018-03-24 08:00 | 8 | 7 | 86.952 | 18.4338 | 2018-03-24 08:00 | 8 | 7 | 33.0418 | 6.9388
2018-03-24 09:00 | 9 | 7 | 86.4912 | 18.2496 | 2018-03-24 09:00 | 9 | 7 | 0 | 0 | 2018-03-24 09:00 | 9 | 7 | 87.0588 | 18.4565 | 2018-03-24 09:00 | 9 | 7 | 33.0823 | 6.9473
2018-03-24 10:00 | 10 | 7 | 86.1982 | 18.1878 | 2018-03-24 10:00 | 10 | 7 | 0 | 0 | 2018-03-24 10:00 | 10 | 7 | 86.6392 | 18.3675 | 2018-03-24 10:00 | 10 | 7 | 32.9229 | 6.9138
2018-03-24 11:00 | 11 | 7 | 86.1707 | 18.182 | 2018-03-24 11:00 | 11 | 7 | 0 | 0 | 2018-03-24 11:00 | 11 | 7 | 86.8849 | 18.4196 | 2018-03-24 11:00 | 11 | 7 | 33.0163 | 6.9334
2018-03-24 12:00 | 12 | 7 | 86.5019 | 18.2519 | 2018-03-24 12:00 | 12 | 7 | 0 | 0 | 2018-03-24 12:00 | 12 | 7 | 87.1504 | 18.4759 | 2018-03-24 12:00 | 12 | 7 | 33.1172 | 6.9546
2018-03-24 13:00 | 13 | 7 | 86.6148 | 18.2757 | 2018-03-24 13:00 | 13 | 7 | 0 | 0 | 2018-03-24 13:00 | 13 | 7 | 87.3167 | 18.5111 | 2018-03-24 13:00 | 13 | 7 | 33.1803 | 6.9679
2018-03-24 14:00 | 14 | 7 | 86.4439 | 18.2397 | 2018-03-24 14:00 | 14 | 7 | 0 | 0 | 2018-03-24 14:00 | 14 | 7 | 87.0832 | 18.4616 | 2018-03-24 14:00 | 14 | 7 | 33.0916 | 6.9492
2018-03-24 15:00 | 15 | 7 | 86.5522 | 18.2625 | 2018-03-24 15:00 | 15 | 7 | 0 | 0 | 2018-03-24 15:00 | 15 | 7 | 87.2938 | 18.5063 | 2018-03-24 15:00 | 15 | 7 | 33.1716 | 6.966
2018-03-24 16:00 | 16 | 7 | 86.5644 | 18.2651 | 2018-03-24 16:00 | 16 | 7 | 0 | 0 | 2018-03-24 16:00 | 16 | 7 | 87.3579 | 18.5199 | 2018-03-24 16:00 | 16 | 7 | 33.196 | 6.9712
2018-03-24 17:00 | 17 | 7 | 86.7445 | 18.3031 | 2018-03-24 17:00 | 17 | 7 | 0 | 0 | 2018-03-24 17:00 | 17 | 7 | 87.57 | 18.5648 | 2018-03-24 17:00 | 17 | 7 | 33.2766 | 6.9881
2018-03-24 18:00 | 18 | 7 | 86.4668 | 18.2445 | 2018-03-24 18:00 | 18 | 7 | 0 | 0 | 2018-03-24 18:00 | 18 | 7 | 87.3014 | 18.5079 | 2018-03-24 18:00 | 18 | 7 | 33.1745 | 6.9667
2018-03-24 19:00 | 19 | 7 | 86.3661 | 18.2232 | 2018-03-24 19:00 | 19 | 7 | 0 | 0 | 2018-03-24 19:00 | 19 | 7 | 87.0954 | 18.4642 | 2018-03-24 19:00 | 19 | 7 | 33.0963 | 6.9502
2018-03-24 20:00 | 20 | 7 | 86.1173 | 18.1708 | 2018-03-24 20:00 | 20 | 7 | 0 | 0 | 2018-03-24 20:00 | 20 | 7 | 86.891 | 18.4209 | 2018-03-24 20:00 | 20 | 7 | 33.0186 | 6.9339
2018-03-24 21:00 | 21 | 7 | 86.1555 | 18.1788 | 2018-03-24 21:00 | 21 | 7 | 0 | 0 | 2018-03-24 21:00 | 21 | 7 | 86.9245 | 18.428 | 2018-03-24 21:00 | 21 | 7 | 33.0313 | 6.9366
2018-03-24 22:00 | 22 | 7 | 86.2211 | 18.1927 | 2018-03-24 22:00 | 22 | 7 | 0 | 0 | 2018-03-24 22:00 | 22 | 7 | 87.0054 | 18.4451 | 2018-03-24 22:00 | 22 | 7 | 33.0621 | 6.943
2018-03-24 23:00 | 23 | 7 | 86.2226 | 18.193 | 2018-03-24 23:00 | 23 | 7 | 0 | 0 | 2018-03-24 23:00 | 23 | 7 | 87.0787 | 18.4607 | 2018-03-24 23:00 | 23 | 7 | 33.0899 | 6.9489
2018-03-25 | 0 | 1 | 86.2364 | 18.1959 | 2018-03-25 | 0 | 1 | 86.7994 | 17.681 | 2018-03-25 | 0 | 1 | 0 | 0 | 2018-03-25 | 0 | 1 | 32.9838 | 6.9266
2018-03-25 01:00 | 1 | 1 | 86.3188 | 18.2133 | 2018-03-25 01:00 | 1 | 1 | 86.952 | 17.7121 | 2018-03-25 01:00 | 1 | 1 | 0 | 0 | 2018-03-25 01:00 | 1 | 1 | 33.0418 | 6.9388
2018-03-25 02:00 | 2 | 1 | 86.2119 | 18.1907 | 2018-03-25 02:00 | 2 | 1 | 86.8177 | 17.6848 | 2018-03-25 02:00 | 2 | 1 | 0 | 0 | 2018-03-25 02:00 | 2 | 1 | 32.9907 | 6.9281
2018-03-25 03:00 | 3 | 1 | 86.1845 | 18.1849 | 2018-03-25 03:00 | 3 | 1 | 86.7857 | 17.6782 | 2018-03-25 03:00 | 3 | 1 | 0 | 0 | 2018-03-25 03:00 | 3 | 1 | 32.9786 | 6.9255
2018-03-25 04:00 | 4 | 1 | 86.2455 | 18.1978 | 2018-03-25 04:00 | 4 | 1 | 86.833 | 17.6879 | 2018-03-25 04:00 | 4 | 1 | 0 | 0 | 2018-03-25 04:00 | 4 | 1 | 32.9965 | 6.9293
2018-03-25 05:00 | 5 | 1 | 86.2333 | 18.1952 | 2018-03-25 05:00 | 5 | 1 | 86.833 | 17.6879 | 2018-03-25 05:00 | 5 | 1 | 0 | 0 | 2018-03-25 05:00 | 5 | 1 | 32.9965 | 6.9293
2018-03-25 06:00 | 6 | 1 | 86.2776 | 18.2046 | 2018-03-25 06:00 | 6 | 1 | 86.8528 | 17.6919 | 2018-03-25 06:00 | 6 | 1 | 0 | 0 | 2018-03-25 06:00 | 6 | 1 | 33.0041 | 6.9309
2018-03-25 07:00 | 7 | 1 | 86.2867 | 18.2065 | 2018-03-25 07:00 | 7 | 1 | 86.8452 | 17.6904 | 2018-03-25 07:00 | 7 | 1 | 0 | 0 | 2018-03-25 07:00 | 7 | 1 | 33.0012 | 6.9302
2018-03-25 08:00 | 8 | 1 | 86.2989 | 18.2091 | 2018-03-25 08:00 | 8 | 1 | 86.9032 | 17.7022 | 2018-03-25 08:00 | 8 | 1 | 0 | 0 | 2018-03-25 08:00 | 8 | 1 | 33.0232 | 6.9349
2018-03-25 09:00 | 9 | 1 | 86.2867 | 18.2065 | 2018-03-25 09:00 | 9 | 1 | 86.8162 | 17.6845 | 2018-03-25 09:00 | 9 | 1 | 0 | 0 | 2018-03-25 09:00 | 9 | 1 | 32.9902 | 6.9279
2018-03-25 10:00 | 10 | 1 | 86.2882 | 18.2068 | 2018-03-25 10:00 | 10 | 1 | 86.8528 | 17.6919 | 2018-03-25 10:00 | 10 | 1 | 0 | 0 | 2018-03-25 10:00 | 10 | 1 | 33.0041 | 6.9309
2018-03-25 11:00 | 11 | 1 | 86.1845 | 18.1849 | 2018-03-25 11:00 | 11 | 1 | 86.743 | 17.6695 | 2018-03-25 11:00 | 11 | 1 | 0 | 0 | 2018-03-25 11:00 | 11 | 1 | 32.9623 | 6.9221
2018-03-25 12:00 | 12 | 1 | 86.1418 | 18.1759 | 2018-03-25 12:00 | 12 | 1 | 86.714 | 17.6636 | 2018-03-25 12:00 | 12 | 1 | 0 | 0 | 2018-03-25 12:00 | 12 | 1 | 32.9513 | 6.9198
2018-03-25 13:00 | 13 | 1 | 86.1479 | 18.1772 | 2018-03-25 13:00 | 13 | 1 | 86.7659 | 17.6742 | 2018-03-25 13:00 | 13 | 1 | 0 | 0 | 2018-03-25 13:00 | 13 | 1 | 32.971 | 6.9239
2018-03-25 14:00 | 14 | 1 | 86.1112 | 18.1695 | 2018-03-25 14:00 | 14 | 1 | 86.7018 | 17.6612 | 2018-03-25 14:00 | 14 | 1 | 0 | 0 | 2018-03-25 14:00 | 14 | 1 | 32.9467 | 6.9188
2018-03-25 15:00 | 15 | 1 | 86.2455 | 18.1978 | 2018-03-25 15:00 | 15 | 1 | 86.8482 | 17.691 | 2018-03-25 15:00 | 15 | 1 | 0 | 0 | 2018-03-25 15:00 | 15 | 1 | 33.0023 | 6.9305
2018-03-25 16:00 | 16 | 1 | 86.3447 | 18.2187 | 2018-03-25 16:00 | 16 | 1 | 86.9398 | 17.7096 | 2018-03-25 16:00 | 16 | 1 | 0 | 0 | 2018-03-25 16:00 | 16 | 1 | 33.0371 | 6.9378
2018-03-25 17:00 | 17 | 1 | 86.4805 | 18.2474 | 2018-03-25 17:00 | 17 | 1 | 86.9856 | 17.719 | 2018-03-25 17:00 | 17 | 1 | 0 | 0 | 2018-03-25 17:00 | 17 | 1 | 33.0545 | 6.9415
2018-03-25 18:00 | 18 | 1 | 86.4332 | 18.2374 | 2018-03-25 18:00 | 18 | 1 | 86.92 | 17.7056 | 2018-03-25 18:00 | 18 | 1 | 0 | 0 | 2018-03-25 18:00 | 18 | 1 | 33.0296 | 6.9362
2018-03-25 19:00 | 19 | 1 | 85.6794 | 18.0784 | 2018-03-25 19:00 | 19 | 1 | 85.9266 | 17.5032 | 2018-03-25 19:00 | 19 | 1 | 0 | 0 | 2018-03-25 19:00 | 19 | 1 | 32.6521 | 6.8569
2018-03-25 20:00 | 20 | 1 | 86.3294 | 18.2155 | 2018-03-25 20:00 | 20 | 1 | 86.5888 | 17.6381 | 2018-03-25 20:00 | 20 | 1 | 0 | 0 | 2018-03-25 20:00 | 20 | 1 | 32.9037 | 6.9098
2018-03-25 21:00 | 21 | 1 | 86.3569 | 18.2213 | 2018-03-25 21:00 | 21 | 1 | 86.6728 | 17.6552 | 2018-03-25 21:00 | 21 | 1 | 0 | 0 | 2018-03-25 21:00 | 21 | 1 | 32.9357 | 6.9165
2018-03-25 22:00 | 22 | 1 | 86.4881 | 18.249 | 2018-03-25 22:00 | 22 | 1 | 86.8086 | 17.6829 | 2018-03-25 22:00 | 22 | 1 | 0 | 0 | 2018-03-25 22:00 | 22 | 1 | 32.9873 | 6.9273
2018-03-25 23:00 | 23 | 1 | 86.4332 | 18.2374 | 2018-03-25 23:00 | 23 | 1 | 86.7353 | 17.668 | 2018-03-25 23:00 | 23 | 1 | 0 | 0 | 2018-03-25 23:00 | 23 | 1 | 32.9594 | 6.9215
2018-03-26 | 0 | 2 | 86.4088 | 18.2323 | 2018-03-26 | 0 | 2 | 86.7002 | 17.6608 | 2018-03-26 | 0 | 2 | 86.9352 | 18.4303 | 2018-03-26 | 0 | 2 | 65.9815 | 13.8561
2018-03-26 01:00 | 1 | 2 | 86.0426 | 18.155 | 2018-03-26 01:00 | 1 | 2 | 86.3127 | 17.5819 | 2018-03-26 01:00 | 1 | 2 | 86.5278 | 18.3439 | 2018-03-26 01:00 | 1 | 2 | 65.6794 | 13.7927
2018-03-26 02:00 | 2 | 2 | 86.392 | 18.2287 | 2018-03-26 02:00 | 2 | 2 | 86.6392 | 17.6484 | 2018-03-26 02:00 | 2 | 2 | 86.8421 | 18.4105 | 2018-03-26 02:00 | 2 | 2 | 65.9229 | 13.8438
2018-03-26 03:00 | 3 | 2 | 86.2776 | 18.2046 | 2018-03-26 03:00 | 3 | 2 | 86.5766 | 17.6357 | 2018-03-26 03:00 | 3 | 2 | 86.7536 | 18.3918 | 2018-03-26 03:00 | 3 | 2 | 65.8655 | 13.8317
2018-03-26 04:00 | 4 | 2 | 86.5034 | 18.2522 | 2018-03-26 04:00 | 4 | 2 | 86.8849 | 17.6985 | 2018-03-26 04:00 | 4 | 2 | 87.0283 | 18.45 | 2018-03-26 04:00 | 4 | 2 | 66.087 | 13.8783
2018-03-26 05:00 | 5 | 2 | 86.3661 | 18.2232 | 2018-03-26 05:00 | 5 | 2 | 86.772 | 17.6755 | 2018-03-26 05:00 | 5 | 2 | 87.0054 | 18.4451 | 2018-03-26 05:00 | 5 | 2 | 66.0354 | 13.8674
2018-03-26 06:00 | 6 | 2 | 86.2898 | 18.2071 | 2018-03-26 06:00 | 6 | 2 | 86.6499 | 17.6506 | 2018-03-26 06:00 | 6 | 2 | 86.8147 | 18.4047 | 2018-03-26 06:00 | 6 | 2 | 65.9165 | 13.8425
2018-03-26 07:00 | 7 | 2 | 86.2043 | 18.1891 | 2018-03-26 07:00 | 7 | 2 | 86.5278 | 17.6257 | 2018-03-26 07:00 | 7 | 2 | 86.7079 | 18.3821 | 2018-03-26 07:00 | 7 | 2 | 65.8296 | 13.8242
2018-03-26 08:00 | 8 | 2 | 86.3355 | 18.2168 | 2018-03-26 08:00 | 8 | 2 | 86.5461 | 17.6294 | 2018-03-26 08:00 | 8 | 2 | 86.8025 | 18.4021 | 2018-03-26 08:00 | 8 | 2 | 65.8725 | 13.8332
2018-03-26 09:00 | 9 | 2 | 86.3798 | 18.2261 | 2018-03-26 09:00 | 9 | 2 | 86.7262 | 17.6661 | 2018-03-26 09:00 | 9 | 2 | 86.8711 | 18.4167 | 2018-03-26 09:00 | 9 | 2 | 65.967 | 13.8531
2018-03-26 10:00 | 10 | 2 | 86.2272 | 18.1939 | 2018-03-26 10:00 | 10 | 2 | 86.5156 | 17.6232 | 2018-03-26 10:00 | 10 | 2 | 86.714 | 18.3834 | 2018-03-26 10:00 | 10 | 2 | 65.8272 | 13.8237
2018-03-26 11:00 | 11 | 2 | 86.2119 | 18.1907 | 2018-03-26 11:00 | 11 | 2 | 86.5141 | 17.6229 | 2018-03-26 11:00 | 11 | 2 | 86.7201 | 18.3847 | 2018-03-26 11:00 | 11 | 2 | 65.829 | 13.8241
2018-03-26 12:00 | 12 | 2 | 86.389 | 18.2281 | 2018-03-26 12:00 | 12 | 2 | 86.6835 | 17.6574 | 2018-03-26 12:00 | 12 | 2 | 86.8574 | 18.4138 | 2018-03-26 12:00 | 12 | 2 | 65.9455 | 13.8486
2018-03-26 13:00 | 13 | 2 | 86.4027 | 18.231 | 2018-03-26 13:00 | 13 | 2 | 86.6224 | 17.645 | 2018-03-26 13:00 | 13 | 2 | 86.7475 | 18.3905 | 2018-03-26 13:00 | 13 | 2 | 65.8806 | 13.8349
2018-03-26 14:00 | 14 | 2 | 86.3783 | 18.2258 | 2018-03-26 14:00 | 14 | 2 | 86.6606 | 17.6528 | 2018-03-26 14:00 | 14 | 2 | 86.7903 | 18.3995 | 2018-03-26 14:00 | 14 | 2 | 65.9113 | 13.8414
2018-03-26 15:00 | 15 | 2 | 86.3355 | 18.2168 | 2018-03-26 15:00 | 15 | 2 | 86.5248 | 17.6251 | 2018-03-26 15:00 | 15 | 2 | 86.7384 | 18.3885 | 2018-03-26 15:00 | 15 | 2 | 65.84 | 13.8264
2018-03-26 16:00 | 16 | 2 | 86.3493 | 18.2197 | 2018-03-26 16:00 | 16 | 2 | 86.4912 | 17.6183 | 2018-03-26 16:00 | 16 | 2 | 86.685 | 18.3772 | 2018-03-26 16:00 | 16 | 2 | 65.807 | 13.8195
2018-03-26 17:00 | 17 | 2 | 86.244 | 18.1975 | 2018-03-26 17:00 | 17 | 2 | 86.4683 | 17.6136 | 2018-03-26 17:00 | 17 | 2 | 86.6743 | 18.375 | 2018-03-26 17:00 | 17 | 2 | 65.7942 | 13.8168
2018-03-26 18:00 | 18 | 2 | 86.3142 | 18.2123 | 2018-03-26 18:00 | 18 | 2 | 86.4378 | 17.6074 | 2018-03-26 18:00 | 18 | 2 | 86.5934 | 18.3578 | 2018-03-26 18:00 | 18 | 2 | 65.7519 | 13.8079
2018-03-26 19:00 | 19 | 2 | 86.2089 | 18.1901 | 2018-03-26 19:00 | 19 | 2 | 86.3508 | 17.5897 | 2018-03-26 19:00 | 19 | 2 | 86.5583 | 18.3504 | 2018-03-26 19:00 | 19 | 2 | 65.7055 | 13.7981
2018-03-26 20:00 | 20 | 2 | 86.2181 | 18.192 | 2018-03-26 20:00 | 20 | 2 | 86.4836 | 17.6167 | 2018-03-26 20:00 | 20 | 2 | 86.6896 | 18.3782 | 2018-03-26 20:00 | 20 | 2 | 65.8058 | 13.8192
2018-03-26 21:00 | 21 | 2 | 86.1494 | 18.1775 | 2018-03-26 21:00 | 21 | 2 | 86.4759 | 17.6151 | 2018-03-26 21:00 | 21 | 2 | 86.63 | 18.3656 | 2018-03-26 21:00 | 21 | 2 | 65.7802 | 13.8139
2018-03-26 22:00 | 22 | 2 | 86.2593 | 18.2007 | 2018-03-26 22:00 | 22 | 2 | 86.5522 | 17.6307 | 2018-03-26 22:00 | 22 | 2 | 86.6468 | 18.3691 | 2018-03-26 22:00 | 22 | 2 | 65.8156 | 13.8213
2018-03-26 23:00 | 23 | 2 | 86.4424 | 18.2393 | 2018-03-26 23:00 | 23 | 2 | 86.8055 | 17.6823 | 2018-03-26 23:00 | 23 | 2 | 86.8864 | 18.4199 | 2018-03-26 23:00 | 23 | 2 | 66.0029 | 13.8606
2018-03-27 | 0 | 3 | 86.4637 | 18.2438 | 2018-03-27 | 0 | 3 | 0 | 0 | 2018-03-27 | 0 | 3 | 0 | 0 | 2018-03-27 | 0 | 3 | 0 | 0
2018-03-27 01:00 | 1 | 3 | 86.5629 | 18.2648 | 2018-03-27 01:00 | 1 | 3 | 0 | 0 | 2018-03-27 01:00 | 1 | 3 | 0 | 0 | 2018-03-27 01:00 | 1 | 3 | 0 | 0
2018-03-27 02:00 | 2 | 3 | 86.3706 | 18.2242 | 2018-03-27 02:00 | 2 | 3 | 0 | 0 | 2018-03-27 02:00 | 2 | 3 | 0 | 0 | 2018-03-27 02:00 | 2 | 3 | 0 | 0
2018-03-27 03:00 | 3 | 3 | 86.3523 | 18.2203 | 2018-03-27 03:00 | 3 | 3 | 0 | 0 | 2018-03-27 03:00 | 3 | 3 | 0 | 0 | 2018-03-27 03:00 | 3 | 3 | 0 | 0
2018-03-27 04:00 | 4 | 3 | 86.3676 | 18.2236 | 2018-03-27 04:00 | 4 | 3 | 0 | 0 | 2018-03-27 04:00 | 4 | 3 | 0 | 0 | 2018-03-27 04:00 | 4 | 3 | 0 | 0
2018-03-27 05:00 | 5 | 3 | 86.4027 | 18.231 | 2018-03-27 05:00 | 5 | 3 | 0 | 0 | 2018-03-27 05:00 | 5 | 3 | 0 | 0 | 2018-03-27 05:00 | 5 | 3 | 0 | 0
2018-03-27 06:00 | 6 | 3 | 86.4652 | 18.2442 | 2018-03-27 06:00 | 6 | 3 | 0 | 0 | 2018-03-27 06:00 | 6 | 3 | 0 | 0 | 2018-03-27 06:00 | 6 | 3 | 0 | 0
2018-03-27 07:00 | 7 | 3 | 86.4012 | 18.2307 | 2018-03-27 07:00 | 7 | 3 | 0 | 0 | 2018-03-27 07:00 | 7 | 3 | 0 | 0 | 2018-03-27 07:00 | 7 | 3 | 0 | 0
2018-03-27 08:00 | 8 | 3 | 86.4515 | 18.2413 | 2018-03-27 08:00 | 8 | 3 | 0 | 0 | 2018-03-27 08:00 | 8 | 3 | 0 | 0 | 2018-03-27 08:00 | 8 | 3 | 0 | 0
2018-03-27 09:00 | 9 | 3 | 86.2028 | 18.1888 | 2018-03-27 09:00 | 9 | 3 | 0 | 0 | 2018-03-27 09:00 | 9 | 3 | 0 | 0 | 2018-03-27 09:00 | 9 | 3 | 0 | 0
2018-03-27 10:00 | 10 | 3 | 86.2715 | 18.2033 | 2018-03-27 10:00 | 10 | 3 | 0 | 0 | 2018-03-27 10:00 | 10 | 3 | 0 | 0 | 2018-03-27 10:00 | 10 | 3 | 0 | 0
2018-03-27 11:00 | 11 | 3 | 86.7567 | 18.3057 | 2018-03-27 11:00 | 11 | 3 | 0 | 0 | 2018-03-27 11:00 | 11 | 3 | 0 | 0 | 2018-03-27 11:00 | 11 | 3 | 0 | 0
2018-03-27 12:00 | 12 | 3 | 86.6194 | 18.2767 | 2018-03-27 12:00 | 12 | 3 | 0 | 0 | 2018-03-27 12:00 | 12 | 3 | 0 | 0 | 2018-03-27 12:00 | 12 | 3 | 0 | 0
2018-03-27 13:00 | 13 | 3 | 86.6377 | 18.2806 | 2018-03-27 13:00 | 13 | 3 | 0 | 0 | 2018-03-27 13:00 | 13 | 3 | 0 | 0 | 2018-03-27 13:00 | 13 | 3 | 0 | 0
2018-03-27 14:00 | 14 | 3 | 86.8757 | 18.3308 | 2018-03-27 14:00 | 14 | 3 | 0 | 0 | 2018-03-27 14:00 | 14 | 3 | 0 | 0 | 2018-03-27 14:00 | 14 | 3 | 0 | 0
2018-03-27 15:00 | 15 | 3 | 86.7994 | 18.3147 | 2018-03-27 15:00 | 15 | 3 | 0 | 0 | 2018-03-27 15:00 | 15 | 3 | 0 | 0 | 2018-03-27 15:00 | 15 | 3 | 0 | 0
2018-03-27 16:00 | 16 | 3 | 86.7674 | 18.3079 | 2018-03-27 16:00 | 16 | 3 | 0 | 0 | 2018-03-27 16:00 | 16 | 3 | 0 | 0 | 2018-03-27 16:00 | 16 | 3 | 0 | 0
2018-03-27 17:00 | 17 | 3 | 86.7384 | 18.3018 | 2018-03-27 17:00 | 17 | 3 | 0 | 0 | 2018-03-27 17:00 | 17 | 3 | 0 | 0 | 2018-03-27 17:00 | 17 | 3 | 0 | 0
2018-03-27 18:00 | 18 | 3 | 86.7124 | 18.2963 | 2018-03-27 18:00 | 18 | 3 | 0 | 0 | 2018-03-27 18:00 | 18 | 3 | 0 | 0 | 2018-03-27 18:00 | 18 | 3 | 0 | 0
2018-03-27 19:00 | 19 | 3 | 86.8376 | 18.3227 | 2018-03-27 19:00 | 19 | 3 | 0 | 0 | 2018-03-27 19:00 | 19 | 3 | 0 | 0 | 2018-03-27 19:00 | 19 | 3 | 0 | 0
2018-03-27 20:00 | 20 | 3 | 86.627 | 18.2783 | 2018-03-27 20:00 | 20 | 3 | 0 | 0 | 2018-03-27 20:00 | 20 | 3 | 0 | 0 | 2018-03-27 20:00 | 20 | 3 | 0 | 0
2018-03-27 21:00 | 21 | 3 | 86.6239 | 18.2776 | 2018-03-27 21:00 | 21 | 3 | 0 | 0 | 2018-03-27 21:00 | 21 | 3 | 0 | 0 | 2018-03-27 21:00 | 21 | 3 | 0 | 0
2018-03-27 22:00 | 22 | 3 | 86.714 | 18.2967 | 2018-03-27 22:00 | 22 | 3 | 0 | 0 | 2018-03-27 22:00 | 22 | 3 | 0 | 0 | 2018-03-27 22:00 | 22 | 3 | 0 | 0
2018-03-27 23:00 | 23 | 3 | 86.8971 | 18.3353 | 2018-03-27 23:00 | 23 | 3 | 0 | 0 | 2018-03-27 23:00 | 23 | 3 | 0 | 0 | 2018-03-27 23:00 | 23 | 3 | 0 | 0
2018-03-28 | 0 | 4 | 0 | 0 | 2018-03-28 | 0 | 4 | 0 | 0 | 2018-03-28 | 0 | 4 | 86.6712 | 18.3743 | 2018-03-28 | 0 | 4 | 32.9351 | 6.9164
2018-03-28 01:00 | 1 | 4 | 0 | 0 | 2018-03-28 01:00 | 1 | 4 | 0 | 0 | 2018-03-28 01:00 | 1 | 4 | 86.511 | 18.3403 | 2018-03-28 01:00 | 1 | 4 | 32.8742 | 6.9036
2018-03-28 02:00 | 2 | 4 | 0 | 0 | 2018-03-28 02:00 | 2 | 4 | 0 | 0 | 2018-03-28 02:00 | 2 | 4 | 86.7628 | 18.3937 | 2018-03-28 02:00 | 2 | 4 | 32.9699 | 6.9237
2018-03-28 03:00 | 3 | 4 | 0 | 0 | 2018-03-28 03:00 | 3 | 4 | 0 | 0 | 2018-03-28 03:00 | 3 | 4 | 86.7384 | 18.3885 | 2018-03-28 03:00 | 3 | 4 | 32.9606 | 6.9217
2018-03-28 04:00 | 4 | 4 | 0 | 0 | 2018-03-28 04:00 | 4 | 4 | 0 | 0 | 2018-03-28 04:00 | 4 | 4 | 86.8376 | 18.4096 | 2018-03-28 04:00 | 4 | 4 | 32.9983 | 6.9296
2018-03-28 05:00 | 5 | 4 | 0 | 0 | 2018-03-28 05:00 | 5 | 4 | 0 | 0 | 2018-03-28 05:00 | 5 | 4 | 87.0222 | 18.4487 | 2018-03-28 05:00 | 5 | 4 | 33.0684 | 6.9444
2018-03-28 06:00 | 6 | 4 | 0 | 0 | 2018-03-28 06:00 | 6 | 4 | 0 | 0 | 2018-03-28 06:00 | 6 | 4 | 86.9627 | 18.4361 | 2018-03-28 06:00 | 6 | 4 | 33.0458 | 6.9396
2018-03-28 07:00 | 7 | 4 | 0 | 0 | 2018-03-28 07:00 | 7 | 4 | 0 | 0 | 2018-03-28 07:00 | 7 | 4 | 87.1321 | 18.472 | 2018-03-28 07:00 | 7 | 4 | 33.1102 | 6.9531
2018-03-28 08:00 | 8 | 4 | 0 | 0 | 2018-03-28 08:00 | 8 | 4 | 0 | 0 | 2018-03-28 08:00 | 8 | 4 | 87.1931 | 18.4849 | 2018-03-28 08:00 | 8 | 4 | 33.1334 | 6.958
2018-03-28 09:00 | 9 | 4 | 0 | 0 | 2018-03-28 09:00 | 9 | 4 | 0 | 0 | 2018-03-28 09:00 | 9 | 4 | 86.7155 | 18.3837 | 2018-03-28 09:00 | 9 | 4 | 32.9519 | 6.9199
2018-03-28 10:00 | 10 | 4 | 0 | 0 | 2018-03-28 10:00 | 10 | 4 | 0 | 0 | 2018-03-28 10:00 | 10 | 4 | 86.6743 | 18.375 | 2018-03-28 10:00 | 10 | 4 | 32.9362 | 6.9166
2018-03-28 11:00 | 11 | 4 | 0 | 0 | 2018-03-28 11:00 | 11 | 4 | 0 | 0 | 2018-03-28 11:00 | 11 | 4 | 86.8956 | 18.4219 | 2018-03-28 11:00 | 11 | 4 | 33.0203 | 6.9343
2018-03-28 12:00 | 12 | 4 | 0 | 0 | 2018-03-28 12:00 | 12 | 4 | 0 | 0 | 2018-03-28 12:00 | 12 | 4 | 86.9276 | 18.4287 | 2018-03-28 12:00 | 12 | 4 | 33.0325 | 6.9368
2018-03-28 13:00 | 13 | 4 | 0 | 0 | 2018-03-28 13:00 | 13 | 4 | 0 | 0 | 2018-03-28 13:00 | 13 | 4 | 87.2541 | 18.4979 | 2018-03-28 13:00 | 13 | 4 | 33.1566 | 6.9629
2018-03-28 14:00 | 14 | 4 | 0 | 0 | 2018-03-28 14:00 | 14 | 4 | 0 | 0 | 2018-03-28 14:00 | 14 | 4 | 87.4037 | 18.5296 | 2018-03-28 14:00 | 14 | 4 | 33.2134 | 6.9748
2018-03-28 15:00 | 15 | 4 | 0 | 0 | 2018-03-28 15:00 | 15 | 4 | 0 | 0 | 2018-03-28 15:00 | 15 | 4 | 87.2129 | 18.4891 | 2018-03-28 15:00 | 15 | 4 | 33.1409 | 6.9596
2018-03-28 16:00 | 16 | 4 | 0 | 0 | 2018-03-28 16:00 | 16 | 4 | 0 | 0 | 2018-03-28 16:00 | 16 | 4 | 86.9718 | 18.438 | 2018-03-28 16:00 | 16 | 4 | 33.0493 | 6.9403
2018-03-28 17:00 | 17 | 4 | 0 | 0 | 2018-03-28 17:00 | 17 | 4 | 0 | 0 | 2018-03-28 17:00 | 17 | 4 | 87.1397 | 18.4736 | 2018-03-28 17:00 | 17 | 4 | 33.1131 | 6.9537
2018-03-28 18:00 | 18 | 4 | 0 | 0 | 2018-03-28 18:00 | 18 | 4 | 0 | 0 | 2018-03-28 18:00 | 18 | 4 | 87.2435 | 18.4956 | 2018-03-28 18:00 | 18 | 4 | 33.1525 | 6.962
2018-03-28 19:00 | 19 | 4 | 0 | 0 | 2018-03-28 19:00 | 19 | 4 | 0 | 0 | 2018-03-28 19:00 | 19 | 4 | 86.8894 | 18.4206 | 2018-03-28 19:00 | 19 | 4 | 33.018 | 6.9338
2018-03-28 20:00 | 20 | 4 | 0 | 0 | 2018-03-28 20:00 | 20 | 4 | 0 | 0 | 2018-03-28 20:00 | 20 | 4 | 87.1839 | 18.483 | 2018-03-28 20:00 | 20 | 4 | 33.1299 | 6.9573
2018-03-28 21:00 | 21 | 4 | 0 | 0 | 2018-03-28 21:00 | 21 | 4 | 0 | 0 | 2018-03-28 21:00 | 21 | 4 | 87.2419 | 18.4953 | 2018-03-28 21:00 | 21 | 4 | 33.1519 | 6.9619
2018-03-28 22:00 | 22 | 4 | 0 | 0 | 2018-03-28 22:00 | 22 | 4 | 0 | 0 | 2018-03-28 22:00 | 22 | 4 | 87.1733 | 18.4807 | 2018-03-28 22:00 | 22 | 4 | 33.1259 | 6.9564
2018-03-28 23:00 | 23 | 4 | 0 | 0 | 2018-03-28 23:00 | 23 | 4 | 0 | 0 | 2018-03-28 23:00 | 23 | 4 | 87.2557 | 18.4982 | 2018-03-28 23:00 | 23 | 4 | 33.1572 | 6.963
2018-03-29 | 0 | 5 | 86.5492 | 18.2619 | 2018-03-29 | 0 | 5 | 0 | 0 | 2018-03-29 | 0 | 5 | 0 | 0 | 2018-03-29 | 0 | 5 | 0 | 0
2018-03-29 01:00 | 1 | 5 | 86.7201 | 18.2979 | 2018-03-29 01:00 | 1 | 5 | 0 | 0 | 2018-03-29 01:00 | 1 | 5 | 0 | 0 | 2018-03-29 01:00 | 1 | 5 | 0 | 0
2018-03-29 02:00 | 2 | 5 | 86.5095 | 18.2535 | 2018-03-29 02:00 | 2 | 5 | 0 | 0 | 2018-03-29 02:00 | 2 | 5 | 0 | 0 | 2018-03-29 02:00 | 2 | 5 | 0 | 0
2018-03-29 03:00 | 3 | 5 | 86.4576 | 18.2426 | 2018-03-29 03:00 | 3 | 5 | 0 | 0 | 2018-03-29 03:00 | 3 | 5 | 0 | 0 | 2018-03-29 03:00 | 3 | 5 | 0 | 0
2018-03-29 04:00 | 4 | 5 | 86.6316 | 18.2793 | 2018-03-29 04:00 | 4 | 5 | 0 | 0 | 2018-03-29 04:00 | 4 | 5 | 0 | 0 | 2018-03-29 04:00 | 4 | 5 | 0 | 0
2018-03-29 05:00 | 5 | 5 | 86.569 | 18.2661 | 2018-03-29 05:00 | 5 | 5 | 0 | 0 | 2018-03-29 05:00 | 5 | 5 | 0 | 0 | 2018-03-29 05:00 | 5 | 5 | 0 | 0
2018-03-29 06:00 | 6 | 5 | 86.6468 | 18.2825 | 2018-03-29 06:00 | 6 | 5 | 0 | 0 | 2018-03-29 06:00 | 6 | 5 | 0 | 0 | 2018-03-29 06:00 | 6 | 5 | 0 | 0
2018-03-29 07:00 | 7 | 5 | 86.6361 | 18.2802 | 2018-03-29 07:00 | 7 | 5 | 0 | 0 | 2018-03-29 07:00 | 7 | 5 | 0 | 0 | 2018-03-29 07:00 | 7 | 5 | 0 | 0
2018-03-29 08:00 | 8 | 5 | 86.6819 | 18.2899 | 2018-03-29 08:00 | 8 | 5 | 0 | 0 | 2018-03-29 08:00 | 8 | 5 | 0 | 0 | 2018-03-29 08:00 | 8 | 5 | 0 | 0
2018-03-29 09:00 | 9 | 5 | 86.7094 | 18.2957 | 2018-03-29 09:00 | 9 | 5 | 0 | 0 | 2018-03-29 09:00 | 9 | 5 | 0 | 0 | 2018-03-29 09:00 | 9 | 5 | 0 | 0
2018-03-29 10:00 | 10 | 5 | 86.7933 | 18.3134 | 2018-03-29 10:00 | 10 | 5 | 0 | 0 | 2018-03-29 10:00 | 10 | 5 | 0 | 0 | 2018-03-29 10:00 | 10 | 5 | 0 | 0
2018-03-29 11:00 | 11 | 5 | 86.8009 | 18.315 | 2018-03-29 11:00 | 11 | 5 | 0 | 0 | 2018-03-29 11:00 | 11 | 5 | 0 | 0 | 2018-03-29 11:00 | 11 | 5 | 0 | 0
2018-03-29 12:00 | 12 | 5 | 86.6728 | 18.288 | 2018-03-29 12:00 | 12 | 5 | 0 | 0 | 2018-03-29 12:00 | 12 | 5 | 0 | 0 | 2018-03-29 12:00 | 12 | 5 | 0 | 0
2018-03-29 13:00 | 13 | 5 | 86.6316 | 18.2793 | 2018-03-29 13:00 | 13 | 5 | 0 | 0 | 2018-03-29 13:00 | 13 | 5 | 0 | 0 | 2018-03-29 13:00 | 13 | 5 | 0 | 0
2018-03-29 14:00 | 14 | 5 | 86.6316 | 18.2793 | 2018-03-29 14:00 | 14 | 5 | 0 | 0 | 2018-03-29 14:00 | 14 | 5 | 0 | 0 | 2018-03-29 14:00 | 14 | 5 | 0 | 0
2018-03-29 15:00 | 15 | 5 | 86.6636 | 18.286 | 2018-03-29 15:00 | 15 | 5 | 0 | 0 | 2018-03-29 15:00 | 15 | 5 | 0 | 0 | 2018-03-29 15:00 | 15 | 5 | 0 | 0
2018-03-29 16:00 | 16 | 5 | 86.5568 | 18.2635 | 2018-03-29 16:00 | 16 | 5 | 0 | 0 | 2018-03-29 16:00 | 16 | 5 | 0 | 0 | 2018-03-29 16:00 | 16 | 5 | 0 | 0
2018-03-29 17:00 | 17 | 5 | 86.6865 | 18.2909 | 2018-03-29 17:00 | 17 | 5 | 0 | 0 | 2018-03-29 17:00 | 17 | 5 | 0 | 0 | 2018-03-29 17:00 | 17 | 5 | 0 | 0
2018-03-29 18:00 | 18 | 5 | 86.7262 | 18.2992 | 2018-03-29 18:00 | 18 | 5 | 0 | 0 | 2018-03-29 18:00 | 18 | 5 | 0 | 0 | 2018-03-29 18:00 | 18 | 5 | 0 | 0
2018-03-29 19:00 | 19 | 5 | 86.5187 | 18.2554 | 2018-03-29 19:00 | 19 | 5 | 0 | 0 | 2018-03-29 19:00 | 19 | 5 | 0 | 0 | 2018-03-29 19:00 | 19 | 5 | 0 | 0
2018-03-29 20:00 | 20 | 5 | 86.5766 | 18.2677 | 2018-03-29 20:00 | 20 | 5 | 0 | 0 | 2018-03-29 20:00 | 20 | 5 | 0 | 0 | 2018-03-29 20:00 | 20 | 5 | 0 | 0
2018-03-29 21:00 | 21 | 5 | 86.6194 | 18.2767 | 2018-03-29 21:00 | 21 | 5 | 0 | 0 | 2018-03-29 21:00 | 21 | 5 | 0 | 0 | 2018-03-29 21:00 | 21 | 5 | 0 | 0
2018-03-29 22:00 | 22 | 5 | 86.6743 | 18.2883 | 2018-03-29 22:00 | 22 | 5 | 0 | 0 | 2018-03-29 22:00 | 22 | 5 | 0 | 0 | 2018-03-29 22:00 | 22 | 5 | 0 | 0
2018-03-29 23:00 | 23 | 5 | 86.5644 | 18.2651 | 2018-03-29 23:00 | 23 | 5 | 0 | 0 | 2018-03-29 23:00 | 23 | 5 | 0 | 0 | 2018-03-29 23:00 | 23 | 5 | 0 | 0
2018-03-30 | 0 | 6 | 86.2226 | 18.193 | 2018-03-30 | 0 | 6 | 86.688 | 17.6583 | 2018-03-30 | 0 | 6 | 0 | 0 | 2018-03-30 | 0 | 6 | 32.9414 | 6.9177
2018-03-30 01:00 | 1 | 6 | 86.1128 | 18.1698 | 2018-03-30 01:00 | 1 | 6 | 86.5232 | 17.6248 | 2018-03-30 01:00 | 1 | 6 | 0 | 0 | 2018-03-30 01:00 | 1 | 6 | 32.8788 | 6.9046
2018-03-30 02:00 | 2 | 6 | 86.2791 | 18.2049 | 2018-03-30 02:00 | 2 | 6 | 86.6896 | 17.6587 | 2018-03-30 02:00 | 2 | 6 | 0 | 0 | 2018-03-30 02:00 | 2 | 6 | 32.942 | 6.9178
2018-03-30 03:00 | 3 | 6 | 86.0014 | 18.1463 | 2018-03-30 03:00 | 3 | 6 | 86.4485 | 17.6096 | 2018-03-30 03:00 | 3 | 6 | 0 | 0 | 2018-03-30 03:00 | 3 | 6 | 32.8504 | 6.8986
2018-03-30 04:00 | 4 | 6 | 86.0533 | 18.1572 | 2018-03-30 04:00 | 4 | 6 | 86.4347 | 17.6067 | 2018-03-30 04:00 | 4 | 6 | 0 | 0 | 2018-03-30 04:00 | 4 | 6 | 32.8452 | 6.8975
2018-03-30 05:00 | 5 | 6 | 86.2257 | 18.1936 | 2018-03-30 05:00 | 5 | 6 | 86.6117 | 17.6428 | 2018-03-30 05:00 | 5 | 6 | 0 | 0 | 2018-03-30 05:00 | 5 | 6 | 32.9124 | 6.9116
2018-03-30 06:00 | 6 | 6 | 86.4332 | 18.2374 | 2018-03-30 06:00 | 6 | 6 | 86.9352 | 17.7087 | 2018-03-30 06:00 | 6 | 6 | 0 | 0 | 2018-03-30 06:00 | 6 | 6 | 33.0354 | 6.9374
2018-03-30 07:00 | 7 | 6 | 86.5873 | 18.2699 | 2018-03-30 07:00 | 7 | 6 | 87.0619 | 17.7345 | 2018-03-30 07:00 | 7 | 6 | 0 | 0 | 2018-03-30 07:00 | 7 | 6 | 33.0835 | 6.9475
2018-03-30 08:00 | 8 | 6 | 86.3691 | 18.2239 | 2018-03-30 08:00 | 8 | 6 | 86.7811 | 17.6773 | 2018-03-30 08:00 | 8 | 6 | 0 | 0 | 2018-03-30 08:00 | 8 | 6 | 32.9768 | 6.9251
2018-03-30 09:00 | 9 | 6 | 86.334 | 18.2165 | 2018-03-30 09:00 | 9 | 6 | 86.7399 | 17.6689 | 2018-03-30 09:00 | 9 | 6 | 0 | 0 | 2018-03-30 09:00 | 9 | 6 | 32.9612 | 6.9218
2018-03-30 10:00 | 10 | 6 | 86.5126 | 18.2542 | 2018-03-30 10:00 | 10 | 6 | 86.862 | 17.6938 | 2018-03-30 10:00 | 10 | 6 | 0 | 0 | 2018-03-30 10:00 | 10 | 6 | 33.0076 | 6.9316
2018-03-30 11:00 | 11 | 6 | 86.5003 | 18.2516 | 2018-03-30 11:00 | 11 | 6 | 86.9306 | 17.7078 | 2018-03-30 11:00 | 11 | 6 | 0 | 0 | 2018-03-30 11:00 | 11 | 6 | 33.0336 | 6.9371
2018-03-30 12:00 | 12 | 6 | 86.7002 | 18.2937 | 2018-03-30 12:00 | 12 | 6 | 87.1412 | 17.7507 | 2018-03-30 12:00 | 12 | 6 | 0 | 0 | 2018-03-30 12:00 | 12 | 6 | 33.1137 | 6.9539
2018-03-30 13:00 | 13 | 6 | 86.363 | 18.2226 | 2018-03-30 13:00 | 13 | 6 | 86.8009 | 17.6813 | 2018-03-30 13:00 | 13 | 6 | 0 | 0 | 2018-03-30 13:00 | 13 | 6 | 32.9843 | 6.9267
2018-03-30 14:00 | 14 | 6 | 86.4408 | 18.239 | 2018-03-30 14:00 | 14 | 6 | 86.8635 | 17.6941 | 2018-03-30 14:00 | 14 | 6 | 0 | 0 | 2018-03-30 14:00 | 14 | 6 | 33.0081 | 6.9317
2018-03-30 15:00 | 15 | 6 | 86.2943 | 18.2081 | 2018-03-30 15:00 | 15 | 6 | 86.6743 | 17.6556 | 2018-03-30 15:00 | 15 | 6 | 0 | 0 | 2018-03-30 15:00 | 15 | 6 | 32.9362 | 6.9166
2018-03-30 16:00 | 16 | 6 | 86.3706 | 18.2242 | 2018-03-30 16:00 | 16 | 6 | 86.7491 | 17.6708 | 2018-03-30 16:00 | 16 | 6 | 0 | 0 | 2018-03-30 16:00 | 16 | 6 | 32.9647 | 6.9226
2018-03-30 17:00 | 17 | 6 | 86.2882 | 18.2068 | 2018-03-30 17:00 | 17 | 6 | 86.7445 | 17.6699 | 2018-03-30 17:00 | 17 | 6 | 0 | 0 | 2018-03-30 17:00 | 17 | 6 | 32.9629 | 6.9222
2018-03-30 18:00 | 18 | 6 | 86.1875 | 18.1856 | 2018-03-30 18:00 | 18 | 6 | 86.6667 | 17.654 | 2018-03-30 18:00 | 18 | 6 | 0 | 0 | 2018-03-30 18:00 | 18 | 6 | 32.9333 | 6.916
2018-03-30 19:00 | 19 | 6 | 86.099 | 18.1669 | 2018-03-30 19:00 | 19 | 6 | 86.5431 | 17.6288 | 2018-03-30 19:00 | 19 | 6 | 0 | 0 | 2018-03-30 19:00 | 19 | 6 | 32.8864 | 6.9061
2018-03-30 20:00 | 20 | 6 | 86.1997 | 18.1881 | 2018-03-30 20:00 | 20 | 6 | 86.5187 | 17.6239 | 2018-03-30 20:00 | 20 | 6 | 0 | 0 | 2018-03-30 20:00 | 20 | 6 | 32.8771 | 6.9042
2018-03-30 21:00 | 21 | 6 | 86.3767 | 18.2255 | 2018-03-30 21:00 | 21 | 6 | 86.7247 | 17.6658 | 2018-03-30 21:00 | 21 | 6 | 0 | 0 | 2018-03-30 21:00 | 21 | 6 | 32.9554 | 6.9206
2018-03-30 22:00 | 22 | 6 | 86.3691 | 18.2239 | 2018-03-30 22:00 | 22 | 6 | 86.7659 | 17.6742 | 2018-03-30 22:00 | 22 | 6 | 0 | 0 | 2018-03-30 22:00 | 22 | 6 | 32.971 | 6.9239
2018-03-30 23:00 | 23 | 6 | 86.4012 | 18.2307 | 2018-03-30 23:00 | 23 | 6 | 86.7918 | 17.6795 | 2018-03-30 23:00 | 23 | 6 | 0 | 0 | 2018-03-30 23:00 | 23 | 6 | 32.9809 | 6.926
2018-03-31 | 0 | 7 | 86.0121 | 18.1486 | 2018-03-31 | 0 | 7 | 0 | 0 | 2018-03-31 | 0 | 7 | 86.5507 | 18.3487 | 2018-03-31 | 0 | 7 | 32.8893 | 6.9067
2018-03-31 01:00 | 1 | 7 | 85.919 | 18.1289 | 2018-03-31 01:00 | 1 | 7 | 0 | 0 | 2018-03-31 01:00 | 1 | 7 | 86.5324 | 18.3449 | 2018-03-31 01:00 | 1 | 7 | 32.8823 | 6.9053
2018-03-31 02:00 | 2 | 7 | 86.0533 | 18.1572 | 2018-03-31 02:00 | 2 | 7 | 0 | 0 | 2018-03-31 02:00 | 2 | 7 | 86.6453 | 18.3688 | 2018-03-31 02:00 | 2 | 7 | 32.9252 | 6.9143
2018-03-31 03:00 | 3 | 7 | 86.1677 | 18.1814 | 2018-03-31 03:00 | 3 | 7 | 0 | 0 | 2018-03-31 03:00 | 3 | 7 | 86.7002 | 18.3804 | 2018-03-31 03:00 | 3 | 7 | 32.9461 | 6.9187
2018-03-31 04:00 | 4 | 7 | 86.3081 | 18.211 | 2018-03-31 04:00 | 4 | 7 | 0 | 0 | 2018-03-31 04:00 | 4 | 7 | 86.8513 | 18.4125 | 2018-03-31 04:00 | 4 | 7 | 33.0035 | 6.9307
2018-03-31 05:00 | 5 | 7 | 86.2562 | 18.2001 | 2018-03-31 05:00 | 5 | 7 | 0 | 0 | 2018-03-31 05:00 | 5 | 7 | 86.8605 | 18.4144 | 2018-03-31 05:00 | 5 | 7 | 33.007 | 6.9315
2018-03-31 06:00 | 6 | 7 | 86.1234 | 18.172 | 2018-03-31 06:00 | 6 | 7 | 0 | 0 | 2018-03-31 06:00 | 6 | 7 | 86.6682 | 18.3737 | 2018-03-31 06:00 | 6 | 7 | 32.9339 | 6.9161
2018-03-31 07:00 | 7 | 7 | 86.1906 | 18.1862 | 2018-03-31 07:00 | 7 | 7 | 0 | 0 | 2018-03-31 07:00 | 7 | 7 | 86.7247 | 18.3856 | 2018-03-31 07:00 | 7 | 7 | 32.9554 | 6.9206
2018-03-31 08:00 | 8 | 7 | 86.36 | 18.222 | 2018-03-31 08:00 | 8 | 7 | 0 | 0 | 2018-03-31 08:00 | 8 | 7 | 86.952 | 18.4338 | 2018-03-31 08:00 | 8 | 7 | 33.0418 | 6.9388
2018-03-31 09:00 | 9 | 7 | 86.4912 | 18.2496 | 2018-03-31 09:00 | 9 | 7 | 0 | 0 | 2018-03-31 09:00 | 9 | 7 | 87.0588 | 18.4565 | 2018-03-31 09:00 | 9 | 7 | 33.0823 | 6.9473
2018-03-31 10:00 | 10 | 7 | 86.1982 | 18.1878 | 2018-03-31 10:00 | 10 | 7 | 0 | 0 | 2018-03-31 10:00 | 10 | 7 | 86.6392 | 18.3675 | 2018-03-31 10:00 | 10 | 7 | 32.9229 | 6.9138
2018-03-31 11:00 | 11 | 7 | 86.1707 | 18.182 | 2018-03-31 11:00 | 11 | 7 | 0 | 0 | 2018-03-31 11:00 | 11 | 7 | 86.8849 | 18.4196 | 2018-03-31 11:00 | 11 | 7 | 33.0163 | 6.9334
2018-03-31 12:00 | 12 | 7 | 86.5019 | 18.2519 | 2018-03-31 12:00 | 12 | 7 | 0 | 0 | 2018-03-31 12:00 | 12 | 7 | 87.1504 | 18.4759 | 2018-03-31 12:00 | 12 | 7 | 33.1172 | 6.9546
2018-03-31 13:00 | 13 | 7 | 86.6148 | 18.2757 | 2018-03-31 13:00 | 13 | 7 | 0 | 0 | 2018-03-31 13:00 | 13 | 7 | 87.3167 | 18.5111 | 2018-03-31 13:00 | 13 | 7 | 33.1803 | 6.9679
2018-03-31 14:00 | 14 | 7 | 86.4439 | 18.2397 | 2018-03-31 14:00 | 14 | 7 | 0 | 0 | 2018-03-31 14:00 | 14 | 7 | 87.0832 | 18.4616 | 2018-03-31 14:00 | 14 | 7 | 33.0916 | 6.9492
2018-03-31 15:00 | 15 | 7 | 86.5522 | 18.2625 | 2018-03-31 15:00 | 15 | 7 | 0 | 0 | 2018-03-31 15:00 | 15 | 7 | 87.2938 | 18.5063 | 2018-03-31 15:00 | 15 | 7 | 33.1716 | 6.966
2018-03-31 16:00 | 16 | 7 | 86.5644 | 18.2651 | 2018-03-31 16:00 | 16 | 7 | 0 | 0 | 2018-03-31 16:00 | 16 | 7 | 87.3579 | 18.5199 | 2018-03-31 16:00 | 16 | 7 | 33.196 | 6.9712
2018-03-31 17:00 | 17 | 7 | 86.7445 | 18.3031 | 2018-03-31 17:00 | 17 | 7 | 0 | 0 | 2018-03-31 17:00 | 17 | 7 | 87.57 | 18.5648 | 2018-03-31 17:00 | 17 | 7 | 33.2766 | 6.9881
2018-03-31 18:00 | 18 | 7 | 86.4668 | 18.2445 | 2018-03-31 18:00 | 18 | 7 | 0 | 0 | 2018-03-31 18:00 | 18 | 7 | 87.3014 | 18.5079 | 2018-03-31 18:00 | 18 | 7 | 33.1745 | 6.9667
2018-03-31 19:00 | 19 | 7 | 86.3661 | 18.2232 | 2018-03-31 19:00 | 19 | 7 | 0 | 0 | 2018-03-31 19:00 | 19 | 7 | 87.0954 | 18.4642 | 2018-03-31 19:00 | 19 | 7 | 33.0963 | 6.9502
2018-03-31 20:00 | 20 | 7 | 86.1173 | 18.1708 | 2018-03-31 20:00 | 20 | 7 | 0 | 0 | 2018-03-31 20:00 | 20 | 7 | 86.891 | 18.4209 | 2018-03-31 20:00 | 20 | 7 | 33.0186 | 6.9339
2018-03-31 21:00 | 21 | 7 | 86.1555 | 18.1788 | 2018-03-31 21:00 | 21 | 7 | 0 | 0 | 2018-03-31 21:00 | 21 | 7 | 86.9245 | 18.428 | 2018-03-31 21:00 | 21 | 7 | 33.0313 | 6.9366
2018-03-31 22:00 | 22 | 7 | 86.2211 | 18.1927 | 2018-03-31 22:00 | 22 | 7 | 0 | 0 | 2018-03-31 22:00 | 22 | 7 | 87.0054 | 18.4451 | 2018-03-31 22:00 | 22 | 7 | 33.0621 | 6.943
2018-03-31 23:00 | 23 | 7 | 86.2226 | 18.193 | 2018-03-31 23:00 | 23 | 7 | 0 | 0 | 2018-03-31 23:00 | 23 | 7 | 87.0787 | 18.4607 | 2018-03-31 23:00 | 23 | 7 | 33.0899 | 6.9489
2018-04-01 | 0 | 1 | 86.2364 | 18.1959 | 2018-04-01 | 0 | 1 | 86.7994 | 17.681 | 2018-04-01 | 0 | 1 | 0 | 0 | 2018-04-01 | 0 | 1 | 32.9838 | 6.9266
2018-04-01 01:00 | 1 | 1 | 86.3188 | 18.2133 | 2018-04-01 01:00 | 1 | 1 | 86.952 | 17.7121 | 2018-04-01 01:00 | 1 | 1 | 0 | 0 | 2018-04-01 01:00 | 1 | 1 | 33.0418 | 6.9388
2018-04-01 02:00 | 2 | 1 | 86.2119 | 18.1907 | 2018-04-01 02:00 | 2 | 1 | 86.8177 | 17.6848 | 2018-04-01 02:00 | 2 | 1 | 0 | 0 | 2018-04-01 02:00 | 2 | 1 | 32.9907 | 6.9281
2018-04-01 03:00 | 3 | 1 | 86.1845 | 18.1849 | 2018-04-01 03:00 | 3 | 1 | 86.7857 | 17.6782 | 2018-04-01 03:00 | 3 | 1 | 0 | 0 | 2018-04-01 03:00 | 3 | 1 | 32.9786 | 6.9255
2018-04-01 04:00 | 4 | 1 | 86.2455 | 18.1978 | 2018-04-01 04:00 | 4 | 1 | 86.833 | 17.6879 | 2018-04-01 04:00 | 4 | 1 | 0 | 0 | 2018-04-01 04:00 | 4 | 1 | 32.9965 | 6.9293
2018-04-01 05:00 | 5 | 1 | 86.2333 | 18.1952 | 2018-04-01 05:00 | 5 | 1 | 86.833 | 17.6879 | 2018-04-01 05:00 | 5 | 1 | 0 | 0 | 2018-04-01 05:00 | 5 | 1 | 32.9965 | 6.9293
2018-04-01 06:00 | 6 | 1 | 86.2776 | 18.2046 | 2018-04-01 06:00 | 6 | 1 | 86.8528 | 17.6919 | 2018-04-01 06:00 | 6 | 1 | 0 | 0 | 2018-04-01 06:00 | 6 | 1 | 33.0041 | 6.9309
2018-04-01 07:00 | 7 | 1 | 86.2867 | 18.2065 | 2018-04-01 07:00 | 7 | 1 | 86.8452 | 17.6904 | 2018-04-01 07:00 | 7 | 1 | 0 | 0 | 2018-04-01 07:00 | 7 | 1 | 33.0012 | 6.9302
2018-04-01 08:00 | 8 | 1 | 86.2989 | 18.2091 | 2018-04-01 08:00 | 8 | 1 | 86.9032 | 17.7022 | 2018-04-01 08:00 | 8 | 1 | 0 | 0 | 2018-04-01 08:00 | 8 | 1 | 33.0232 | 6.9349
2018-04-01 09:00 | 9 | 1 | 86.2867 | 18.2065 | 2018-04-01 09:00 | 9 | 1 | 86.8162 | 17.6845 | 2018-04-01 09:00 | 9 | 1 | 0 | 0 | 2018-04-01 09:00 | 9 | 1 | 32.9902 | 6.9279
2018-04-01 10:00 | 10 | 1 | 86.2882 | 18.2068 | 2018-04-01 10:00 | 10 | 1 | 86.8528 | 17.6919 | 2018-04-01 10:00 | 10 | 1 | 0 | 0 | 2018-04-01 10:00 | 10 | 1 | 33.0041 | 6.9309
2018-04-01 11:00 | 11 | 1 | 86.1845 | 18.1849 | 2018-04-01 11:00 | 11 | 1 | 86.743 | 17.6695 | 2018-04-01 11:00 | 11 | 1 | 0 | 0 | 2018-04-01 11:00 | 11 | 1 | 32.9623 | 6.9221
2018-04-01 12:00 | 12 | 1 | 86.1418 | 18.1759 | 2018-04-01 12:00 | 12 | 1 | 86.714 | 17.6636 | 2018-04-01 12:00 | 12 | 1 | 0 | 0 | 2018-04-01 12:00 | 12 | 1 | 32.9513 | 6.9198
2018-04-01 13:00 | 13 | 1 | 86.1479 | 18.1772 | 2018-04-01 13:00 | 13 | 1 | 86.7659 | 17.6742 | 2018-04-01 13:00 | 13 | 1 | 0 | 0 | 2018-04-01 13:00 | 13 | 1 | 32.971 | 6.9239
2018-04-01 14:00 | 14 | 1 | 86.1112 | 18.1695 | 2018-04-01 14:00 | 14 | 1 | 86.7018 | 17.6612 | 2018-04-01 14:00 | 14 | 1 | 0 | 0 | 2018-04-01 14:00 | 14 | 1 | 32.9467 | 6.9188
2018-04-01 15:00 | 15 | 1 | 86.2455 | 18.1978 | 2018-04-01 15:00 | 15 | 1 | 86.8482 | 17.691 | 2018-04-01 15:00 | 15 | 1 | 0 | 0 | 2018-04-01 15:00 | 15 | 1 | 33.0023 | 6.9305
2018-04-01 16:00 | 16 | 1 | 86.3447 | 18.2187 | 2018-04-01 16:00 | 16 | 1 | 86.9398 | 17.7096 | 2018-04-01 16:00 | 16 | 1 | 0 | 0 | 2018-04-01 16:00 | 16 | 1 | 33.0371 | 6.9378
2018-04-01 17:00 | 17 | 1 | 86.4805 | 18.2474 | 2018-04-01 17:00 | 17 | 1 | 86.9856 | 17.719 | 2018-04-01 17:00 | 17 | 1 | 0 | 0 | 2018-04-01 17:00 | 17 | 1 | 33.0545 | 6.9415
2018-04-01 18:00 | 18 | 1 | 86.4332 | 18.2374 | 2018-04-01 18:00 | 18 | 1 | 86.92 | 17.7056 | 2018-04-01 18:00 | 18 | 1 | 0 | 0 | 2018-04-01 18:00 | 18 | 1 | 33.0296 | 6.9362
2018-04-01 19:00 | 19 | 1 | 85.6794 | 18.0784 | 2018-04-01 19:00 | 19 | 1 | 85.9266 | 17.5032 | 2018-04-01 19:00 | 19 | 1 | 0 | 0 | 2018-04-01 19:00 | 19 | 1 | 32.6521 | 6.8569
2018-04-01 20:00 | 20 | 1 | 86.3294 | 18.2155 | 2018-04-01 20:00 | 20 | 1 | 86.5888 | 17.6381 | 2018-04-01 20:00 | 20 | 1 | 0 | 0 | 2018-04-01 20:00 | 20 | 1 | 32.9037 | 6.9098
2018-04-01 21:00 | 21 | 1 | 86.3569 | 18.2213 | 2018-04-01 21:00 | 21 | 1 | 86.6728 | 17.6552 | 2018-04-01 21:00 | 21 | 1 | 0 | 0 | 2018-04-01 21:00 | 21 | 1 | 32.9357 | 6.9165
2018-04-01 22:00 | 22 | 1 | 86.4881 | 18.249 | 2018-04-01 22:00 | 22 | 1 | 86.8086 | 17.6829 | 2018-04-01 22:00 | 22 | 1 | 0 | 0 | 2018-04-01 22:00 | 22 | 1 | 32.9873 | 6.9273
2018-04-01 23:00 | 23 | 1 | 86.4332 | 18.2374 | 2018-04-01 23:00 | 23 | 1 | 86.7353 | 17.668 | 2018-04-01 23:00 | 23 | 1 | 0 | 0 | 2018-04-01 23:00 | 23 | 1 | 32.9594 | 6.9215
2018-04-02 | 0 | 2 | 86.4088 | 18.2323 | 2018-04-02 | 0 | 2 | 86.7002 | 17.6608 | 2018-04-02 | 0 | 2 | 86.9352 | 18.4303 | 2018-04-02 | 0 | 2 | 65.9815 | 13.8561
2018-04-02 01:00 | 1 | 2 | 86.0426 | 18.155 | 2018-04-02 01:00 | 1 | 2 | 86.3127 | 17.5819 | 2018-04-02 01:00 | 1 | 2 | 86.5278 | 18.3439 | 2018-04-02 01:00 | 1 | 2 | 65.6794 | 13.7927
2018-04-02 02:00 | 2 | 2 | 86.392 | 18.2287 | 2018-04-02 02:00 | 2 | 2 | 86.6392 | 17.6484 | 2018-04-02 02:00 | 2 | 2 | 86.8421 | 18.4105 | 2018-04-02 02:00 | 2 | 2 | 65.9229 | 13.8438
2018-04-02 03:00 | 3 | 2 | 86.2776 | 18.2046 | 2018-04-02 03:00 | 3 | 2 | 86.5766 | 17.6357 | 2018-04-02 03:00 | 3 | 2 | 86.7536 | 18.3918 | 2018-04-02 03:00 | 3 | 2 | 65.8655 | 13.8317
2018-04-02 04:00 | 4 | 2 | 86.5034 | 18.2522 | 2018-04-02 04:00 | 4 | 2 | 86.8849 | 17.6985 | 2018-04-02 04:00 | 4 | 2 | 87.0283 | 18.45 | 2018-04-02 04:00 | 4 | 2 | 66.087 | 13.8783
2018-04-02 05:00 | 5 | 2 | 86.3661 | 18.2232 | 2018-04-02 05:00 | 5 | 2 | 86.772 | 17.6755 | 2018-04-02 05:00 | 5 | 2 | 87.0054 | 18.4451 | 2018-04-02 05:00 | 5 | 2 | 66.0354 | 13.8674
2018-04-02 06:00 | 6 | 2 | 86.2898 | 18.2071 | 2018-04-02 06:00 | 6 | 2 | 86.6499 | 17.6506 | 2018-04-02 06:00 | 6 | 2 | 86.8147 | 18.4047 | 2018-04-02 06:00 | 6 | 2 | 65.9165 | 13.8425
2018-04-02 07:00 | 7 | 2 | 86.2043 | 18.1891 | 2018-04-02 07:00 | 7 | 2 | 86.5278 | 17.6257 | 2018-04-02 07:00 | 7 | 2 | 86.7079 | 18.3821 | 2018-04-02 07:00 | 7 | 2 | 65.8296 | 13.8242
2018-04-02 08:00 | 8 | 2 | 86.3355 | 18.2168 | 2018-04-02 08:00 | 8 | 2 | 86.5461 | 17.6294 | 2018-04-02 08:00 | 8 | 2 | 86.8025 | 18.4021 | 2018-04-02 08:00 | 8 | 2 | 65.8725 | 13.8332
2018-04-02 09:00 | 9 | 2 | 86.3798 | 18.2261 | 2018-04-02 09:00 | 9 | 2 | 86.7262 | 17.6661 | 2018-04-02 09:00 | 9 | 2 | 86.8711 | 18.4167 | 2018-04-02 09:00 | 9 | 2 | 65.967 | 13.8531
2018-04-02 10:00 | 10 | 2 | 86.2272 | 18.1939 | 2018-04-02 10:00 | 10 | 2 | 86.5156 | 17.6232 | 2018-04-02 10:00 | 10 | 2 | 86.714 | 18.3834 | 2018-04-02 10:00 | 10 | 2 | 65.8272 | 13.8237
2018-04-02 11:00 | 11 | 2 | 86.2119 | 18.1907 | 2018-04-02 11:00 | 11 | 2 | 86.5141 | 17.6229 | 2018-04-02 11:00 | 11 | 2 | 86.7201 | 18.3847 | 2018-04-02 11:00 | 11 | 2 | 65.829 | 13.8241
2018-04-02 12:00 | 12 | 2 | 86.389 | 18.2281 | 2018-04-02 12:00 | 12 | 2 | 86.6835 | 17.6574 | 2018-04-02 12:00 | 12 | 2 | 86.8574 | 18.4138 | 2018-04-02 12:00 | 12 | 2 | 65.9455 | 13.8486
2018-04-02 13:00 | 13 | 2 | 86.4027 | 18.231 | 2018-04-02 13:00 | 13 | 2 | 86.6224 | 17.645 | 2018-04-02 13:00 | 13 | 2 | 86.7475 | 18.3905 | 2018-04-02 13:00 | 13 | 2 | 65.8806 | 13.8349
2018-04-02 14:00 | 14 | 2 | 86.3783 | 18.2258 | 2018-04-02 14:00 | 14 | 2 | 86.6606 | 17.6528 | 2018-04-02 14:00 | 14 | 2 | 86.7903 | 18.3995 | 2018-04-02 14:00 | 14 | 2 | 65.9113 | 13.8414
2018-04-02 15:00 | 15 | 2 | 86.3355 | 18.2168 | 2018-04-02 15:00 | 15 | 2 | 86.5248 | 17.6251 | 2018-04-02 15:00 | 15 | 2 | 86.7384 | 18.3885 | 2018-04-02 15:00 | 15 | 2 | 65.84 | 13.8264
2018-04-02 16:00 | 16 | 2 | 86.3493 | 18.2197 | 2018-04-02 16:00 | 16 | 2 | 86.4912 | 17.6183 | 2018-04-02 16:00 | 16 | 2 | 86.685 | 18.3772 | 2018-04-02 16:00 | 16 | 2 | 65.807 | 13.8195
2018-04-02 17:00 | 17 | 2 | 86.244 | 18.1975 | 2018-04-02 17:00 | 17 | 2 | 86.4683 | 17.6136 | 2018-04-02 17:00 | 17 | 2 | 86.6743 | 18.375 | 2018-04-02 17:00 | 17 | 2 | 65.7942 | 13.8168
2018-04-02 18:00 | 18 | 2 | 86.3142 | 18.2123 | 2018-04-02 18:00 | 18 | 2 | 86.4378 | 17.6074 | 2018-04-02 18:00 | 18 | 2 | 86.5934 | 18.3578 | 2018-04-02 18:00 | 18 | 2 | 65.7519 | 13.8079
2018-04-02 19:00 | 19 | 2 | 86.2089 | 18.1901 | 2018-04-02 19:00 | 19 | 2 | 86.3508 | 17.5897 | 2018-04-02 19:00 | 19 | 2 | 86.5583 | 18.3504 | 2018-04-02 19:00 | 19 | 2 | 65.7055 | 13.7981
2018-04-02 20:00 | 20 | 2 | 86.2181 | 18.192 | 2018-04-02 20:00 | 20 | 2 | 86.4836 | 17.6167 | 2018-04-02 20:00 | 20 | 2 | 86.6896 | 18.3782 | 2018-04-02 20:00 | 20 | 2 | 65.8058 | 13.8192
2018-04-02 21:00 | 21 | 2 | 86.1494 | 18.1775 | 2018-04-02 21:00 | 21 | 2 | 86.4759 | 17.6151 | 2018-04-02 21:00 | 21 | 2 | 86.63 | 18.3656 | 2018-04-02 21:00 | 21 | 2 | 65.7802 | 13.8139
2018-04-02 22:00 | 22 | 2 | 86.2593 | 18.2007 | 2018-04-02 22:00 | 22 | 2 | 86.5522 | 17.6307 | 2018-04-02 22:00 | 22 | 2 | 86.6468 | 18.3691 | 2018-04-02 22:00 | 22 | 2 | 65.8156 | 13.8213
2018-04-02 23:00 | 23 | 2 | 86.4424 | 18.2393 | 2018-04-02 23:00 | 23 | 2 | 86.8055 | 17.6823 | 2018-04-02 23:00 | 23 | 2 | 86.8864 | 18.4199 | 2018-04-02 23:00 | 23 | 2 | 66.0029 | 13.8606
2018-04-03 | 0 | 3 | 86.4637 | 18.2438 | 2018-04-03 | 0 | 3 | 0 | 0 | 2018-04-03 | 0 | 3 | 0 | 0 | 2018-04-03 | 0 | 3 | 0 | 0
2018-04-03 01:00 | 1 | 3 | 86.5629 | 18.2648 | 2018-04-03 01:00 | 1 | 3 | 0 | 0 | 2018-04-03 01:00 | 1 | 3 | 0 | 0 | 2018-04-03 01:00 | 1 | 3 | 0 | 0
2018-04-03 02:00 | 2 | 3 | 86.3706 | 18.2242 | 2018-04-03 02:00 | 2 | 3 | 0 | 0 | 2018-04-03 02:00 | 2 | 3 | 0 | 0 | 2018-04-03 02:00 | 2 | 3 | 0 | 0
2018-04-03 03:00 | 3 | 3 | 86.3523 | 18.2203 | 2018-04-03 03:00 | 3 | 3 | 0 | 0 | 2018-04-03 03:00 | 3 | 3 | 0 | 0 | 2018-04-03 03:00 | 3 | 3 | 0 | 0
2018-04-03 04:00 | 4 | 3 | 86.3676 | 18.2236 | 2018-04-03 04:00 | 4 | 3 | 0 | 0 | 2018-04-03 04:00 | 4 | 3 | 0 | 0 | 2018-04-03 04:00 | 4 | 3 | 0 | 0
2018-04-03 05:00 | 5 | 3 | 86.4027 | 18.231 | 2018-04-03 05:00 | 5 | 3 | 0 | 0 | 2018-04-03 05:00 | 5 | 3 | 0 | 0 | 2018-04-03 05:00 | 5 | 3 | 0 | 0
2018-04-03 06:00 | 6 | 3 | 86.4652 | 18.2442 | 2018-04-03 06:00 | 6 | 3 | 0 | 0 | 2018-04-03 06:00 | 6 | 3 | 0 | 0 | 2018-04-03 06:00 | 6 | 3 | 0 | 0
2018-04-03 07:00 | 7 | 3 | 86.4012 | 18.2307 | 2018-04-03 07:00 | 7 | 3 | 0 | 0 | 2018-04-03 07:00 | 7 | 3 | 0 | 0 | 2018-04-03 07:00 | 7 | 3 | 0 | 0
2018-04-03 08:00 | 8 | 3 | 86.4515 | 18.2413 | 2018-04-03 08:00 | 8 | 3 | 0 | 0 | 2018-04-03 08:00 | 8 | 3 | 0 | 0 | 2018-04-03 08:00 | 8 | 3 | 0 | 0
2018-04-03 09:00 | 9 | 3 | 86.2028 | 18.1888 | 2018-04-03 09:00 | 9 | 3 | 0 | 0 | 2018-04-03 09:00 | 9 | 3 | 0 | 0 | 2018-04-03 09:00 | 9 | 3 | 0 | 0
2018-04-03 10:00 | 10 | 3 | 86.2715 | 18.2033 | 2018-04-03 10:00 | 10 | 3 | 0 | 0 | 2018-04-03 10:00 | 10 | 3 | 0 | 0 | 2018-04-03 10:00 | 10 | 3 | 0 | 0
2018-04-03 11:00 | 11 | 3 | 86.7567 | 18.3057 | 2018-04-03 11:00 | 11 | 3 | 0 | 0 | 2018-04-03 11:00 | 11 | 3 | 0 | 0 | 2018-04-03 11:00 | 11 | 3 | 0 | 0
2018-04-03 12:00 | 12 | 3 | 86.6194 | 18.2767 | 2018-04-03 12:00 | 12 | 3 | 0 | 0 | 2018-04-03 12:00 | 12 | 3 | 0 | 0 | 2018-04-03 12:00 | 12 | 3 | 0 | 0
2018-04-03 13:00 | 13 | 3 | 86.6377 | 18.2806 | 2018-04-03 13:00 | 13 | 3 | 0 | 0 | 2018-04-03 13:00 | 13 | 3 | 0 | 0 | 2018-04-03 13:00 | 13 | 3 | 0 | 0
2018-04-03 14:00 | 14 | 3 | 86.8757 | 18.3308 | 2018-04-03 14:00 | 14 | 3 | 0 | 0 | 2018-04-03 14:00 | 14 | 3 | 0 | 0 | 2018-04-03 14:00 | 14 | 3 | 0 | 0
2018-04-03 15:00 | 15 | 3 | 86.7994 | 18.3147 | 2018-04-03 15:00 | 15 | 3 | 0 | 0 | 2018-04-03 15:00 | 15 | 3 | 0 | 0 | 2018-04-03 15:00 | 15 | 3 | 0 | 0
2018-04-03 16:00 | 16 | 3 | 86.7674 | 18.3079 | 2018-04-03 16:00 | 16 | 3 | 0 | 0 | 2018-04-03 16:00 | 16 | 3 | 0 | 0 | 2018-04-03 16:00 | 16 | 3 | 0 | 0
2018-04-03 17:00 | 17 | 3 | 86.7384 | 18.3018 | 2018-04-03 17:00 | 17 | 3 | 0 | 0 | 2018-04-03 17:00 | 17 | 3 | 0 | 0 | 2018-04-03 17:00 | 17 | 3 | 0 | 0
2018-04-03 18:00 | 18 | 3 | 86.7124 | 18.2963 | 2018-04-03 18:00 | 18 | 3 | 0 | 0 | 2018-04-03 18:00 | 18 | 3 | 0 | 0 | 2018-04-03 18:00 | 18 | 3 | 0 | 0
2018-04-03 19:00 | 19 | 3 | 86.8376 | 18.3227 | 2018-04-03 19:00 | 19 | 3 | 0 | 0 | 2018-04-03 19:00 | 19 | 3 | 0 | 0 | 2018-04-03 19:00 | 19 | 3 | 0 | 0
2018-04-03 20:00 | 20 | 3 | 86.627 | 18.2783 | 2018-04-03 20:00 | 20 | 3 | 0 | 0 | 2018-04-03 20:00 | 20 | 3 | 0 | 0 | 2018-04-03 20:00 | 20 | 3 | 0 | 0
2018-04-03 21:00 | 21 | 3 | 86.6239 | 18.2776 | 2018-04-03 21:00 | 21 | 3 | 0 | 0 | 2018-04-03 21:00 | 21 | 3 | 0 | 0 | 2018-04-03 21:00 | 21 | 3 | 0 | 0
2018-04-03 22:00 | 22 | 3 | 86.714 | 18.2967 | 2018-04-03 22:00 | 22 | 3 | 0 | 0 | 2018-04-03 22:00 | 22 | 3 | 0 | 0 | 2018-04-03 22:00 | 22 | 3 | 0 | 0
2018-04-03 23:00 | 23 | 3 | 86.8971 | 18.3353 | 2018-04-03 23:00 | 23 | 3 | 0 | 0 | 2018-04-03 23:00 | 23 | 3 | 0 | 0 | 2018-04-03 23:00 | 23 | 3 | 0 | 0
2018-04-04 | 0 | 4 | 0 | 0 | 2018-04-04 | 0 | 4 | 0 | 0 | 2018-04-04 | 0 | 4 | 86.6712 | 18.3743 | 2018-04-04 | 0 | 4 | 32.9351 | 6.9164
2018-04-04 01:00 | 1 | 4 | 0 | 0 | 2018-04-04 01:00 | 1 | 4 | 0 | 0 | 2018-04-04 01:00 | 1 | 4 | 86.511 | 18.3403 | 2018-04-04 01:00 | 1 | 4 | 32.8742 | 6.9036
2018-04-04 02:00 | 2 | 4 | 0 | 0 | 2018-04-04 02:00 | 2 | 4 | 0 | 0 | 2018-04-04 02:00 | 2 | 4 | 86.7628 | 18.3937 | 2018-04-04 02:00 | 2 | 4 | 32.9699 | 6.9237
2018-04-04 03:00 | 3 | 4 | 0 | 0 | 2018-04-04 03:00 | 3 | 4 | 0 | 0 | 2018-04-04 03:00 | 3 | 4 | 86.7384 | 18.3885 | 2018-04-04 03:00 | 3 | 4 | 32.9606 | 6.9217
2018-04-04 04:00 | 4 | 4 | 0 | 0 | 2018-04-04 04:00 | 4 | 4 | 0 | 0 | 2018-04-04 04:00 | 4 | 4 | 86.8376 | 18.4096 | 2018-04-04 04:00 | 4 | 4 | 32.9983 | 6.9296
2018-04-04 05:00 | 5 | 4 | 0 | 0 | 2018-04-04 05:00 | 5 | 4 | 0 | 0 | 2018-04-04 05:00 | 5 | 4 | 87.0222 | 18.4487 | 2018-04-04 05:00 | 5 | 4 | 33.0684 | 6.9444
2018-04-04 06:00 | 6 | 4 | 0 | 0 | 2018-04-04 06:00 | 6 | 4 | 0 | 0 | 2018-04-04 06:00 | 6 | 4 | 86.9627 | 18.4361 | 2018-04-04 06:00 | 6 | 4 | 33.0458 | 6.9396
2018-04-04 07:00 | 7 | 4 | 0 | 0 | 2018-04-04 07:00 | 7 | 4 | 0 | 0 | 2018-04-04 07:00 | 7 | 4 | 87.1321 | 18.472 | 2018-04-04 07:00 | 7 | 4 | 33.1102 | 6.9531
2018-04-04 08:00 | 8 | 4 | 0 | 0 | 2018-04-04 08:00 | 8 | 4 | 0 | 0 | 2018-04-04 08:00 | 8 | 4 | 87.1931 | 18.4849 | 2018-04-04 08:00 | 8 | 4 | 33.1334 | 6.958
2018-04-04 09:00 | 9 | 4 | 0 | 0 | 2018-04-04 09:00 | 9 | 4 | 0 | 0 | 2018-04-04 09:00 | 9 | 4 | 86.7155 | 18.3837 | 2018-04-04 09:00 | 9 | 4 | 32.9519 | 6.9199
2018-04-04 10:00 | 10 | 4 | 0 | 0 | 2018-04-04 10:00 | 10 | 4 | 0 | 0 | 2018-04-04 10:00 | 10 | 4 | 86.6743 | 18.375 | 2018-04-04 10:00 | 10 | 4 | 32.9362 | 6.9166
2018-04-04 11:00 | 11 | 4 | 0 | 0 | 2018-04-04 11:00 | 11 | 4 | 0 | 0 | 2018-04-04 11:00 | 11 | 4 | 86.8956 | 18.4219 | 2018-04-04 11:00 | 11 | 4 | 33.0203 | 6.9343
2018-04-04 12:00 | 12 | 4 | 0 | 0 | 2018-04-04 12:00 | 12 | 4 | 0 | 0 | 2018-04-04 12:00 | 12 | 4 | 86.9276 | 18.4287 | 2018-04-04 12:00 | 12 | 4 | 33.0325 | 6.9368
2018-04-04 13:00 | 13 | 4 | 0 | 0 | 2018-04-04 13:00 | 13 | 4 | 0 | 0 | 2018-04-04 13:00 | 13 | 4 | 87.2541 | 18.4979 | 2018-04-04 13:00 | 13 | 4 | 33.1566 | 6.9629
2018-04-04 14:00 | 14 | 4 | 0 | 0 | 2018-04-04 14:00 | 14 | 4 | 0 | 0 | 2018-04-04 14:00 | 14 | 4 | 87.4037 | 18.5296 | 2018-04-04 14:00 | 14 | 4 | 33.2134 | 6.9748
2018-04-04 15:00 | 15 | 4 | 0 | 0 | 2018-04-04 15:00 | 15 | 4 | 0 | 0 | 2018-04-04 15:00 | 15 | 4 | 87.2129 | 18.4891 | 2018-04-04 15:00 | 15 | 4 | 33.1409 | 6.9596
2018-04-04 16:00 | 16 | 4 | 0 | 0 | 2018-04-04 16:00 | 16 | 4 | 0 | 0 | 2018-04-04 16:00 | 16 | 4 | 86.9718 | 18.438 | 2018-04-04 16:00 | 16 | 4 | 33.0493 | 6.9403
2018-04-04 17:00 | 17 | 4 | 0 | 0 | 2018-04-04 17:00 | 17 | 4 | 0 | 0 | 2018-04-04 17:00 | 17 | 4 | 87.1397 | 18.4736 | 2018-04-04 17:00 | 17 | 4 | 33.1131 | 6.9537
2018-04-04 18:00 | 18 | 4 | 0 | 0 | 2018-04-04 18:00 | 18 | 4 | 0 | 0 | 2018-04-04 18:00 | 18 | 4 | 87.2435 | 18.4956 | 2018-04-04 18:00 | 18 | 4 | 33.1525 | 6.962
2018-04-04 19:00 | 19 | 4 | 0 | 0 | 2018-04-04 19:00 | 19 | 4 | 0 | 0 | 2018-04-04 19:00 | 19 | 4 | 86.8894 | 18.4206 | 2018-04-04 19:00 | 19 | 4 | 33.018 | 6.9338
2018-04-04 20:00 | 20 | 4 | 0 | 0 | 2018-04-04 20:00 | 20 | 4 | 0 | 0 | 2018-04-04 20:00 | 20 | 4 | 87.1839 | 18.483 | 2018-04-04 20:00 | 20 | 4 | 33.1299 | 6.9573
2018-04-04 21:00 | 21 | 4 | 0 | 0 | 2018-04-04 21:00 | 21 | 4 | 0 | 0 | 2018-04-04 21:00 | 21 | 4 | 87.2419 | 18.4953 | 2018-04-04 21:00 | 21 | 4 | 33.1519 | 6.9619
2018-04-04 22:00 | 22 | 4 | 0 | 0 | 2018-04-04 22:00 | 22 | 4 | 0 | 0 | 2018-04-04 22:00 | 22 | 4 | 87.1733 | 18.4807 | 2018-04-04 22:00 | 22 | 4 | 33.1259 | 6.9564
2018-04-04 23:00 | 23 | 4 | 0 | 0 | 2018-04-04 23:00 | 23 | 4 | 0 | 0 | 2018-04-04 23:00 | 23 | 4 | 87.2557 | 18.4982 | 2018-04-04 23:00 | 23 | 4 | 33.1572 | 6.963
2018-04-05 | 0 | 5 | 86.5492 | 18.2619 | 2018-04-05 | 0 | 5 | 0 | 0 | 2018-04-05 | 0 | 5 | 0 | 0 | 2018-04-05 | 0 | 5 | 0 | 0
2018-04-05 01:00 | 1 | 5 | 86.7201 | 18.2979 | 2018-04-05 01:00 | 1 | 5 | 0 | 0 | 2018-04-05 01:00 | 1 | 5 | 0 | 0 | 2018-04-05 01:00 | 1 | 5 | 0 | 0
2018-04-05 02:00 | 2 | 5 | 86.5095 | 18.2535 | 2018-04-05 02:00 | 2 | 5 | 0 | 0 | 2018-04-05 02:00 | 2 | 5 | 0 | 0 | 2018-04-05 02:00 | 2 | 5 | 0 | 0
2018-04-05 03:00 | 3 | 5 | 86.4576 | 18.2426 | 2018-04-05 03:00 | 3 | 5 | 0 | 0 | 2018-04-05 03:00 | 3 | 5 | 0 | 0 | 2018-04-05 03:00 | 3 | 5 | 0 | 0
2018-04-05 04:00 | 4 | 5 | 86.6316 | 18.2793 | 2018-04-05 04:00 | 4 | 5 | 0 | 0 | 2018-04-05 04:00 | 4 | 5 | 0 | 0 | 2018-04-05 04:00 | 4 | 5 | 0 | 0
2018-04-05 05:00 | 5 | 5 | 86.569 | 18.2661 | 2018-04-05 05:00 | 5 | 5 | 0 | 0 | 2018-04-05 05:00 | 5 | 5 | 0 | 0 | 2018-04-05 05:00 | 5 | 5 | 0 | 0
2018-04-05 06:00 | 6 | 5 | 86.6468 | 18.2825 | 2018-04-05 06:00 | 6 | 5 | 0 | 0 | 2018-04-05 06:00 | 6 | 5 | 0 | 0 | 2018-04-05 06:00 | 6 | 5 | 0 | 0
2018-04-05 07:00 | 7 | 5 | 86.6361 | 18.2802 | 2018-04-05 07:00 | 7 | 5 | 0 | 0 | 2018-04-05 07:00 | 7 | 5 | 0 | 0 | 2018-04-05 07:00 | 7 | 5 | 0 | 0
2018-04-05 08:00 | 8 | 5 | 86.6819 | 18.2899 | 2018-04-05 08:00 | 8 | 5 | 0 | 0 | 2018-04-05 08:00 | 8 | 5 | 0 | 0 | 2018-04-05 08:00 | 8 | 5 | 0 | 0
2018-04-05 09:00 | 9 | 5 | 86.7094 | 18.2957 | 2018-04-05 09:00 | 9 | 5 | 0 | 0 | 2018-04-05 09:00 | 9 | 5 | 0 | 0 | 2018-04-05 09:00 | 9 | 5 | 0 | 0
2018-04-05 10:00 | 10 | 5 | 86.7933 | 18.3134 | 2018-04-05 10:00 | 10 | 5 | 0 | 0 | 2018-04-05 10:00 | 10 | 5 | 0 | 0 | 2018-04-05 10:00 | 10 | 5 | 0 | 0
2018-04-05 11:00 | 11 | 5 | 86.8009 | 18.315 | 2018-04-05 11:00 | 11 | 5 | 0 | 0 | 2018-04-05 11:00 | 11 | 5 | 0 | 0 | 2018-04-05 11:00 | 11 | 5 | 0 | 0
2018-04-05 12:00 | 12 | 5 | 86.6728 | 18.288 | 2018-04-05 12:00 | 12 | 5 | 0 | 0 | 2018-04-05 12:00 | 12 | 5 | 0 | 0 | 2018-04-05 12:00 | 12 | 5 | 0 | 0
2018-04-05 13:00 | 13 | 5 | 86.6316 | 18.2793 | 2018-04-05 13:00 | 13 | 5 | 0 | 0 | 2018-04-05 13:00 | 13 | 5 | 0 | 0 | 2018-04-05 13:00 | 13 | 5 | 0 | 0
2018-04-05 14:00 | 14 | 5 | 86.6316 | 18.2793 | 2018-04-05 14:00 | 14 | 5 | 0 | 0 | 2018-04-05 14:00 | 14 | 5 | 0 | 0 | 2018-04-05 14:00 | 14 | 5 | 0 | 0
2018-04-05 15:00 | 15 | 5 | 86.6636 | 18.286 | 2018-04-05 15:00 | 15 | 5 | 0 | 0 | 2018-04-05 15:00 | 15 | 5 | 0 | 0 | 2018-04-05 15:00 | 15 | 5 | 0 | 0
2018-04-05 16:00 | 16 | 5 | 86.5568 | 18.2635 | 2018-04-05 16:00 | 16 | 5 | 0 | 0 | 2018-04-05 16:00 | 16 | 5 | 0 | 0 | 2018-04-05 16:00 | 16 | 5 | 0 | 0
2018-04-05 17:00 | 17 | 5 | 86.6865 | 18.2909 | 2018-04-05 17:00 | 17 | 5 | 0 | 0 | 2018-04-05 17:00 | 17 | 5 | 0 | 0 | 2018-04-05 17:00 | 17 | 5 | 0 | 0
2018-04-05 18:00 | 18 | 5 | 86.7262 | 18.2992 | 2018-04-05 18:00 | 18 | 5 | 0 | 0 | 2018-04-05 18:00 | 18 | 5 | 0 | 0 | 2018-04-05 18:00 | 18 | 5 | 0 | 0
2018-04-05 19:00 | 19 | 5 | 86.5187 | 18.2554 | 2018-04-05 19:00 | 19 | 5 | 0 | 0 | 2018-04-05 19:00 | 19 | 5 | 0 | 0 | 2018-04-05 19:00 | 19 | 5 | 0 | 0
2018-04-05 20:00 | 20 | 5 | 86.5766 | 18.2677 | 2018-04-05 20:00 | 20 | 5 | 0 | 0 | 2018-04-05 20:00 | 20 | 5 | 0 | 0 | 2018-04-05 20:00 | 20 | 5 | 0 | 0
2018-04-05 21:00 | 21 | 5 | 86.6194 | 18.2767 | 2018-04-05 21:00 | 21 | 5 | 0 | 0 | 2018-04-05 21:00 | 21 | 5 | 0 | 0 | 2018-04-05 21:00 | 21 | 5 | 0 | 0
2018-04-05 22:00 | 22 | 5 | 86.6743 | 18.2883 | 2018-04-05 22:00 | 22 | 5 | 0 | 0 | 2018-04-05 22:00 | 22 | 5 | 0 | 0 | 2018-04-05 22:00 | 22 | 5 | 0 | 0
2018-04-05 23:00 | 23 | 5 | 86.5644 | 18.2651 | 2018-04-05 23:00 | 23 | 5 | 0 | 0 | 2018-04-05 23:00 | 23 | 5 | 0 | 0 | 2018-04-05 23:00 | 23 | 5 | 0 | 0
2018-04-06 | 0 | 6 | 86.2226 | 18.193 | 2018-04-06 | 0 | 6 | 86.688 | 17.6583 | 2018-04-06 | 0 | 6 | 0 | 0 | 2018-04-06 | 0 | 6 | 32.9414 | 6.9177
2018-04-06 01:00 | 1 | 6 | 86.1128 | 18.1698 | 2018-04-06 01:00 | 1 | 6 | 86.5232 | 17.6248 | 2018-04-06 01:00 | 1 | 6 | 0 | 0 | 2018-04-06 01:00 | 1 | 6 | 32.8788 | 6.9046
2018-04-06 02:00 | 2 | 6 | 86.2791 | 18.2049 | 2018-04-06 02:00 | 2 | 6 | 86.6896 | 17.6587 | 2018-04-06 02:00 | 2 | 6 | 0 | 0 | 2018-04-06 02:00 | 2 | 6 | 32.942 | 6.9178
2018-04-06 03:00 | 3 | 6 | 86.0014 | 18.1463 | 2018-04-06 03:00 | 3 | 6 | 86.4485 | 17.6096 | 2018-04-06 03:00 | 3 | 6 | 0 | 0 | 2018-04-06 03:00 | 3 | 6 | 32.8504 | 6.8986
2018-04-06 04:00 | 4 | 6 | 86.0533 | 18.1572 | 2018-04-06 04:00 | 4 | 6 | 86.4347 | 17.6067 | 2018-04-06 04:00 | 4 | 6 | 0 | 0 | 2018-04-06 04:00 | 4 | 6 | 32.8452 | 6.8975
2018-04-06 05:00 | 5 | 6 | 86.2257 | 18.1936 | 2018-04-06 05:00 | 5 | 6 | 86.6117 | 17.6428 | 2018-04-06 05:00 | 5 | 6 | 0 | 0 | 2018-04-06 05:00 | 5 | 6 | 32.9124 | 6.9116
2018-04-06 06:00 | 6 | 6 | 86.4332 | 18.2374 | 2018-04-06 06:00 | 6 | 6 | 86.9352 | 17.7087 | 2018-04-06 06:00 | 6 | 6 | 0 | 0 | 2018-04-06 06:00 | 6 | 6 | 33.0354 | 6.9374
2018-04-06 07:00 | 7 | 6 | 86.5873 | 18.2699 | 2018-04-06 07:00 | 7 | 6 | 87.0619 | 17.7345 | 2018-04-06 07:00 | 7 | 6 | 0 | 0 | 2018-04-06 07:00 | 7 | 6 | 33.0835 | 6.9475
2018-04-06 08:00 | 8 | 6 | 86.3691 | 18.2239 | 2018-04-06 08:00 | 8 | 6 | 86.7811 | 17.6773 | 2018-04-06 08:00 | 8 | 6 | 0 | 0 | 2018-04-06 08:00 | 8 | 6 | 32.9768 | 6.9251
2018-04-06 09:00 | 9 | 6 | 86.334 | 18.2165 | 2018-04-06 09:00 | 9 | 6 | 86.7399 | 17.6689 | 2018-04-06 09:00 | 9 | 6 | 0 | 0 | 2018-04-06 09:00 | 9 | 6 | 32.9612 | 6.9218
2018-04-06 10:00 | 10 | 6 | 86.5126 | 18.2542 | 2018-04-06 10:00 | 10 | 6 | 86.862 | 17.6938 | 2018-04-06 10:00 | 10 | 6 | 0 | 0 | 2018-04-06 10:00 | 10 | 6 | 33.0076 | 6.9316
2018-04-06 11:00 | 11 | 6 | 86.5003 | 18.2516 | 2018-04-06 11:00 | 11 | 6 | 86.9306 | 17.7078 | 2018-04-06 11:00 | 11 | 6 | 0 | 0 | 2018-04-06 11:00 | 11 | 6 | 33.0336 | 6.9371
2018-04-06 12:00 | 12 | 6 | 86.7002 | 18.2937 | 2018-04-06 12:00 | 12 | 6 | 87.1412 | 17.7507 | 2018-04-06 12:00 | 12 | 6 | 0 | 0 | 2018-04-06 12:00 | 12 | 6 | 33.1137 | 6.9539
2018-04-06 13:00 | 13 | 6 | 86.363 | 18.2226 | 2018-04-06 13:00 | 13 | 6 | 86.8009 | 17.6813 | 2018-04-06 13:00 | 13 | 6 | 0 | 0 | 2018-04-06 13:00 | 13 | 6 | 32.9843 | 6.9267
2018-04-06 14:00 | 14 | 6 | 86.4408 | 18.239 | 2018-04-06 14:00 | 14 | 6 | 86.8635 | 17.6941 | 2018-04-06 14:00 | 14 | 6 | 0 | 0 | 2018-04-06 14:00 | 14 | 6 | 33.0081 | 6.9317
2018-04-06 15:00 | 15 | 6 | 86.2943 | 18.2081 | 2018-04-06 15:00 | 15 | 6 | 86.6743 | 17.6556 | 2018-04-06 15:00 | 15 | 6 | 0 | 0 | 2018-04-06 15:00 | 15 | 6 | 32.9362 | 6.9166
2018-04-06 16:00 | 16 | 6 | 86.3706 | 18.2242 | 2018-04-06 16:00 | 16 | 6 | 86.7491 | 17.6708 | 2018-04-06 16:00 | 16 | 6 | 0 | 0 | 2018-04-06 16:00 | 16 | 6 | 32.9647 | 6.9226
2018-04-06 17:00 | 17 | 6 | 86.2882 | 18.2068 | 2018-04-06 17:00 | 17 | 6 | 86.7445 | 17.6699 | 2018-04-06 17:00 | 17 | 6 | 0 | 0 | 2018-04-06 17:00 | 17 | 6 | 32.9629 | 6.9222
2018-04-06 18:00 | 18 | 6 | 86.1875 | 18.1856 | 2018-04-06 18:00 | 18 | 6 | 86.6667 | 17.654 | 2018-04-06 18:00 | 18 | 6 | 0 | 0 | 2018-04-06 18:00 | 18 | 6 | 32.9333 | 6.916
2018-04-06 19:00 | 19 | 6 | 86.099 | 18.1669 | 2018-04-06 19:00 | 19 | 6 | 86.5431 | 17.6288 | 2018-04-06 19:00 | 19 | 6 | 0 | 0 | 2018-04-06 19:00 | 19 | 6 | 32.8864 | 6.9061
2018-04-06 20:00 | 20 | 6 | 86.1997 | 18.1881 | 2018-04-06 20:00 | 20 | 6 | 86.5187 | 17.6239 | 2018-04-06 20:00 | 20 | 6 | 0 | 0 | 2018-04-06 20:00 | 20 | 6 | 32.8771 | 6.9042
2018-04-06 21:00 | 21 | 6 | 86.3767 | 18.2255 | 2018-04-06 21:00 | 21 | 6 | 86.7247 | 17.6658 | 2018-04-06 21:00 | 21 | 6 | 0 | 0 | 2018-04-06 21:00 | 21 | 6 | 32.9554 | 6.9206
2018-04-06 22:00 | 22 | 6 | 86.3691 | 18.2239 | 2018-04-06 22:00 | 22 | 6 | 86.7659 | 17.6742 | 2018-04-06 22:00 | 22 | 6 | 0 | 0 | 2018-04-06 22:00 | 22 | 6 | 32.971 | 6.9239
2018-04-06 23:00 | 23 | 6 | 86.4012 | 18.2307 | 2018-04-06 23:00 | 23 | 6 | 86.7918 | 17.6795 | 2018-04-06 23:00 | 23 | 6 | 0 | 0 | 2018-04-06 23:00 | 23 | 6 | 32.9809 | 6.926
2018-04-07 | 0 | 7 | 86.0121 | 18.1486 | 2018-04-07 | 0 | 7 | 0 | 0 | 2018-04-07 | 0 | 7 | 86.5507 | 18.3487 | 2018-04-07 | 0 | 7 | 32.8893 | 6.9067
2018-04-07 01:00 | 1 | 7 | 85.919 | 18.1289 | 2018-04-07 01:00 | 1 | 7 | 0 | 0 | 2018-04-07 01:00 | 1 | 7 | 86.5324 | 18.3449 | 2018-04-07 01:00 | 1 | 7 | 32.8823 | 6.9053
2018-04-07 02:00 | 2 | 7 | 86.0533 | 18.1572 | 2018-04-07 02:00 | 2 | 7 | 0 | 0 | 2018-04-07 02:00 | 2 | 7 | 86.6453 | 18.3688 | 2018-04-07 02:00 | 2 | 7 | 32.9252 | 6.9143
2018-04-07 03:00 | 3 | 7 | 86.1677 | 18.1814 | 2018-04-07 03:00 | 3 | 7 | 0 | 0 | 2018-04-07 03:00 | 3 | 7 | 86.7002 | 18.3804 | 2018-04-07 03:00 | 3 | 7 | 32.9461 | 6.9187
2018-04-07 04:00 | 4 | 7 | 86.3081 | 18.211 | 2018-04-07 04:00 | 4 | 7 | 0 | 0 | 2018-04-07 04:00 | 4 | 7 | 86.8513 | 18.4125 | 2018-04-07 04:00 | 4 | 7 | 33.0035 | 6.9307
2018-04-07 05:00 | 5 | 7 | 86.2562 | 18.2001 | 2018-04-07 05:00 | 5 | 7 | 0 | 0 | 2018-04-07 05:00 | 5 | 7 | 86.8605 | 18.4144 | 2018-04-07 05:00 | 5 | 7 | 33.007 | 6.9315
2018-04-07 06:00 | 6 | 7 | 86.1234 | 18.172 | 2018-04-07 06:00 | 6 | 7 | 0 | 0 | 2018-04-07 06:00 | 6 | 7 | 86.6682 | 18.3737 | 2018-04-07 06:00 | 6 | 7 | 32.9339 | 6.9161
2018-04-07 07:00 | 7 | 7 | 86.1906 | 18.1862 | 2018-04-07 07:00 | 7 | 7 | 0 | 0 | 2018-04-07 07:00 | 7 | 7 | 86.7247 | 18.3856 | 2018-04-07 07:00 | 7 | 7 | 32.9554 | 6.9206
2018-04-07 08:00 | 8 | 7 | 86.36 | 18.222 | 2018-04-07 08:00 | 8 | 7 | 0 | 0 | 2018-04-07 08:00 | 8 | 7 | 86.952 | 18.4338 | 2018-04-07 08:00 | 8 | 7 | 33.0418 | 6.9388
2018-04-07 09:00 | 9 | 7 | 86.4912 | 18.2496 | 2018-04-07 09:00 | 9 | 7 | 0 | 0 | 2018-04-07 09:00 | 9 | 7 | 87.0588 | 18.4565 | 2018-04-07 09:00 | 9 | 7 | 33.0823 | 6.9473
2018-04-07 10:00 | 10 | 7 | 86.1982 | 18.1878 | 2018-04-07 10:00 | 10 | 7 | 0 | 0 | 2018-04-07 10:00 | 10 | 7 | 86.6392 | 18.3675 | 2018-04-07 10:00 | 10 | 7 | 32.9229 | 6.9138
2018-04-07 11:00 | 11 | 7 | 86.1707 | 18.182 | 2018-04-07 11:00 | 11 | 7 | 0 | 0 | 2018-04-07 11:00 | 11 | 7 | 86.8849 | 18.4196 | 2018-04-07 11:00 | 11 | 7 | 33.0163 | 6.9334
2018-04-07 12:00 | 12 | 7 | 86.5019 | 18.2519 | 2018-04-07 12:00 | 12 | 7 | 0 | 0 | 2018-04-07 12:00 | 12 | 7 | 87.1504 | 18.4759 | 2018-04-07 12:00 | 12 | 7 | 33.1172 | 6.9546
2018-04-07 13:00 | 13 | 7 | 86.6148 | 18.2757 | 2018-04-07 13:00 | 13 | 7 | 0 | 0 | 2018-04-07 13:00 | 13 | 7 | 87.3167 | 18.5111 | 2018-04-07 13:00 | 13 | 7 | 33.1803 | 6.9679
2018-04-07 14:00 | 14 | 7 | 86.4439 | 18.2397 | 2018-04-07 14:00 | 14 | 7 | 0 | 0 | 2018-04-07 14:00 | 14 | 7 | 87.0832 | 18.4616 | 2018-04-07 14:00 | 14 | 7 | 33.0916 | 6.9492
2018-04-07 15:00 | 15 | 7 | 86.5522 | 18.2625 | 2018-04-07 15:00 | 15 | 7 | 0 | 0 | 2018-04-07 15:00 | 15 | 7 | 87.2938 | 18.5063 | 2018-04-07 15:00 | 15 | 7 | 33.1716 | 6.966
2018-04-07 16:00 | 16 | 7 | 86.5644 | 18.2651 | 2018-04-07 16:00 | 16 | 7 | 0 | 0 | 2018-04-07 16:00 | 16 | 7 | 87.3579 | 18.5199 | 2018-04-07 16:00 | 16 | 7 | 33.196 | 6.9712
2018-04-07 17:00 | 17 | 7 | 86.7445 | 18.3031 | 2018-04-07 17:00 | 17 | 7 | 0 | 0 | 2018-04-07 17:00 | 17 | 7 | 87.57 | 18.5648 | 2018-04-07 17:00 | 17 | 7 | 33.2766 | 6.9881
2018-04-07 18:00 | 18 | 7 | 86.4668 | 18.2445 | 2018-04-07 18:00 | 18 | 7 | 0 | 0 | 2018-04-07 18:00 | 18 | 7 | 87.3014 | 18.5079 | 2018-04-07 18:00 | 18 | 7 | 33.1745 | 6.9667
2018-04-07 19:00 | 19 | 7 | 86.3661 | 18.2232 | 2018-04-07 19:00 | 19 | 7 | 0 | 0 | 2018-04-07 19:00 | 19 | 7 | 87.0954 | 18.4642 | 2018-04-07 19:00 | 19 | 7 | 33.0963 | 6.9502
2018-04-07 20:00 | 20 | 7 | 86.1173 | 18.1708 | 2018-04-07 20:00 | 20 | 7 | 0 | 0 | 2018-04-07 20:00 | 20 | 7 | 86.891 | 18.4209 | 2018-04-07 20:00 | 20 | 7 | 33.0186 | 6.9339
2018-04-07 21:00 | 21 | 7 | 86.1555 | 18.1788 | 2018-04-07 21:00 | 21 | 7 | 0 | 0 | 2018-04-07 21:00 | 21 | 7 | 86.9245 | 18.428 | 2018-04-07 21:00 | 21 | 7 | 33.0313 | 6.9366
2018-04-07 22:00 | 22 | 7 | 86.2211 | 18.1927 | 2018-04-07 22:00 | 22 | 7 | 0 | 0 | 2018-04-07 22:00 | 22 | 7 | 87.0054 | 18.4451 | 2018-04-07 22:00 | 22 | 7 | 33.0621 | 6.943
2018-04-07 23:00 | 23 | 7 | 86.2226 | 18.193 | 2018-04-07 23:00 | 23 | 7 | 0 | 0 | 2018-04-07 23:00 | 23 | 7 | 87.0787 | 18.4607 | 2018-04-07 23:00 | 23 | 7 | 33.0899 | 6.9489
2018-04-08 | 0 | 1 | 86.2364 | 18.1959 | 2018-04-08 | 0 | 1 | 86.7994 | 17.681 | 2018-04-08 | 0 | 1 | 0 | 0 | 2018-04-08 | 0 | 1 | 32.9838 | 6.9266
2018-04-08 01:00 | 1 | 1 | 86.3188 | 18.2133 | 2018-04-08 01:00 | 1 | 1 | 86.952 | 17.7121 | 2018-04-08 01:00 | 1 | 1 | 0 | 0 | 2018-04-08 01:00 | 1 | 1 | 33.0418 | 6.9388
2018-04-08 02:00 | 2 | 1 | 86.2119 | 18.1907 | 2018-04-08 02:00 | 2 | 1 | 86.8177 | 17.6848 | 2018-04-08 02:00 | 2 | 1 | 0 | 0 | 2018-04-08 02:00 | 2 | 1 | 32.9907 | 6.9281
2018-04-08 03:00 | 3 | 1 | 86.1845 | 18.1849 | 2018-04-08 03:00 | 3 | 1 | 86.7857 | 17.6782 | 2018-04-08 03:00 | 3 | 1 | 0 | 0 | 2018-04-08 03:00 | 3 | 1 | 32.9786 | 6.9255
2018-04-08 04:00 | 4 | 1 | 86.2455 | 18.1978 | 2018-04-08 04:00 | 4 | 1 | 86.833 | 17.6879 | 2018-04-08 04:00 | 4 | 1 | 0 | 0 | 2018-04-08 04:00 | 4 | 1 | 32.9965 | 6.9293
2018-04-08 05:00 | 5 | 1 | 86.2333 | 18.1952 | 2018-04-08 05:00 | 5 | 1 | 86.833 | 17.6879 | 2018-04-08 05:00 | 5 | 1 | 0 | 0 | 2018-04-08 05:00 | 5 | 1 | 32.9965 | 6.9293
2018-04-08 06:00 | 6 | 1 | 86.2776 | 18.2046 | 2018-04-08 06:00 | 6 | 1 | 86.8528 | 17.6919 | 2018-04-08 06:00 | 6 | 1 | 0 | 0 | 2018-04-08 06:00 | 6 | 1 | 33.0041 | 6.9309
2018-04-08 07:00 | 7 | 1 | 86.2867 | 18.2065 | 2018-04-08 07:00 | 7 | 1 | 86.8452 | 17.6904 | 2018-04-08 07:00 | 7 | 1 | 0 | 0 | 2018-04-08 07:00 | 7 | 1 | 33.0012 | 6.9302
2018-04-08 08:00 | 8 | 1 | 86.2989 | 18.2091 | 2018-04-08 08:00 | 8 | 1 | 86.9032 | 17.7022 | 2018-04-08 08:00 | 8 | 1 | 0 | 0 | 2018-04-08 08:00 | 8 | 1 | 33.0232 | 6.9349
2018-04-08 09:00 | 9 | 1 | 86.2867 | 18.2065 | 2018-04-08 09:00 | 9 | 1 | 86.8162 | 17.6845 | 2018-04-08 09:00 | 9 | 1 | 0 | 0 | 2018-04-08 09:00 | 9 | 1 | 32.9902 | 6.9279
2018-04-08 10:00 | 10 | 1 | 86.2882 | 18.2068 | 2018-04-08 10:00 | 10 | 1 | 86.8528 | 17.6919 | 2018-04-08 10:00 | 10 | 1 | 0 | 0 | 2018-04-08 10:00 | 10 | 1 | 33.0041 | 6.9309
2018-04-08 11:00 | 11 | 1 | 86.1845 | 18.1849 | 2018-04-08 11:00 | 11 | 1 | 86.743 | 17.6695 | 2018-04-08 11:00 | 11 | 1 | 0 | 0 | 2018-04-08 11:00 | 11 | 1 | 32.9623 | 6.9221
2018-04-08 12:00 | 12 | 1 | 86.1418 | 18.1759 | 2018-04-08 12:00 | 12 | 1 | 86.714 | 17.6636 | 2018-04-08 12:00 | 12 | 1 | 0 | 0 | 2018-04-08 12:00 | 12 | 1 | 32.9513 | 6.9198
2018-04-08 13:00 | 13 | 1 | 86.1479 | 18.1772 | 2018-04-08 13:00 | 13 | 1 | 86.7659 | 17.6742 | 2018-04-08 13:00 | 13 | 1 | 0 | 0 | 2018-04-08 13:00 | 13 | 1 | 32.971 | 6.9239
2018-04-08 14:00 | 14 | 1 | 86.1112 | 18.1695 | 2018-04-08 14:00 | 14 | 1 | 86.7018 | 17.6612 | 2018-04-08 14:00 | 14 | 1 | 0 | 0 | 2018-04-08 14:00 | 14 | 1 | 32.9467 | 6.9188
2018-04-08 15:00 | 15 | 1 | 86.2455 | 18.1978 | 2018-04-08 15:00 | 15 | 1 | 86.8482 | 17.691 | 2018-04-08 15:00 | 15 | 1 | 0 | 0 | 2018-04-08 15:00 | 15 | 1 | 33.0023 | 6.9305
2018-04-08 16:00 | 16 | 1 | 86.3447 | 18.2187 | 2018-04-08 16:00 | 16 | 1 | 86.9398 | 17.7096 | 2018-04-08 16:00 | 16 | 1 | 0 | 0 | 2018-04-08 16:00 | 16 | 1 | 33.0371 | 6.9378
2018-04-08 17:00 | 17 | 1 | 86.4805 | 18.2474 | 2018-04-08 17:00 | 17 | 1 | 86.9856 | 17.719 | 2018-04-08 17:00 | 17 | 1 | 0 | 0 | 2018-04-08 17:00 | 17 | 1 | 33.0545 | 6.9415
2018-04-08 18:00 | 18 | 1 | 86.4332 | 18.2374 | 2018-04-08 18:00 | 18 | 1 | 86.92 | 17.7056 | 2018-04-08 18:00 | 18 | 1 | 0 | 0 | 2018-04-08 18:00 | 18 | 1 | 33.0296 | 6.9362
2018-04-08 19:00 | 19 | 1 | 85.6794 | 18.0784 | 2018-04-08 19:00 | 19 | 1 | 85.9266 | 17.5032 | 2018-04-08 19:00 | 19 | 1 | 0 | 0 | 2018-04-08 19:00 | 19 | 1 | 32.6521 | 6.8569
2018-04-08 20:00 | 20 | 1 | 86.3294 | 18.2155 | 2018-04-08 20:00 | 20 | 1 | 86.5888 | 17.6381 | 2018-04-08 20:00 | 20 | 1 | 0 | 0 | 2018-04-08 20:00 | 20 | 1 | 32.9037 | 6.9098
2018-04-08 21:00 | 21 | 1 | 86.3569 | 18.2213 | 2018-04-08 21:00 | 21 | 1 | 86.6728 | 17.6552 | 2018-04-08 21:00 | 21 | 1 | 0 | 0 | 2018-04-08 21:00 | 21 | 1 | 32.9357 | 6.9165
2018-04-08 22:00 | 22 | 1 | 86.4881 | 18.249 | 2018-04-08 22:00 | 22 | 1 | 86.8086 | 17.6829 | 2018-04-08 22:00 | 22 | 1 | 0 | 0 | 2018-04-08 22:00 | 22 | 1 | 32.9873 | 6.9273
2018-04-08 23:00 | 23 | 1 | 86.4332 | 18.2374 | 2018-04-08 23:00 | 23 | 1 | 86.7353 | 17.668 | 2018-04-08 23:00 | 23 | 1 | 0 | 0 | 2018-04-08 23:00 | 23 | 1 | 32.9594 | 6.9215
2018-04-09 | 0 | 2 | 86.4088 | 18.2323 | 2018-04-09 | 0 | 2 | 86.7002 | 17.6608 | 2018-04-09 | 0 | 2 | 86.9352 | 18.4303 | 2018-04-09 | 0 | 2 | 65.9815 | 13.8561
2018-04-09 01:00 | 1 | 2 | 86.0426 | 18.155 | 2018-04-09 01:00 | 1 | 2 | 86.3127 | 17.5819 | 2018-04-09 01:00 | 1 | 2 | 86.5278 | 18.3439 | 2018-04-09 01:00 | 1 | 2 | 65.6794 | 13.7927
2018-04-09 02:00 | 2 | 2 | 86.392 | 18.2287 | 2018-04-09 02:00 | 2 | 2 | 86.6392 | 17.6484 | 2018-04-09 02:00 | 2 | 2 | 86.8421 | 18.4105 | 2018-04-09 02:00 | 2 | 2 | 65.9229 | 13.8438
2018-04-09 03:00 | 3 | 2 | 86.2776 | 18.2046 | 2018-04-09 03:00 | 3 | 2 | 86.5766 | 17.6357 | 2018-04-09 03:00 | 3 | 2 | 86.7536 | 18.3918 | 2018-04-09 03:00 | 3 | 2 | 65.8655 | 13.8317
2018-04-09 04:00 | 4 | 2 | 86.5034 | 18.2522 | 2018-04-09 04:00 | 4 | 2 | 86.8849 | 17.6985 | 2018-04-09 04:00 | 4 | 2 | 87.0283 | 18.45 | 2018-04-09 04:00 | 4 | 2 | 66.087 | 13.8783
2018-04-09 05:00 | 5 | 2 | 86.3661 | 18.2232 | 2018-04-09 05:00 | 5 | 2 | 86.772 | 17.6755 | 2018-04-09 05:00 | 5 | 2 | 87.0054 | 18.4451 | 2018-04-09 05:00 | 5 | 2 | 66.0354 | 13.8674
2018-04-09 06:00 | 6 | 2 | 86.2898 | 18.2071 | 2018-04-09 06:00 | 6 | 2 | 86.6499 | 17.6506 | 2018-04-09 06:00 | 6 | 2 | 86.8147 | 18.4047 | 2018-04-09 06:00 | 6 | 2 | 65.9165 | 13.8425
2018-04-09 07:00 | 7 | 2 | 86.2043 | 18.1891 | 2018-04-09 07:00 | 7 | 2 | 86.5278 | 17.6257 | 2018-04-09 07:00 | 7 | 2 | 86.7079 | 18.3821 | 2018-04-09 07:00 | 7 | 2 | 65.8296 | 13.8242
2018-04-09 08:00 | 8 | 2 | 86.3355 | 18.2168 | 2018-04-09 08:00 | 8 | 2 | 86.5461 | 17.6294 | 2018-04-09 08:00 | 8 | 2 | 86.8025 | 18.4021 | 2018-04-09 08:00 | 8 | 2 | 65.8725 | 13.8332
2018-04-09 09:00 | 9 | 2 | 86.3798 | 18.2261 | 2018-04-09 09:00 | 9 | 2 | 86.7262 | 17.6661 | 2018-04-09 09:00 | 9 | 2 | 86.8711 | 18.4167 | 2018-04-09 09:00 | 9 | 2 | 65.967 | 13.8531
2018-04-09 10:00 | 10 | 2 | 86.2272 | 18.1939 | 2018-04-09 10:00 | 10 | 2 | 86.5156 | 17.6232 | 2018-04-09 10:00 | 10 | 2 | 86.714 | 18.3834 | 2018-04-09 10:00 | 10 | 2 | 65.8272 | 13.8237
2018-04-09 11:00 | 11 | 2 | 86.2119 | 18.1907 | 2018-04-09 11:00 | 11 | 2 | 86.5141 | 17.6229 | 2018-04-09 11:00 | 11 | 2 | 86.7201 | 18.3847 | 2018-04-09 11:00 | 11 | 2 | 65.829 | 13.8241
2018-04-09 12:00 | 12 | 2 | 86.389 | 18.2281 | 2018-04-09 12:00 | 12 | 2 | 86.6835 | 17.6574 | 2018-04-09 12:00 | 12 | 2 | 86.8574 | 18.4138 | 2018-04-09 12:00 | 12 | 2 | 65.9455 | 13.8486
2018-04-09 13:00 | 13 | 2 | 86.4027 | 18.231 | 2018-04-09 13:00 | 13 | 2 | 86.6224 | 17.645 | 2018-04-09 13:00 | 13 | 2 | 86.7475 | 18.3905 | 2018-04-09 13:00 | 13 | 2 | 65.8806 | 13.8349
2018-04-09 14:00 | 14 | 2 | 86.3783 | 18.2258 | 2018-04-09 14:00 | 14 | 2 | 86.6606 | 17.6528 | 2018-04-09 14:00 | 14 | 2 | 86.7903 | 18.3995 | 2018-04-09 14:00 | 14 | 2 | 65.9113 | 13.8414
2018-04-09 15:00 | 15 | 2 | 86.3355 | 18.2168 | 2018-04-09 15:00 | 15 | 2 | 86.5248 | 17.6251 | 2018-04-09 15:00 | 15 | 2 | 86.7384 | 18.3885 | 2018-04-09 15:00 | 15 | 2 | 65.84 | 13.8264
2018-04-09 16:00 | 16 | 2 | 86.3493 | 18.2197 | 2018-04-09 16:00 | 16 | 2 | 86.4912 | 17.6183 | 2018-04-09 16:00 | 16 | 2 | 86.685 | 18.3772 | 2018-04-09 16:00 | 16 | 2 | 65.807 | 13.8195
2018-04-09 17:00 | 17 | 2 | 86.244 | 18.1975 | 2018-04-09 17:00 | 17 | 2 | 86.4683 | 17.6136 | 2018-04-09 17:00 | 17 | 2 | 86.6743 | 18.375 | 2018-04-09 17:00 | 17 | 2 | 65.7942 | 13.8168
2018-04-09 18:00 | 18 | 2 | 86.3142 | 18.2123 | 2018-04-09 18:00 | 18 | 2 | 86.4378 | 17.6074 | 2018-04-09 18:00 | 18 | 2 | 86.5934 | 18.3578 | 2018-04-09 18:00 | 18 | 2 | 65.7519 | 13.8079
2018-04-09 19:00 | 19 | 2 | 86.2089 | 18.1901 | 2018-04-09 19:00 | 19 | 2 | 86.3508 | 17.5897 | 2018-04-09 19:00 | 19 | 2 | 86.5583 | 18.3504 | 2018-04-09 19:00 | 19 | 2 | 65.7055 | 13.7981
2018-04-09 20:00 | 20 | 2 | 86.2181 | 18.192 | 2018-04-09 20:00 | 20 | 2 | 86.4836 | 17.6167 | 2018-04-09 20:00 | 20 | 2 | 86.6896 | 18.3782 | 2018-04-09 20:00 | 20 | 2 | 65.8058 | 13.8192
2018-04-09 21:00 | 21 | 2 | 86.1494 | 18.1775 | 2018-04-09 21:00 | 21 | 2 | 86.4759 | 17.6151 | 2018-04-09 21:00 | 21 | 2 | 86.63 | 18.3656 | 2018-04-09 21:00 | 21 | 2 | 65.7802 | 13.8139
2018-04-09 22:00 | 22 | 2 | 86.2593 | 18.2007 | 2018-04-09 22:00 | 22 | 2 | 86.5522 | 17.6307 | 2018-04-09 22:00 | 22 | 2 | 86.6468 | 18.3691 | 2018-04-09 22:00 | 22 | 2 | 65.8156 | 13.8213
2018-04-09 23:00 | 23 | 2 | 86.4424 | 18.2393 | 2018-04-09 23:00 | 23 | 2 | 86.8055 | 17.6823 | 2018-04-09 23:00 | 23 | 2 | 86.8864 | 18.4199 | 2018-04-09 23:00 | 23 | 2 | 66.0029 | 13.8606
2018-04-10 | 0 | 3 | 86.4637 | 18.2438 | 2018-04-10 | 0 | 3 | 0 | 0 | 2018-04-10 | 0 | 3 | 0 | 0 | 2018-04-10 | 0 | 3 | 0 | 0
2018-04-10 01:00 | 1 | 3 | 86.5629 | 18.2648 | 2018-04-10 01:00 | 1 | 3 | 0 | 0 | 2018-04-10 01:00 | 1 | 3 | 0 | 0 | 2018-04-10 01:00 | 1 | 3 | 0 | 0
2018-04-10 02:00 | 2 | 3 | 86.3706 | 18.2242 | 2018-04-10 02:00 | 2 | 3 | 0 | 0 | 2018-04-10 02:00 | 2 | 3 | 0 | 0 | 2018-04-10 02:00 | 2 | 3 | 0 | 0
2018-04-10 03:00 | 3 | 3 | 86.3523 | 18.2203 | 2018-04-10 03:00 | 3 | 3 | 0 | 0 | 2018-04-10 03:00 | 3 | 3 | 0 | 0 | 2018-04-10 03:00 | 3 | 3 | 0 | 0
2018-04-10 04:00 | 4 | 3 | 86.3676 | 18.2236 | 2018-04-10 04:00 | 4 | 3 | 0 | 0 | 2018-04-10 04:00 | 4 | 3 | 0 | 0 | 2018-04-10 04:00 | 4 | 3 | 0 | 0
2018-04-10 05:00 | 5 | 3 | 86.4027 | 18.231 | 2018-04-10 05:00 | 5 | 3 | 0 | 0 | 2018-04-10 05:00 | 5 | 3 | 0 | 0 | 2018-04-10 05:00 | 5 | 3 | 0 | 0
2018-04-10 06:00 | 6 | 3 | 86.4652 | 18.2442 | 2018-04-10 06:00 | 6 | 3 | 0 | 0 | 2018-04-10 06:00 | 6 | 3 | 0 | 0 | 2018-04-10 06:00 | 6 | 3 | 0 | 0
2018-04-10 07:00 | 7 | 3 | 86.4012 | 18.2307 | 2018-04-10 07:00 | 7 | 3 | 0 | 0 | 2018-04-10 07:00 | 7 | 3 | 0 | 0 | 2018-04-10 07:00 | 7 | 3 | 0 | 0
2018-04-10 08:00 | 8 | 3 | 86.4515 | 18.2413 | 2018-04-10 08:00 | 8 | 3 | 0 | 0 | 2018-04-10 08:00 | 8 | 3 | 0 | 0 | 2018-04-10 08:00 | 8 | 3 | 0 | 0
2018-04-10 09:00 | 9 | 3 | 86.2028 | 18.1888 | 2018-04-10 09:00 | 9 | 3 | 0 | 0 | 2018-04-10 09:00 | 9 | 3 | 0 | 0 | 2018-04-10 09:00 | 9 | 3 | 0 | 0
2018-04-10 10:00 | 10 | 3 | 86.2715 | 18.2033 | 2018-04-10 10:00 | 10 | 3 | 0 | 0 | 2018-04-10 10:00 | 10 | 3 | 0 | 0 | 2018-04-10 10:00 | 10 | 3 | 0 | 0
2018-04-10 11:00 | 11 | 3 | 86.7567 | 18.3057 | 2018-04-10 11:00 | 11 | 3 | 0 | 0 | 2018-04-10 11:00 | 11 | 3 | 0 | 0 | 2018-04-10 11:00 | 11 | 3 | 0 | 0
2018-04-10 12:00 | 12 | 3 | 86.6194 | 18.2767 | 2018-04-10 12:00 | 12 | 3 | 0 | 0 | 2018-04-10 12:00 | 12 | 3 | 0 | 0 | 2018-04-10 12:00 | 12 | 3 | 0 | 0
2018-04-10 13:00 | 13 | 3 | 86.6377 | 18.2806 | 2018-04-10 13:00 | 13 | 3 | 0 | 0 | 2018-04-10 13:00 | 13 | 3 | 0 | 0 | 2018-04-10 13:00 | 13 | 3 | 0 | 0
2018-04-10 14:00 | 14 | 3 | 86.8757 | 18.3308 | 2018-04-10 14:00 | 14 | 3 | 0 | 0 | 2018-04-10 14:00 | 14 | 3 | 0 | 0 | 2018-04-10 14:00 | 14 | 3 | 0 | 0
2018-04-10 15:00 | 15 | 3 | 86.7994 | 18.3147 | 2018-04-10 15:00 | 15 | 3 | 0 | 0 | 2018-04-10 15:00 | 15 | 3 | 0 | 0 | 2018-04-10 15:00 | 15 | 3 | 0 | 0
2018-04-10 16:00 | 16 | 3 | 86.7674 | 18.3079 | 2018-04-10 16:00 | 16 | 3 | 0 | 0 | 2018-04-10 16:00 | 16 | 3 | 0 | 0 | 2018-04-10 16:00 | 16 | 3 | 0 | 0
2018-04-10 17:00 | 17 | 3 | 86.7384 | 18.3018 | 2018-04-10 17:00 | 17 | 3 | 0 | 0 | 2018-04-10 17:00 | 17 | 3 | 0 | 0 | 2018-04-10 17:00 | 17 | 3 | 0 | 0
2018-04-10 18:00 | 18 | 3 | 86.7124 | 18.2963 | 2018-04-10 18:00 | 18 | 3 | 0 | 0 | 2018-04-10 18:00 | 18 | 3 | 0 | 0 | 2018-04-10 18:00 | 18 | 3 | 0 | 0
2018-04-10 19:00 | 19 | 3 | 86.8376 | 18.3227 | 2018-04-10 19:00 | 19 | 3 | 0 | 0 | 2018-04-10 19:00 | 19 | 3 | 0 | 0 | 2018-04-10 19:00 | 19 | 3 | 0 | 0
2018-04-10 20:00 | 20 | 3 | 86.627 | 18.2783 | 2018-04-10 20:00 | 20 | 3 | 0 | 0 | 2018-04-10 20:00 | 20 | 3 | 0 | 0 | 2018-04-10 20:00 | 20 | 3 | 0 | 0
2018-04-10 21:00 | 21 | 3 | 86.6239 | 18.2776 | 2018-04-10 21:00 | 21 | 3 | 0 | 0 | 2018-04-10 21:00 | 21 | 3 | 0 | 0 | 2018-04-10 21:00 | 21 | 3 | 0 | 0
2018-04-10 22:00 | 22 | 3 | 86.714 | 18.2967 | 2018-04-10 22:00 | 22 | 3 | 0 | 0 | 2018-04-10 22:00 | 22 | 3 | 0 | 0 | 2018-04-10 22:00 | 22 | 3 | 0 | 0
2018-04-10 23:00 | 23 | 3 | 86.8971 | 18.3353 | 2018-04-10 23:00 | 23 | 3 | 0 | 0 | 2018-04-10 23:00 | 23 | 3 | 0 | 0 | 2018-04-10 23:00 | 23 | 3 | 0 | 0
2018-04-11 | 0 | 4 | 0 | 0 | 2018-04-11 | 0 | 4 | 0 | 0 | 2018-04-11 | 0 | 4 | 86.6712 | 18.3743 | 2018-04-11 | 0 | 4 | 32.9351 | 6.9164
2018-04-11 01:00 | 1 | 4 | 0 | 0 | 2018-04-11 01:00 | 1 | 4 | 0 | 0 | 2018-04-11 01:00 | 1 | 4 | 86.511 | 18.3403 | 2018-04-11 01:00 | 1 | 4 | 32.8742 | 6.9036
2018-04-11 02:00 | 2 | 4 | 0 | 0 | 2018-04-11 02:00 | 2 | 4 | 0 | 0 | 2018-04-11 02:00 | 2 | 4 | 86.7628 | 18.3937 | 2018-04-11 02:00 | 2 | 4 | 32.9699 | 6.9237
2018-04-11 03:00 | 3 | 4 | 0 | 0 | 2018-04-11 03:00 | 3 | 4 | 0 | 0 | 2018-04-11 03:00 | 3 | 4 | 86.7384 | 18.3885 | 2018-04-11 03:00 | 3 | 4 | 32.9606 | 6.9217
2018-04-11 04:00 | 4 | 4 | 0 | 0 | 2018-04-11 04:00 | 4 | 4 | 0 | 0 | 2018-04-11 04:00 | 4 | 4 | 86.8376 | 18.4096 | 2018-04-11 04:00 | 4 | 4 | 32.9983 | 6.9296
2018-04-11 05:00 | 5 | 4 | 0 | 0 | 2018-04-11 05:00 | 5 | 4 | 0 | 0 | 2018-04-11 05:00 | 5 | 4 | 87.0222 | 18.4487 | 2018-04-11 05:00 | 5 | 4 | 33.0684 | 6.9444
2018-04-11 06:00 | 6 | 4 | 0 | 0 | 2018-04-11 06:00 | 6 | 4 | 0 | 0 | 2018-04-11 06:00 | 6 | 4 | 86.9627 | 18.4361 | 2018-04-11 06:00 | 6 | 4 | 33.0458 | 6.9396
2018-04-11 07:00 | 7 | 4 | 0 | 0 | 2018-04-11 07:00 | 7 | 4 | 0 | 0 | 2018-04-11 07:00 | 7 | 4 | 87.1321 | 18.472 | 2018-04-11 07:00 | 7 | 4 | 33.1102 | 6.9531
2018-04-11 08:00 | 8 | 4 | 0 | 0 | 2018-04-11 08:00 | 8 | 4 | 0 | 0 | 2018-04-11 08:00 | 8 | 4 | 87.1931 | 18.4849 | 2018-04-11 08:00 | 8 | 4 | 33.1334 | 6.958
2018-04-11 09:00 | 9 | 4 | 0 | 0 | 2018-04-11 09:00 | 9 | 4 | 0 | 0 | 2018-04-11 09:00 | 9 | 4 | 86.7155 | 18.3837 | 2018-04-11 09:00 | 9 | 4 | 32.9519 | 6.9199
2018-04-11 10:00 | 10 | 4 | 0 | 0 | 2018-04-11 10:00 | 10 | 4 | 0 | 0 | 2018-04-11 10:00 | 10 | 4 | 86.6743 | 18.375 | 2018-04-11 10:00 | 10 | 4 | 32.9362 | 6.9166
2018-04-11 11:00 | 11 | 4 | 0 | 0 | 2018-04-11 11:00 | 11 | 4 | 0 | 0 | 2018-04-11 11:00 | 11 | 4 | 86.8956 | 18.4219 | 2018-04-11 11:00 | 11 | 4 | 33.0203 | 6.9343
2018-04-11 12:00 | 12 | 4 | 0 | 0 | 2018-04-11 12:00 | 12 | 4 | 0 | 0 | 2018-04-11 12:00 | 12 | 4 | 86.9276 | 18.4287 | 2018-04-11 12:00 | 12 | 4 | 33.0325 | 6.9368
2018-04-11 13:00 | 13 | 4 | 0 | 0 | 2018-04-11 13:00 | 13 | 4 | 0 | 0 | 2018-04-11 13:00 | 13 | 4 | 87.2541 | 18.4979 | 2018-04-11 13:00 | 13 | 4 | 33.1566 | 6.9629
2018-04-11 14:00 | 14 | 4 | 0 | 0 | 2018-04-11 14:00 | 14 | 4 | 0 | 0 | 2018-04-11 14:00 | 14 | 4 | 87.4037 | 18.5296 | 2018-04-11 14:00 | 14 | 4 | 33.2134 | 6.9748
2018-04-11 15:00 | 15 | 4 | 0 | 0 | 2018-04-11 15:00 | 15 | 4 | 0 | 0 | 2018-04-11 15:00 | 15 | 4 | 87.2129 | 18.4891 | 2018-04-11 15:00 | 15 | 4 | 33.1409 | 6.9596
2018-04-11 16:00 | 16 | 4 | 0 | 0 | 2018-04-11 16:00 | 16 | 4 | 0 | 0 | 2018-04-11 16:00 | 16 | 4 | 86.9718 | 18.438 | 2018-04-11 16:00 | 16 | 4 | 33.0493 | 6.9403
2018-04-11 17:00 | 17 | 4 | 0 | 0 | 2018-04-11 17:00 | 17 | 4 | 0 | 0 | 2018-04-11 17:00 | 17 | 4 | 87.1397 | 18.4736 | 2018-04-11 17:00 | 17 | 4 | 33.1131 | 6.9537
2018-04-11 18:00 | 18 | 4 | 0 | 0 | 2018-04-11 18:00 | 18 | 4 | 0 | 0 | 2018-04-11 18:00 | 18 | 4 | 87.2435 | 18.4956 | 2018-04-11 18:00 | 18 | 4 | 33.1525 | 6.962
2018-04-11 19:00 | 19 | 4 | 0 | 0 | 2018-04-11 19:00 | 19 | 4 | 0 | 0 | 2018-04-11 19:00 | 19 | 4 | 86.8894 | 18.4206 | 2018-04-11 19:00 | 19 | 4 | 33.018 | 6.9338
2018-04-11 20:00 | 20 | 4 | 0 | 0 | 2018-04-11 20:00 | 20 | 4 | 0 | 0 | 2018-04-11 20:00 | 20 | 4 | 87.1839 | 18.483 | 2018-04-11 20:00 | 20 | 4 | 33.1299 | 6.9573
2018-04-11 21:00 | 21 | 4 | 0 | 0 | 2018-04-11 21:00 | 21 | 4 | 0 | 0 | 2018-04-11 21:00 | 21 | 4 | 87.2419 | 18.4953 | 2018-04-11 21:00 | 21 | 4 | 33.1519 | 6.9619
2018-04-11 22:00 | 22 | 4 | 0 | 0 | 2018-04-11 22:00 | 22 | 4 | 0 | 0 | 2018-04-11 22:00 | 22 | 4 | 87.1733 | 18.4807 | 2018-04-11 22:00 | 22 | 4 | 33.1259 | 6.9564
2018-04-11 23:00 | 23 | 4 | 0 | 0 | 2018-04-11 23:00 | 23 | 4 | 0 | 0 | 2018-04-11 23:00 | 23 | 4 | 87.2557 | 18.4982 | 2018-04-11 23:00 | 23 | 4 | 33.1572 | 6.963
2018-04-12 | 0 | 5 | 86.5492 | 18.2619 | 2018-04-12 | 0 | 5 | 0 | 0 | 2018-04-12 | 0 | 5 | 0 | 0 | 2018-04-12 | 0 | 5 | 0 | 0
2018-04-12 01:00 | 1 | 5 | 86.7201 | 18.2979 | 2018-04-12 01:00 | 1 | 5 | 0 | 0 | 2018-04-12 01:00 | 1 | 5 | 0 | 0 | 2018-04-12 01:00 | 1 | 5 | 0 | 0
2018-04-12 02:00 | 2 | 5 | 86.5095 | 18.2535 | 2018-04-12 02:00 | 2 | 5 | 0 | 0 | 2018-04-12 02:00 | 2 | 5 | 0 | 0 | 2018-04-12 02:00 | 2 | 5 | 0 | 0
2018-04-12 03:00 | 3 | 5 | 86.4576 | 18.2426 | 2018-04-12 03:00 | 3 | 5 | 0 | 0 | 2018-04-12 03:00 | 3 | 5 | 0 | 0 | 2018-04-12 03:00 | 3 | 5 | 0 | 0
2018-04-12 04:00 | 4 | 5 | 86.6316 | 18.2793 | 2018-04-12 04:00 | 4 | 5 | 0 | 0 | 2018-04-12 04:00 | 4 | 5 | 0 | 0 | 2018-04-12 04:00 | 4 | 5 | 0 | 0
2018-04-12 05:00 | 5 | 5 | 86.569 | 18.2661 | 2018-04-12 05:00 | 5 | 5 | 0 | 0 | 2018-04-12 05:00 | 5 | 5 | 0 | 0 | 2018-04-12 05:00 | 5 | 5 | 0 | 0
2018-04-12 06:00 | 6 | 5 | 86.6468 | 18.2825 | 2018-04-12 06:00 | 6 | 5 | 0 | 0 | 2018-04-12 06:00 | 6 | 5 | 0 | 0 | 2018-04-12 06:00 | 6 | 5 | 0 | 0
2018-04-12 07:00 | 7 | 5 | 86.6361 | 18.2802 | 2018-04-12 07:00 | 7 | 5 | 0 | 0 | 2018-04-12 07:00 | 7 | 5 | 0 | 0 | 2018-04-12 07:00 | 7 | 5 | 0 | 0
2018-04-12 08:00 | 8 | 5 | 86.6819 | 18.2899 | 2018-04-12 08:00 | 8 | 5 | 0 | 0 | 2018-04-12 08:00 | 8 | 5 | 0 | 0 | 2018-04-12 08:00 | 8 | 5 | 0 | 0
2018-04-12 09:00 | 9 | 5 | 86.7094 | 18.2957 | 2018-04-12 09:00 | 9 | 5 | 0 | 0 | 2018-04-12 09:00 | 9 | 5 | 0 | 0 | 2018-04-12 09:00 | 9 | 5 | 0 | 0
2018-04-12 10:00 | 10 | 5 | 86.7933 | 18.3134 | 2018-04-12 10:00 | 10 | 5 | 0 | 0 | 2018-04-12 10:00 | 10 | 5 | 0 | 0 | 2018-04-12 10:00 | 10 | 5 | 0 | 0
2018-04-12 11:00 | 11 | 5 | 86.8009 | 18.315 | 2018-04-12 11:00 | 11 | 5 | 0 | 0 | 2018-04-12 11:00 | 11 | 5 | 0 | 0 | 2018-04-12 11:00 | 11 | 5 | 0 | 0
2018-04-12 12:00 | 12 | 5 | 86.6728 | 18.288 | 2018-04-12 12:00 | 12 | 5 | 0 | 0 | 2018-04-12 12:00 | 12 | 5 | 0 | 0 | 2018-04-12 12:00 | 12 | 5 | 0 | 0
2018-04-12 13:00 | 13 | 5 | 86.6316 | 18.2793 | 2018-04-12 13:00 | 13 | 5 | 0 | 0 | 2018-04-12 13:00 | 13 | 5 | 0 | 0 | 2018-04-12 13:00 | 13 | 5 | 0 | 0
2018-04-12 14:00 | 14 | 5 | 86.6316 | 18.2793 | 2018-04-12 14:00 | 14 | 5 | 0 | 0 | 2018-04-12 14:00 | 14 | 5 | 0 | 0 | 2018-04-12 14:00 | 14 | 5 | 0 | 0
2018-04-12 15:00 | 15 | 5 | 86.6636 | 18.286 | 2018-04-12 15:00 | 15 | 5 | 0 | 0 | 2018-04-12 15:00 | 15 | 5 | 0 | 0 | 2018-04-12 15:00 | 15 | 5 | 0 | 0
2018-04-12 16:00 | 16 | 5 | 86.5568 | 18.2635 | 2018-04-12 16:00 | 16 | 5 | 0 | 0 | 2018-04-12 16:00 | 16 | 5 | 0 | 0 | 2018-04-12 16:00 | 16 | 5 | 0 | 0
2018-04-12 17:00 | 17 | 5 | 86.6865 | 18.2909 | 2018-04-12 17:00 | 17 | 5 | 0 | 0 | 2018-04-12 17:00 | 17 | 5 | 0 | 0 | 2018-04-12 17:00 | 17 | 5 | 0 | 0
2018-04-12 18:00 | 18 | 5 | 86.7262 | 18.2992 | 2018-04-12 18:00 | 18 | 5 | 0 | 0 | 2018-04-12 18:00 | 18 | 5 | 0 | 0 | 2018-04-12 18:00 | 18 | 5 | 0 | 0
2018-04-12 19:00 | 19 | 5 | 86.5187 | 18.2554 | 2018-04-12 19:00 | 19 | 5 | 0 | 0 | 2018-04-12 19:00 | 19 | 5 | 0 | 0 | 2018-04-12 19:00 | 19 | 5 | 0 | 0
2018-04-12 20:00 | 20 | 5 | 86.5766 | 18.2677 | 2018-04-12 20:00 | 20 | 5 | 0 | 0 | 2018-04-12 20:00 | 20 | 5 | 0 | 0 | 2018-04-12 20:00 | 20 | 5 | 0 | 0
2018-04-12 21:00 | 21 | 5 | 86.6194 | 18.2767 | 2018-04-12 21:00 | 21 | 5 | 0 | 0 | 2018-04-12 21:00 | 21 | 5 | 0 | 0 | 2018-04-12 21:00 | 21 | 5 | 0 | 0
2018-04-12 22:00 | 22 | 5 | 86.6743 | 18.2883 | 2018-04-12 22:00 | 22 | 5 | 0 | 0 | 2018-04-12 22:00 | 22 | 5 | 0 | 0 | 2018-04-12 22:00 | 22 | 5 | 0 | 0
2018-04-12 23:00 | 23 | 5 | 86.5644 | 18.2651 | 2018-04-12 23:00 | 23 | 5 | 0 | 0 | 2018-04-12 23:00 | 23 | 5 | 0 | 0 | 2018-04-12 23:00 | 23 | 5 | 0 | 0
2018-04-13 | 0 | 6 | 86.2226 | 18.193 | 2018-04-13 | 0 | 6 | 86.688 | 17.6583 | 2018-04-13 | 0 | 6 | 0 | 0 | 2018-04-13 | 0 | 6 | 32.9414 | 6.9177
2018-04-13 01:00 | 1 | 6 | 86.1128 | 18.1698 | 2018-04-13 01:00 | 1 | 6 | 86.5232 | 17.6248 | 2018-04-13 01:00 | 1 | 6 | 0 | 0 | 2018-04-13 01:00 | 1 | 6 | 32.8788 | 6.9046
2018-04-13 02:00 | 2 | 6 | 86.2791 | 18.2049 | 2018-04-13 02:00 | 2 | 6 | 86.6896 | 17.6587 | 2018-04-13 02:00 | 2 | 6 | 0 | 0 | 2018-04-13 02:00 | 2 | 6 | 32.942 | 6.9178
2018-04-13 03:00 | 3 | 6 | 86.0014 | 18.1463 | 2018-04-13 03:00 | 3 | 6 | 86.4485 | 17.6096 | 2018-04-13 03:00 | 3 | 6 | 0 | 0 | 2018-04-13 03:00 | 3 | 6 | 32.8504 | 6.8986
2018-04-13 04:00 | 4 | 6 | 86.0533 | 18.1572 | 2018-04-13 04:00 | 4 | 6 | 86.4347 | 17.6067 | 2018-04-13 04:00 | 4 | 6 | 0 | 0 | 2018-04-13 04:00 | 4 | 6 | 32.8452 | 6.8975
2018-04-13 05:00 | 5 | 6 | 86.2257 | 18.1936 | 2018-04-13 05:00 | 5 | 6 | 86.6117 | 17.6428 | 2018-04-13 05:00 | 5 | 6 | 0 | 0 | 2018-04-13 05:00 | 5 | 6 | 32.9124 | 6.9116
2018-04-13 06:00 | 6 | 6 | 86.4332 | 18.2374 | 2018-04-13 06:00 | 6 | 6 | 86.9352 | 17.7087 | 2018-04-13 06:00 | 6 | 6 | 0 | 0 | 2018-04-13 06:00 | 6 | 6 | 33.0354 | 6.9374
2018-04-13 07:00 | 7 | 6 | 86.5873 | 18.2699 | 2018-04-13 07:00 | 7 | 6 | 87.0619 | 17.7345 | 2018-04-13 07:00 | 7 | 6 | 0 | 0 | 2018-04-13 07:00 | 7 | 6 | 33.0835 | 6.9475
2018-04-13 08:00 | 8 | 6 | 86.3691 | 18.2239 | 2018-04-13 08:00 | 8 | 6 | 86.7811 | 17.6773 | 2018-04-13 08:00 | 8 | 6 | 0 | 0 | 2018-04-13 08:00 | 8 | 6 | 32.9768 | 6.9251
2018-04-13 09:00 | 9 | 6 | 86.334 | 18.2165 | 2018-04-13 09:00 | 9 | 6 | 86.7399 | 17.6689 | 2018-04-13 09:00 | 9 | 6 | 0 | 0 | 2018-04-13 09:00 | 9 | 6 | 32.9612 | 6.9218
2018-04-13 10:00 | 10 | 6 | 86.5126 | 18.2542 | 2018-04-13 10:00 | 10 | 6 | 86.862 | 17.6938 | 2018-04-13 10:00 | 10 | 6 | 0 | 0 | 2018-04-13 10:00 | 10 | 6 | 33.0076 | 6.9316
2018-04-13 11:00 | 11 | 6 | 86.5003 | 18.2516 | 2018-04-13 11:00 | 11 | 6 | 86.9306 | 17.7078 | 2018-04-13 11:00 | 11 | 6 | 0 | 0 | 2018-04-13 11:00 | 11 | 6 | 33.0336 | 6.9371
2018-04-13 12:00 | 12 | 6 | 86.7002 | 18.2937 | 2018-04-13 12:00 | 12 | 6 | 87.1412 | 17.7507 | 2018-04-13 12:00 | 12 | 6 | 0 | 0 | 2018-04-13 12:00 | 12 | 6 | 33.1137 | 6.9539
2018-04-13 13:00 | 13 | 6 | 86.363 | 18.2226 | 2018-04-13 13:00 | 13 | 6 | 86.8009 | 17.6813 | 2018-04-13 13:00 | 13 | 6 | 0 | 0 | 2018-04-13 13:00 | 13 | 6 | 32.9843 | 6.9267
2018-04-13 14:00 | 14 | 6 | 86.4408 | 18.239 | 2018-04-13 14:00 | 14 | 6 | 86.8635 | 17.6941 | 2018-04-13 14:00 | 14 | 6 | 0 | 0 | 2018-04-13 14:00 | 14 | 6 | 33.0081 | 6.9317
2018-04-13 15:00 | 15 | 6 | 86.2943 | 18.2081 | 2018-04-13 15:00 | 15 | 6 | 86.6743 | 17.6556 | 2018-04-13 15:00 | 15 | 6 | 0 | 0 | 2018-04-13 15:00 | 15 | 6 | 32.9362 | 6.9166
2018-04-13 16:00 | 16 | 6 | 86.3706 | 18.2242 | 2018-04-13 16:00 | 16 | 6 | 86.7491 | 17.6708 | 2018-04-13 16:00 | 16 | 6 | 0 | 0 | 2018-04-13 16:00 | 16 | 6 | 32.9647 | 6.9226
2018-04-13 17:00 | 17 | 6 | 86.2882 | 18.2068 | 2018-04-13 17:00 | 17 | 6 | 86.7445 | 17.6699 | 2018-04-13 17:00 | 17 | 6 | 0 | 0 | 2018-04-13 17:00 | 17 | 6 | 32.9629 | 6.9222
2018-04-13 18:00 | 18 | 6 | 86.1875 | 18.1856 | 2018-04-13 18:00 | 18 | 6 | 86.6667 | 17.654 | 2018-04-13 18:00 | 18 | 6 | 0 | 0 | 2018-04-13 18:00 | 18 | 6 | 32.9333 | 6.916
2018-04-13 19:00 | 19 | 6 | 86.099 | 18.1669 | 2018-04-13 19:00 | 19 | 6 | 86.5431 | 17.6288 | 2018-04-13 19:00 | 19 | 6 | 0 | 0 | 2018-04-13 19:00 | 19 | 6 | 32.8864 | 6.9061
2018-04-13 20:00 | 20 | 6 | 86.1997 | 18.1881 | 2018-04-13 20:00 | 20 | 6 | 86.5187 | 17.6239 | 2018-04-13 20:00 | 20 | 6 | 0 | 0 | 2018-04-13 20:00 | 20 | 6 | 32.8771 | 6.9042
2018-04-13 21:00 | 21 | 6 | 86.3767 | 18.2255 | 2018-04-13 21:00 | 21 | 6 | 86.7247 | 17.6658 | 2018-04-13 21:00 | 21 | 6 | 0 | 0 | 2018-04-13 21:00 | 21 | 6 | 32.9554 | 6.9206
2018-04-13 22:00 | 22 | 6 | 86.3691 | 18.2239 | 2018-04-13 22:00 | 22 | 6 | 86.7659 | 17.6742 | 2018-04-13 22:00 | 22 | 6 | 0 | 0 | 2018-04-13 22:00 | 22 | 6 | 32.971 | 6.9239
2018-04-13 23:00 | 23 | 6 | 86.4012 | 18.2307 | 2018-04-13 23:00 | 23 | 6 | 86.7918 | 17.6795 | 2018-04-13 23:00 | 23 | 6 | 0 | 0 | 2018-04-13 23:00 | 23 | 6 | 32.9809 | 6.926
2018-04-14 | 0 | 7 | 86.0121 | 18.1486 | 2018-04-14 | 0 | 7 | 0 | 0 | 2018-04-14 | 0 | 7 | 86.5507 | 18.3487 | 2018-04-14 | 0 | 7 | 32.8893 | 6.9067
2018-04-14 01:00 | 1 | 7 | 85.919 | 18.1289 | 2018-04-14 01:00 | 1 | 7 | 0 | 0 | 2018-04-14 01:00 | 1 | 7 | 86.5324 | 18.3449 | 2018-04-14 01:00 | 1 | 7 | 32.8823 | 6.9053
2018-04-14 02:00 | 2 | 7 | 86.0533 | 18.1572 | 2018-04-14 02:00 | 2 | 7 | 0 | 0 | 2018-04-14 02:00 | 2 | 7 | 86.6453 | 18.3688 | 2018-04-14 02:00 | 2 | 7 | 32.9252 | 6.9143
2018-04-14 03:00 | 3 | 7 | 86.1677 | 18.1814 | 2018-04-14 03:00 | 3 | 7 | 0 | 0 | 2018-04-14 03:00 | 3 | 7 | 86.7002 | 18.3804 | 2018-04-14 03:00 | 3 | 7 | 32.9461 | 6.9187
2018-04-14 04:00 | 4 | 7 | 86.3081 | 18.211 | 2018-04-14 04:00 | 4 | 7 | 0 | 0 | 2018-04-14 04:00 | 4 | 7 | 86.8513 | 18.4125 | 2018-04-14 04:00 | 4 | 7 | 33.0035 | 6.9307
2018-04-14 05:00 | 5 | 7 | 86.2562 | 18.2001 | 2018-04-14 05:00 | 5 | 7 | 0 | 0 | 2018-04-14 05:00 | 5 | 7 | 86.8605 | 18.4144 | 2018-04-14 05:00 | 5 | 7 | 33.007 | 6.9315
2018-04-14 06:00 | 6 | 7 | 86.1234 | 18.172 | 2018-04-14 06:00 | 6 | 7 | 0 | 0 | 2018-04-14 06:00 | 6 | 7 | 86.6682 | 18.3737 | 2018-04-14 06:00 | 6 | 7 | 32.9339 | 6.9161
2018-04-14 07:00 | 7 | 7 | 86.1906 | 18.1862 | 2018-04-14 07:00 | 7 | 7 | 0 | 0 | 2018-04-14 07:00 | 7 | 7 | 86.7247 | 18.3856 | 2018-04-14 07:00 | 7 | 7 | 32.9554 | 6.9206
2018-04-14 08:00 | 8 | 7 | 86.36 | 18.222 | 2018-04-14 08:00 | 8 | 7 | 0 | 0 | 2018-04-14 08:00 | 8 | 7 | 86.952 | 18.4338 | 2018-04-14 08:00 | 8 | 7 | 33.0418 | 6.9388
2018-04-14 09:00 | 9 | 7 | 86.4912 | 18.2496 | 2018-04-14 09:00 | 9 | 7 | 0 | 0 | 2018-04-14 09:00 | 9 | 7 | 87.0588 | 18.4565 | 2018-04-14 09:00 | 9 | 7 | 33.0823 | 6.9473
2018-04-14 10:00 | 10 | 7 | 86.1982 | 18.1878 | 2018-04-14 10:00 | 10 | 7 | 0 | 0 | 2018-04-14 10:00 | 10 | 7 | 86.6392 | 18.3675 | 2018-04-14 10:00 | 10 | 7 | 32.9229 | 6.9138
2018-04-14 11:00 | 11 | 7 | 86.1707 | 18.182 | 2018-04-14 11:00 | 11 | 7 | 0 | 0 | 2018-04-14 11:00 | 11 | 7 | 86.8849 | 18.4196 | 2018-04-14 11:00 | 11 | 7 | 33.0163 | 6.9334
2018-04-14 12:00 | 12 | 7 | 86.5019 | 18.2519 | 2018-04-14 12:00 | 12 | 7 | 0 | 0 | 2018-04-14 12:00 | 12 | 7 | 87.1504 | 18.4759 | 2018-04-14 12:00 | 12 | 7 | 33.1172 | 6.9546
2018-04-14 13:00 | 13 | 7 | 86.6148 | 18.2757 | 2018-04-14 13:00 | 13 | 7 | 0 | 0 | 2018-04-14 13:00 | 13 | 7 | 87.3167 | 18.5111 | 2018-04-14 13:00 | 13 | 7 | 33.1803 | 6.9679
2018-04-14 14:00 | 14 | 7 | 86.4439 | 18.2397 | 2018-04-14 14:00 | 14 | 7 | 0 | 0 | 2018-04-14 14:00 | 14 | 7 | 87.0832 | 18.4616 | 2018-04-14 14:00 | 14 | 7 | 33.0916 | 6.9492
2018-04-14 15:00 | 15 | 7 | 86.5522 | 18.2625 | 2018-04-14 15:00 | 15 | 7 | 0 | 0 | 2018-04-14 15:00 | 15 | 7 | 87.2938 | 18.5063 | 2018-04-14 15:00 | 15 | 7 | 33.1716 | 6.966
2018-04-14 16:00 | 16 | 7 | 86.5644 | 18.2651 | 2018-04-14 16:00 | 16 | 7 | 0 | 0 | 2018-04-14 16:00 | 16 | 7 | 87.3579 | 18.5199 | 2018-04-14 16:00 | 16 | 7 | 33.196 | 6.9712
2018-04-14 17:00 | 17 | 7 | 86.7445 | 18.3031 | 2018-04-14 17:00 | 17 | 7 | 0 | 0 | 2018-04-14 17:00 | 17 | 7 | 87.57 | 18.5648 | 2018-04-14 17:00 | 17 | 7 | 33.2766 | 6.9881
2018-04-14 18:00 | 18 | 7 | 86.4668 | 18.2445 | 2018-04-14 18:00 | 18 | 7 | 0 | 0 | 2018-04-14 18:00 | 18 | 7 | 87.3014 | 18.5079 | 2018-04-14 18:00 | 18 | 7 | 33.1745 | 6.9667
2018-04-14 19:00 | 19 | 7 | 86.3661 | 18.2232 | 2018-04-14 19:00 | 19 | 7 | 0 | 0 | 2018-04-14 19:00 | 19 | 7 | 87.0954 | 18.4642 | 2018-04-14 19:00 | 19 | 7 | 33.0963 | 6.9502
2018-04-14 20:00 | 20 | 7 | 86.1173 | 18.1708 | 2018-04-14 20:00 | 20 | 7 | 0 | 0 | 2018-04-14 20:00 | 20 | 7 | 86.891 | 18.4209 | 2018-04-14 20:00 | 20 | 7 | 33.0186 | 6.9339
2018-04-14 21:00 | 21 | 7 | 86.1555 | 18.1788 | 2018-04-14 21:00 | 21 | 7 | 0 | 0 | 2018-04-14 21:00 | 21 | 7 | 86.9245 | 18.428 | 2018-04-14 21:00 | 21 | 7 | 33.0313 | 6.9366
2018-04-14 22:00 | 22 | 7 | 86.2211 | 18.1927 | 2018-04-14 22:00 | 22 | 7 | 0 | 0 | 2018-04-14 22:00 | 22 | 7 | 87.0054 | 18.4451 | 2018-04-14 22:00 | 22 | 7 | 33.0621 | 6.943
2018-04-14 23:00 | 23 | 7 | 86.2226 | 18.193 | 2018-04-14 23:00 | 23 | 7 | 0 | 0 | 2018-04-14 23:00 | 23 | 7 | 87.0787 | 18.4607 | 2018-04-14 23:00 | 23 | 7 | 33.0899 | 6.9489
2018-04-15 | 0 | 1 | 86.2364 | 18.1959 | 2018-04-15 | 0 | 1 | 86.7994 | 17.681 | 2018-04-15 | 0 | 1 | 0 | 0 | 2018-04-15 | 0 | 1 | 32.9838 | 6.9266
2018-04-15 01:00 | 1 | 1 | 86.3188 | 18.2133 | 2018-04-15 01:00 | 1 | 1 | 86.952 | 17.7121 | 2018-04-15 01:00 | 1 | 1 | 0 | 0 | 2018-04-15 01:00 | 1 | 1 | 33.0418 | 6.9388
2018-04-15 02:00 | 2 | 1 | 86.2119 | 18.1907 | 2018-04-15 02:00 | 2 | 1 | 86.8177 | 17.6848 | 2018-04-15 02:00 | 2 | 1 | 0 | 0 | 2018-04-15 02:00 | 2 | 1 | 32.9907 | 6.9281
2018-04-15 03:00 | 3 | 1 | 86.1845 | 18.1849 | 2018-04-15 03:00 | 3 | 1 | 86.7857 | 17.6782 | 2018-04-15 03:00 | 3 | 1 | 0 | 0 | 2018-04-15 03:00 | 3 | 1 | 32.9786 | 6.9255
2018-04-15 04:00 | 4 | 1 | 86.2455 | 18.1978 | 2018-04-15 04:00 | 4 | 1 | 86.833 | 17.6879 | 2018-04-15 04:00 | 4 | 1 | 0 | 0 | 2018-04-15 04:00 | 4 | 1 | 32.9965 | 6.9293
2018-04-15 05:00 | 5 | 1 | 86.2333 | 18.1952 | 2018-04-15 05:00 | 5 | 1 | 86.833 | 17.6879 | 2018-04-15 05:00 | 5 | 1 | 0 | 0 | 2018-04-15 05:00 | 5 | 1 | 32.9965 | 6.9293
2018-04-15 06:00 | 6 | 1 | 86.2776 | 18.2046 | 2018-04-15 06:00 | 6 | 1 | 86.8528 | 17.6919 | 2018-04-15 06:00 | 6 | 1 | 0 | 0 | 2018-04-15 06:00 | 6 | 1 | 33.0041 | 6.9309
2018-04-15 07:00 | 7 | 1 | 86.2867 | 18.2065 | 2018-04-15 07:00 | 7 | 1 | 86.8452 | 17.6904 | 2018-04-15 07:00 | 7 | 1 | 0 | 0 | 2018-04-15 07:00 | 7 | 1 | 33.0012 | 6.9302
2018-04-15 08:00 | 8 | 1 | 86.2989 | 18.2091 | 2018-04-15 08:00 | 8 | 1 | 86.9032 | 17.7022 | 2018-04-15 08:00 | 8 | 1 | 0 | 0 | 2018-04-15 08:00 | 8 | 1 | 33.0232 | 6.9349
2018-04-15 09:00 | 9 | 1 | 86.2867 | 18.2065 | 2018-04-15 09:00 | 9 | 1 | 86.8162 | 17.6845 | 2018-04-15 09:00 | 9 | 1 | 0 | 0 | 2018-04-15 09:00 | 9 | 1 | 32.9902 | 6.9279
2018-04-15 10:00 | 10 | 1 | 86.2882 | 18.2068 | 2018-04-15 10:00 | 10 | 1 | 86.8528 | 17.6919 | 2018-04-15 10:00 | 10 | 1 | 0 | 0 | 2018-04-15 10:00 | 10 | 1 | 33.0041 | 6.9309
2018-04-15 11:00 | 11 | 1 | 86.1845 | 18.1849 | 2018-04-15 11:00 | 11 | 1 | 86.743 | 17.6695 | 2018-04-15 11:00 | 11 | 1 | 0 | 0 | 2018-04-15 11:00 | 11 | 1 | 32.9623 | 6.9221
2018-04-15 12:00 | 12 | 1 | 86.1418 | 18.1759 | 2018-04-15 12:00 | 12 | 1 | 86.714 | 17.6636 | 2018-04-15 12:00 | 12 | 1 | 0 | 0 | 2018-04-15 12:00 | 12 | 1 | 32.9513 | 6.9198
2018-04-15 13:00 | 13 | 1 | 86.1479 | 18.1772 | 2018-04-15 13:00 | 13 | 1 | 86.7659 | 17.6742 | 2018-04-15 13:00 | 13 | 1 | 0 | 0 | 2018-04-15 13:00 | 13 | 1 | 32.971 | 6.9239
2018-04-15 14:00 | 14 | 1 | 86.1112 | 18.1695 | 2018-04-15 14:00 | 14 | 1 | 86.7018 | 17.6612 | 2018-04-15 14:00 | 14 | 1 | 0 | 0 | 2018-04-15 14:00 | 14 | 1 | 32.9467 | 6.9188
2018-04-15 15:00 | 15 | 1 | 86.2455 | 18.1978 | 2018-04-15 15:00 | 15 | 1 | 86.8482 | 17.691 | 2018-04-15 15:00 | 15 | 1 | 0 | 0 | 2018-04-15 15:00 | 15 | 1 | 33.0023 | 6.9305
2018-04-15 16:00 | 16 | 1 | 86.3447 | 18.2187 | 2018-04-15 16:00 | 16 | 1 | 86.9398 | 17.7096 | 2018-04-15 16:00 | 16 | 1 | 0 | 0 | 2018-04-15 16:00 | 16 | 1 | 33.0371 | 6.9378
2018-04-15 17:00 | 17 | 1 | 86.4805 | 18.2474 | 2018-04-15 17:00 | 17 | 1 | 86.9856 | 17.719 | 2018-04-15 17:00 | 17 | 1 | 0 | 0 | 2018-04-15 17:00 | 17 | 1 | 33.0545 | 6.9415
2018-04-15 18:00 | 18 | 1 | 86.4332 | 18.2374 | 2018-04-15 18:00 | 18 | 1 | 86.92 | 17.7056 | 2018-04-15 18:00 | 18 | 1 | 0 | 0 | 2018-04-15 18:00 | 18 | 1 | 33.0296 | 6.9362
2018-04-15 19:00 | 19 | 1 | 85.6794 | 18.0784 | 2018-04-15 19:00 | 19 | 1 | 85.9266 | 17.5032 | 2018-04-15 19:00 | 19 | 1 | 0 | 0 | 2018-04-15 19:00 | 19 | 1 | 32.6521 | 6.8569
2018-04-15 20:00 | 20 | 1 | 86.3294 | 18.2155 | 2018-04-15 20:00 | 20 | 1 | 86.5888 | 17.6381 | 2018-04-15 20:00 | 20 | 1 | 0 | 0 | 2018-04-15 20:00 | 20 | 1 | 32.9037 | 6.9098
2018-04-15 21:00 | 21 | 1 | 86.3569 | 18.2213 | 2018-04-15 21:00 | 21 | 1 | 86.6728 | 17.6552 | 2018-04-15 21:00 | 21 | 1 | 0 | 0 | 2018-04-15 21:00 | 21 | 1 | 32.9357 | 6.9165
2018-04-15 22:00 | 22 | 1 | 86.4881 | 18.249 | 2018-04-15 22:00 | 22 | 1 | 86.8086 | 17.6829 | 2018-04-15 22:00 | 22 | 1 | 0 | 0 | 2018-04-15 22:00 | 22 | 1 | 32.9873 | 6.9273
2018-04-15 23:00 | 23 | 1 | 86.4332 | 18.2374 | 2018-04-15 23:00 | 23 | 1 | 86.7353 | 17.668 | 2018-04-15 23:00 | 23 | 1 | 0 | 0 | 2018-04-15 23:00 | 23 | 1 | 32.9594 | 6.9215
2018-04-16 | 0 | 2 | 86.4088 | 18.2323 | 2018-04-16 | 0 | 2 | 86.7002 | 17.6608 | 2018-04-16 | 0 | 2 | 86.9352 | 18.4303 | 2018-04-16 | 0 | 2 | 65.9815 | 13.8561
2018-04-16 01:00 | 1 | 2 | 86.0426 | 18.155 | 2018-04-16 01:00 | 1 | 2 | 86.3127 | 17.5819 | 2018-04-16 01:00 | 1 | 2 | 86.5278 | 18.3439 | 2018-04-16 01:00 | 1 | 2 | 65.6794 | 13.7927
2018-04-16 02:00 | 2 | 2 | 86.392 | 18.2287 | 2018-04-16 02:00 | 2 | 2 | 86.6392 | 17.6484 | 2018-04-16 02:00 | 2 | 2 | 86.8421 | 18.4105 | 2018-04-16 02:00 | 2 | 2 | 65.9229 | 13.8438
2018-04-16 03:00 | 3 | 2 | 86.2776 | 18.2046 | 2018-04-16 03:00 | 3 | 2 | 86.5766 | 17.6357 | 2018-04-16 03:00 | 3 | 2 | 86.7536 | 18.3918 | 2018-04-16 03:00 | 3 | 2 | 65.8655 | 13.8317
2018-04-16 04:00 | 4 | 2 | 86.5034 | 18.2522 | 2018-04-16 04:00 | 4 | 2 | 86.8849 | 17.6985 | 2018-04-16 04:00 | 4 | 2 | 87.0283 | 18.45 | 2018-04-16 04:00 | 4 | 2 | 66.087 | 13.8783
2018-04-16 05:00 | 5 | 2 | 86.3661 | 18.2232 | 2018-04-16 05:00 | 5 | 2 | 86.772 | 17.6755 | 2018-04-16 05:00 | 5 | 2 | 87.0054 | 18.4451 | 2018-04-16 05:00 | 5 | 2 | 66.0354 | 13.8674
2018-04-16 06:00 | 6 | 2 | 86.2898 | 18.2071 | 2018-04-16 06:00 | 6 | 2 | 86.6499 | 17.6506 | 2018-04-16 06:00 | 6 | 2 | 86.8147 | 18.4047 | 2018-04-16 06:00 | 6 | 2 | 65.9165 | 13.8425
2018-04-16 07:00 | 7 | 2 | 86.2043 | 18.1891 | 2018-04-16 07:00 | 7 | 2 | 86.5278 | 17.6257 | 2018-04-16 07:00 | 7 | 2 | 86.7079 | 18.3821 | 2018-04-16 07:00 | 7 | 2 | 65.8296 | 13.8242
2018-04-16 08:00 | 8 | 2 | 86.3355 | 18.2168 | 2018-04-16 08:00 | 8 | 2 | 86.5461 | 17.6294 | 2018-04-16 08:00 | 8 | 2 | 86.8025 | 18.4021 | 2018-04-16 08:00 | 8 | 2 | 65.8725 | 13.8332
2018-04-16 09:00 | 9 | 2 | 86.3798 | 18.2261 | 2018-04-16 09:00 | 9 | 2 | 86.7262 | 17.6661 | 2018-04-16 09:00 | 9 | 2 | 86.8711 | 18.4167 | 2018-04-16 09:00 | 9 | 2 | 65.967 | 13.8531
2018-04-16 10:00 | 10 | 2 | 86.2272 | 18.1939 | 2018-04-16 10:00 | 10 | 2 | 86.5156 | 17.6232 | 2018-04-16 10:00 | 10 | 2 | 86.714 | 18.3834 | 2018-04-16 10:00 | 10 | 2 | 65.8272 | 13.8237
2018-04-16 11:00 | 11 | 2 | 86.2119 | 18.1907 | 2018-04-16 11:00 | 11 | 2 | 86.5141 | 17.6229 | 2018-04-16 11:00 | 11 | 2 | 86.7201 | 18.3847 | 2018-04-16 11:00 | 11 | 2 | 65.829 | 13.8241
2018-04-16 12:00 | 12 | 2 | 86.389 | 18.2281 | 2018-04-16 12:00 | 12 | 2 | 86.6835 | 17.6574 | 2018-04-16 12:00 | 12 | 2 | 86.8574 | 18.4138 | 2018-04-16 12:00 | 12 | 2 | 65.9455 | 13.8486
2018-04-16 13:00 | 13 | 2 | 86.4027 | 18.231 | 2018-04-16 13:00 | 13 | 2 | 86.6224 | 17.645 | 2018-04-16 13:00 | 13 | 2 | 86.7475 | 18.3905 | 2018-04-16 13:00 | 13 | 2 | 65.8806 | 13.8349
2018-04-16 14:00 | 14 | 2 | 86.3783 | 18.2258 | 2018-04-16 14:00 | 14 | 2 | 86.6606 | 17.6528 | 2018-04-16 14:00 | 14 | 2 | 86.7903 | 18.3995 | 2018-04-16 14:00 | 14 | 2 | 65.9113 | 13.8414
2018-04-16 15:00 | 15 | 2 | 86.3355 | 18.2168 | 2018-04-16 15:00 | 15 | 2 | 86.5248 | 17.6251 | 2018-04-16 15:00 | 15 | 2 | 86.7384 | 18.3885 | 2018-04-16 15:00 | 15 | 2 | 65.84 | 13.8264
2018-04-16 16:00 | 16 | 2 | 86.3493 | 18.2197 | 2018-04-16 16:00 | 16 | 2 | 86.4912 | 17.6183 | 2018-04-16 16:00 | 16 | 2 | 86.685 | 18.3772 | 2018-04-16 16:00 | 16 | 2 | 65.807 | 13.8195
2018-04-16 17:00 | 17 | 2 | 86.244 | 18.1975 | 2018-04-16 17:00 | 17 | 2 | 86.4683 | 17.6136 | 2018-04-16 17:00 | 17 | 2 | 86.6743 | 18.375 | 2018-04-16 17:00 | 17 | 2 | 65.7942 | 13.8168
2018-04-16 18:00 | 18 | 2 | 86.3142 | 18.2123 | 2018-04-16 18:00 | 18 | 2 | 86.4378 | 17.6074 | 2018-04-16 18:00 | 18 | 2 | 86.5934 | 18.3578 | 2018-04-16 18:00 | 18 | 2 | 65.7519 | 13.8079
2018-04-16 19:00 | 19 | 2 | 86.2089 | 18.1901 | 2018-04-16 19:00 | 19 | 2 | 86.3508 | 17.5897 | 2018-04-16 19:00 | 19 | 2 | 86.5583 | 18.3504 | 2018-04-16 19:00 | 19 | 2 | 65.7055 | 13.7981
2018-04-16 20:00 | 20 | 2 | 86.2181 | 18.192 | 2018-04-16 20:00 | 20 | 2 | 86.4836 | 17.6167 | 2018-04-16 20:00 | 20 | 2 | 86.6896 | 18.3782 | 2018-04-16 20:00 | 20 | 2 | 65.8058 | 13.8192
2018-04-16 21:00 | 21 | 2 | 86.1494 | 18.1775 | 2018-04-16 21:00 | 21 | 2 | 86.4759 | 17.6151 | 2018-04-16 21:00 | 21 | 2 | 86.63 | 18.3656 | 2018-04-16 21:00 | 21 | 2 | 65.7802 | 13.8139
2018-04-16 22:00 | 22 | 2 | 86.2593 | 18.2007 | 2018-04-16 22:00 | 22 | 2 | 86.5522 | 17.6307 | 2018-04-16 22:00 | 22 | 2 | 86.6468 | 18.3691 | 2018-04-16 22:00 | 22 | 2 | 65.8156 | 13.8213
2018-04-16 23:00 | 23 | 2 | 86.4424 | 18.2393 | 2018-04-16 23:00 | 23 | 2 | 86.8055 | 17.6823 | 2018-04-16 23:00 | 23 | 2 | 86.8864 | 18.4199 | 2018-04-16 23:00 | 23 | 2 | 66.0029 | 13.8606
2018-04-17 | 0 | 3 | 86.4637 | 18.2438 | 2018-04-17 | 0 | 3 | 0 | 0 | 2018-04-17 | 0 | 3 | 0 | 0 | 2018-04-17 | 0 | 3 | 0 | 0
2018-04-17 01:00 | 1 | 3 | 86.5629 | 18.2648 | 2018-04-17 01:00 | 1 | 3 | 0 | 0 | 2018-04-17 01:00 | 1 | 3 | 0 | 0 | 2018-04-17 01:00 | 1 | 3 | 0 | 0
2018-04-17 02:00 | 2 | 3 | 86.3706 | 18.2242 | 2018-04-17 02:00 | 2 | 3 | 0 | 0 | 2018-04-17 02:00 | 2 | 3 | 0 | 0 | 2018-04-17 02:00 | 2 | 3 | 0 | 0
2018-04-17 03:00 | 3 | 3 | 86.3523 | 18.2203 | 2018-04-17 03:00 | 3 | 3 | 0 | 0 | 2018-04-17 03:00 | 3 | 3 | 0 | 0 | 2018-04-17 03:00 | 3 | 3 | 0 | 0
2018-04-17 04:00 | 4 | 3 | 86.3676 | 18.2236 | 2018-04-17 04:00 | 4 | 3 | 0 | 0 | 2018-04-17 04:00 | 4 | 3 | 0 | 0 | 2018-04-17 04:00 | 4 | 3 | 0 | 0
2018-04-17 05:00 | 5 | 3 | 86.4027 | 18.231 | 2018-04-17 05:00 | 5 | 3 | 0 | 0 | 2018-04-17 05:00 | 5 | 3 | 0 | 0 | 2018-04-17 05:00 | 5 | 3 | 0 | 0
2018-04-17 06:00 | 6 | 3 | 86.4652 | 18.2442 | 2018-04-17 06:00 | 6 | 3 | 0 | 0 | 2018-04-17 06:00 | 6 | 3 | 0 | 0 | 2018-04-17 06:00 | 6 | 3 | 0 | 0
2018-04-17 07:00 | 7 | 3 | 86.4012 | 18.2307 | 2018-04-17 07:00 | 7 | 3 | 0 | 0 | 2018-04-17 07:00 | 7 | 3 | 0 | 0 | 2018-04-17 07:00 | 7 | 3 | 0 | 0
2018-04-17 08:00 | 8 | 3 | 86.4515 | 18.2413 | 2018-04-17 08:00 | 8 | 3 | 0 | 0 | 2018-04-17 08:00 | 8 | 3 | 0 | 0 | 2018-04-17 08:00 | 8 | 3 | 0 | 0
2018-04-17 09:00 | 9 | 3 | 86.2028 | 18.1888 | 2018-04-17 09:00 | 9 | 3 | 0 | 0 | 2018-04-17 09:00 | 9 | 3 | 0 | 0 | 2018-04-17 09:00 | 9 | 3 | 0 | 0
2018-04-17 10:00 | 10 | 3 | 86.2715 | 18.2033 | 2018-04-17 10:00 | 10 | 3 | 0 | 0 | 2018-04-17 10:00 | 10 | 3 | 0 | 0 | 2018-04-17 10:00 | 10 | 3 | 0 | 0
2018-04-17 11:00 | 11 | 3 | 86.7567 | 18.3057 | 2018-04-17 11:00 | 11 | 3 | 0 | 0 | 2018-04-17 11:00 | 11 | 3 | 0 | 0 | 2018-04-17 11:00 | 11 | 3 | 0 | 0
2018-04-17 12:00 | 12 | 3 | 86.6194 | 18.2767 | 2018-04-17 12:00 | 12 | 3 | 0 | 0 | 2018-04-17 12:00 | 12 | 3 | 0 | 0 | 2018-04-17 12:00 | 12 | 3 | 0 | 0
2018-04-17 13:00 | 13 | 3 | 86.6377 | 18.2806 | 2018-04-17 13:00 | 13 | 3 | 0 | 0 | 2018-04-17 13:00 | 13 | 3 | 0 | 0 | 2018-04-17 13:00 | 13 | 3 | 0 | 0
2018-04-17 14:00 | 14 | 3 | 86.8757 | 18.3308 | 2018-04-17 14:00 | 14 | 3 | 0 | 0 | 2018-04-17 14:00 | 14 | 3 | 0 | 0 | 2018-04-17 14:00 | 14 | 3 | 0 | 0
2018-04-17 15:00 | 15 | 3 | 86.7994 | 18.3147 | 2018-04-17 15:00 | 15 | 3 | 0 | 0 | 2018-04-17 15:00 | 15 | 3 | 0 | 0 | 2018-04-17 15:00 | 15 | 3 | 0 | 0
2018-04-17 16:00 | 16 | 3 | 86.7674 | 18.3079 | 2018-04-17 16:00 | 16 | 3 | 0 | 0 | 2018-04-17 16:00 | 16 | 3 | 0 | 0 | 2018-04-17 16:00 | 16 | 3 | 0 | 0
2018-04-17 17:00 | 17 | 3 | 86.7384 | 18.3018 | 2018-04-17 17:00 | 17 | 3 | 0 | 0 | 2018-04-17 17:00 | 17 | 3 | 0 | 0 | 2018-04-17 17:00 | 17 | 3 | 0 | 0
2018-04-17 18:00 | 18 | 3 | 86.7124 | 18.2963 | 2018-04-17 18:00 | 18 | 3 | 0 | 0 | 2018-04-17 18:00 | 18 | 3 | 0 | 0 | 2018-04-17 18:00 | 18 | 3 | 0 | 0
2018-04-17 19:00 | 19 | 3 | 86.8376 | 18.3227 | 2018-04-17 19:00 | 19 | 3 | 0 | 0 | 2018-04-17 19:00 | 19 | 3 | 0 | 0 | 2018-04-17 19:00 | 19 | 3 | 0 | 0
2018-04-17 20:00 | 20 | 3 | 86.627 | 18.2783 | 2018-04-17 20:00 | 20 | 3 | 0 | 0 | 2018-04-17 20:00 | 20 | 3 | 0 | 0 | 2018-04-17 20:00 | 20 | 3 | 0 | 0
2018-04-17 21:00 | 21 | 3 | 86.6239 | 18.2776 | 2018-04-17 21:00 | 21 | 3 | 0 | 0 | 2018-04-17 21:00 | 21 | 3 | 0 | 0 | 2018-04-17 21:00 | 21 | 3 | 0 | 0
2018-04-17 22:00 | 22 | 3 | 86.714 | 18.2967 | 2018-04-17 22:00 | 22 | 3 | 0 | 0 | 2018-04-17 22:00 | 22 | 3 | 0 | 0 | 2018-04-17 22:00 | 22 | 3 | 0 | 0
2018-04-17 23:00 | 23 | 3 | 86.8971 | 18.3353 | 2018-04-17 23:00 | 23 | 3 | 0 | 0 | 2018-04-17 23:00 | 23 | 3 | 0 | 0 | 2018-04-17 23:00 | 23 | 3 | 0 | 0
2018-04-18 | 0 | 4 | 0 | 0 | 2018-04-18 | 0 | 4 | 0 | 0 | 2018-04-18 | 0 | 4 | 86.6712 | 18.3743 | 2018-04-18 | 0 | 4 | 32.9351 | 6.9164
2018-04-18 01:00 | 1 | 4 | 0 | 0 | 2018-04-18 01:00 | 1 | 4 | 0 | 0 | 2018-04-18 01:00 | 1 | 4 | 86.511 | 18.3403 | 2018-04-18 01:00 | 1 | 4 | 32.8742 | 6.9036
2018-04-18 02:00 | 2 | 4 | 0 | 0 | 2018-04-18 02:00 | 2 | 4 | 0 | 0 | 2018-04-18 02:00 | 2 | 4 | 86.7628 | 18.3937 | 2018-04-18 02:00 | 2 | 4 | 32.9699 | 6.9237
2018-04-18 03:00 | 3 | 4 | 0 | 0 | 2018-04-18 03:00 | 3 | 4 | 0 | 0 | 2018-04-18 03:00 | 3 | 4 | 86.7384 | 18.3885 | 2018-04-18 03:00 | 3 | 4 | 32.9606 | 6.9217
2018-04-18 04:00 | 4 | 4 | 0 | 0 | 2018-04-18 04:00 | 4 | 4 | 0 | 0 | 2018-04-18 04:00 | 4 | 4 | 86.8376 | 18.4096 | 2018-04-18 04:00 | 4 | 4 | 32.9983 | 6.9296
2018-04-18 05:00 | 5 | 4 | 0 | 0 | 2018-04-18 05:00 | 5 | 4 | 0 | 0 | 2018-04-18 05:00 | 5 | 4 | 87.0222 | 18.4487 | 2018-04-18 05:00 | 5 | 4 | 33.0684 | 6.9444
2018-04-18 06:00 | 6 | 4 | 0 | 0 | 2018-04-18 06:00 | 6 | 4 | 0 | 0 | 2018-04-18 06:00 | 6 | 4 | 86.9627 | 18.4361 | 2018-04-18 06:00 | 6 | 4 | 33.0458 | 6.9396
2018-04-18 07:00 | 7 | 4 | 0 | 0 | 2018-04-18 07:00 | 7 | 4 | 0 | 0 | 2018-04-18 07:00 | 7 | 4 | 87.1321 | 18.472 | 2018-04-18 07:00 | 7 | 4 | 33.1102 | 6.9531
2018-04-18 08:00 | 8 | 4 | 0 | 0 | 2018-04-18 08:00 | 8 | 4 | 0 | 0 | 2018-04-18 08:00 | 8 | 4 | 87.1931 | 18.4849 | 2018-04-18 08:00 | 8 | 4 | 33.1334 | 6.958
2018-04-18 09:00 | 9 | 4 | 0 | 0 | 2018-04-18 09:00 | 9 | 4 | 0 | 0 | 2018-04-18 09:00 | 9 | 4 | 86.7155 | 18.3837 | 2018-04-18 09:00 | 9 | 4 | 32.9519 | 6.9199
2018-04-18 10:00 | 10 | 4 | 0 | 0 | 2018-04-18 10:00 | 10 | 4 | 0 | 0 | 2018-04-18 10:00 | 10 | 4 | 86.6743 | 18.375 | 2018-04-18 10:00 | 10 | 4 | 32.9362 | 6.9166
2018-04-18 11:00 | 11 | 4 | 0 | 0 | 2018-04-18 11:00 | 11 | 4 | 0 | 0 | 2018-04-18 11:00 | 11 | 4 | 86.8956 | 18.4219 | 2018-04-18 11:00 | 11 | 4 | 33.0203 | 6.9343
2018-04-18 12:00 | 12 | 4 | 0 | 0 | 2018-04-18 12:00 | 12 | 4 | 0 | 0 | 2018-04-18 12:00 | 12 | 4 | 86.9276 | 18.4287 | 2018-04-18 12:00 | 12 | 4 | 33.0325 | 6.9368
2018-04-18 13:00 | 13 | 4 | 0 | 0 | 2018-04-18 13:00 | 13 | 4 | 0 | 0 | 2018-04-18 13:00 | 13 | 4 | 87.2541 | 18.4979 | 2018-04-18 13:00 | 13 | 4 | 33.1566 | 6.9629
2018-04-18 14:00 | 14 | 4 | 0 | 0 | 2018-04-18 14:00 | 14 | 4 | 0 | 0 | 2018-04-18 14:00 | 14 | 4 | 87.4037 | 18.5296 | 2018-04-18 14:00 | 14 | 4 | 33.2134 | 6.9748
2018-04-18 15:00 | 15 | 4 | 0 | 0 | 2018-04-18 15:00 | 15 | 4 | 0 | 0 | 2018-04-18 15:00 | 15 | 4 | 87.2129 | 18.4891 | 2018-04-18 15:00 | 15 | 4 | 33.1409 | 6.9596
2018-04-18 16:00 | 16 | 4 | 0 | 0 | 2018-04-18 16:00 | 16 | 4 | 0 | 0 | 2018-04-18 16:00 | 16 | 4 | 86.9718 | 18.438 | 2018-04-18 16:00 | 16 | 4 | 33.0493 | 6.9403
2018-04-18 17:00 | 17 | 4 | 0 | 0 | 2018-04-18 17:00 | 17 | 4 | 0 | 0 | 2018-04-18 17:00 | 17 | 4 | 87.1397 | 18.4736 | 2018-04-18 17:00 | 17 | 4 | 33.1131 | 6.9537
2018-04-18 18:00 | 18 | 4 | 0 | 0 | 2018-04-18 18:00 | 18 | 4 | 0 | 0 | 2018-04-18 18:00 | 18 | 4 | 87.2435 | 18.4956 | 2018-04-18 18:00 | 18 | 4 | 33.1525 | 6.962
2018-04-18 19:00 | 19 | 4 | 0 | 0 | 2018-04-18 19:00 | 19 | 4 | 0 | 0 | 2018-04-18 19:00 | 19 | 4 | 86.8894 | 18.4206 | 2018-04-18 19:00 | 19 | 4 | 33.018 | 6.9338
2018-04-18 20:00 | 20 | 4 | 0 | 0 | 2018-04-18 20:00 | 20 | 4 | 0 | 0 | 2018-04-18 20:00 | 20 | 4 | 87.1839 | 18.483 | 2018-04-18 20:00 | 20 | 4 | 33.1299 | 6.9573
2018-04-18 21:00 | 21 | 4 | 0 | 0 | 2018-04-18 21:00 | 21 | 4 | 0 | 0 | 2018-04-18 21:00 | 21 | 4 | 87.2419 | 18.4953 | 2018-04-18 21:00 | 21 | 4 | 33.1519 | 6.9619
2018-04-18 22:00 | 22 | 4 | 0 | 0 | 2018-04-18 22:00 | 22 | 4 | 0 | 0 | 2018-04-18 22:00 | 22 | 4 | 87.1733 | 18.4807 | 2018-04-18 22:00 | 22 | 4 | 33.1259 | 6.9564
2018-04-18 23:00 | 23 | 4 | 0 | 0 | 2018-04-18 23:00 | 23 | 4 | 0 | 0 | 2018-04-18 23:00 | 23 | 4 | 87.2557 | 18.4982 | 2018-04-18 23:00 | 23 | 4 | 33.1572 | 6.963
2018-04-19 | 0 | 5 | 86.5492 | 18.2619 | 2018-04-19 | 0 | 5 | 0 | 0 | 2018-04-19 | 0 | 5 | 0 | 0 | 2018-04-19 | 0 | 5 | 0 | 0
2018-04-19 01:00 | 1 | 5 | 86.7201 | 18.2979 | 2018-04-19 01:00 | 1 | 5 | 0 | 0 | 2018-04-19 01:00 | 1 | 5 | 0 | 0 | 2018-04-19 01:00 | 1 | 5 | 0 | 0
2018-04-19 02:00 | 2 | 5 | 86.5095 | 18.2535 | 2018-04-19 02:00 | 2 | 5 | 0 | 0 | 2018-04-19 02:00 | 2 | 5 | 0 | 0 | 2018-04-19 02:00 | 2 | 5 | 0 | 0
2018-04-19 03:00 | 3 | 5 | 86.4576 | 18.2426 | 2018-04-19 03:00 | 3 | 5 | 0 | 0 | 2018-04-19 03:00 | 3 | 5 | 0 | 0 | 2018-04-19 03:00 | 3 | 5 | 0 | 0
2018-04-19 04:00 | 4 | 5 | 86.6316 | 18.2793 | 2018-04-19 04:00 | 4 | 5 | 0 | 0 | 2018-04-19 04:00 | 4 | 5 | 0 | 0 | 2018-04-19 04:00 | 4 | 5 | 0 | 0
2018-04-19 05:00 | 5 | 5 | 86.569 | 18.2661 | 2018-04-19 05:00 | 5 | 5 | 0 | 0 | 2018-04-19 05:00 | 5 | 5 | 0 | 0 | 2018-04-19 05:00 | 5 | 5 | 0 | 0
2018-04-19 06:00 | 6 | 5 | 86.6468 | 18.2825 | 2018-04-19 06:00 | 6 | 5 | 0 | 0 | 2018-04-19 06:00 | 6 | 5 | 0 | 0 | 2018-04-19 06:00 | 6 | 5 | 0 | 0
2018-04-19 07:00 | 7 | 5 | 86.6361 | 18.2802 | 2018-04-19 07:00 | 7 | 5 | 0 | 0 | 2018-04-19 07:00 | 7 | 5 | 0 | 0 | 2018-04-19 07:00 | 7 | 5 | 0 | 0
2018-04-19 08:00 | 8 | 5 | 86.6819 | 18.2899 | 2018-04-19 08:00 | 8 | 5 | 0 | 0 | 2018-04-19 08:00 | 8 | 5 | 0 | 0 | 2018-04-19 08:00 | 8 | 5 | 0 | 0
2018-04-19 09:00 | 9 | 5 | 86.7094 | 18.2957 | 2018-04-19 09:00 | 9 | 5 | 0 | 0 | 2018-04-19 09:00 | 9 | 5 | 0 | 0 | 2018-04-19 09:00 | 9 | 5 | 0 | 0
2018-04-19 10:00 | 10 | 5 | 86.7933 | 18.3134 | 2018-04-19 10:00 | 10 | 5 | 0 | 0 | 2018-04-19 10:00 | 10 | 5 | 0 | 0 | 2018-04-19 10:00 | 10 | 5 | 0 | 0
2018-04-19 11:00 | 11 | 5 | 86.8009 | 18.315 | 2018-04-19 11:00 | 11 | 5 | 0 | 0 | 2018-04-19 11:00 | 11 | 5 | 0 | 0 | 2018-04-19 11:00 | 11 | 5 | 0 | 0
2018-04-19 12:00 | 12 | 5 | 86.6728 | 18.288 | 2018-04-19 12:00 | 12 | 5 | 0 | 0 | 2018-04-19 12:00 | 12 | 5 | 0 | 0 | 2018-04-19 12:00 | 12 | 5 | 0 | 0
2018-04-19 13:00 | 13 | 5 | 86.6316 | 18.2793 | 2018-04-19 13:00 | 13 | 5 | 0 | 0 | 2018-04-19 13:00 | 13 | 5 | 0 | 0 | 2018-04-19 13:00 | 13 | 5 | 0 | 0
2018-04-19 14:00 | 14 | 5 | 86.6316 | 18.2793 | 2018-04-19 14:00 | 14 | 5 | 0 | 0 | 2018-04-19 14:00 | 14 | 5 | 0 | 0 | 2018-04-19 14:00 | 14 | 5 | 0 | 0
2018-04-19 15:00 | 15 | 5 | 86.6636 | 18.286 | 2018-04-19 15:00 | 15 | 5 | 0 | 0 | 2018-04-19 15:00 | 15 | 5 | 0 | 0 | 2018-04-19 15:00 | 15 | 5 | 0 | 0
2018-04-19 16:00 | 16 | 5 | 86.5568 | 18.2635 | 2018-04-19 16:00 | 16 | 5 | 0 | 0 | 2018-04-19 16:00 | 16 | 5 | 0 | 0 | 2018-04-19 16:00 | 16 | 5 | 0 | 0
2018-04-19 17:00 | 17 | 5 | 86.6865 | 18.2909 | 2018-04-19 17:00 | 17 | 5 | 0 | 0 | 2018-04-19 17:00 | 17 | 5 | 0 | 0 | 2018-04-19 17:00 | 17 | 5 | 0 | 0
2018-04-19 18:00 | 18 | 5 | 86.7262 | 18.2992 | 2018-04-19 18:00 | 18 | 5 | 0 | 0 | 2018-04-19 18:00 | 18 | 5 | 0 | 0 | 2018-04-19 18:00 | 18 | 5 | 0 | 0
2018-04-19 19:00 | 19 | 5 | 86.5187 | 18.2554 | 2018-04-19 19:00 | 19 | 5 | 0 | 0 | 2018-04-19 19:00 | 19 | 5 | 0 | 0 | 2018-04-19 19:00 | 19 | 5 | 0 | 0
2018-04-19 20:00 | 20 | 5 | 86.5766 | 18.2677 | 2018-04-19 20:00 | 20 | 5 | 0 | 0 | 2018-04-19 20:00 | 20 | 5 | 0 | 0 | 2018-04-19 20:00 | 20 | 5 | 0 | 0
2018-04-19 21:00 | 21 | 5 | 86.6194 | 18.2767 | 2018-04-19 21:00 | 21 | 5 | 0 | 0 | 2018-04-19 21:00 | 21 | 5 | 0 | 0 | 2018-04-19 21:00 | 21 | 5 | 0 | 0
2018-04-19 22:00 | 22 | 5 | 86.6743 | 18.2883 | 2018-04-19 22:00 | 22 | 5 | 0 | 0 | 2018-04-19 22:00 | 22 | 5 | 0 | 0 | 2018-04-19 22:00 | 22 | 5 | 0 | 0
2018-04-19 23:00 | 23 | 5 | 86.5644 | 18.2651 | 2018-04-19 23:00 | 23 | 5 | 0 | 0 | 2018-04-19 23:00 | 23 | 5 | 0 | 0 | 2018-04-19 23:00 | 23 | 5 | 0 | 0
2018-04-20 | 0 | 6 | 86.2226 | 18.193 | 2018-04-20 | 0 | 6 | 86.688 | 17.6583 | 2018-04-20 | 0 | 6 | 0 | 0 | 2018-04-20 | 0 | 6 | 32.9414 | 6.9177
2018-04-20 01:00 | 1 | 6 | 86.1128 | 18.1698 | 2018-04-20 01:00 | 1 | 6 | 86.5232 | 17.6248 | 2018-04-20 01:00 | 1 | 6 | 0 | 0 | 2018-04-20 01:00 | 1 | 6 | 32.8788 | 6.9046
2018-04-20 02:00 | 2 | 6 | 86.2791 | 18.2049 | 2018-04-20 02:00 | 2 | 6 | 86.6896 | 17.6587 | 2018-04-20 02:00 | 2 | 6 | 0 | 0 | 2018-04-20 02:00 | 2 | 6 | 32.942 | 6.9178
2018-04-20 03:00 | 3 | 6 | 86.0014 | 18.1463 | 2018-04-20 03:00 | 3 | 6 | 86.4485 | 17.6096 | 2018-04-20 03:00 | 3 | 6 | 0 | 0 | 2018-04-20 03:00 | 3 | 6 | 32.8504 | 6.8986
2018-04-20 04:00 | 4 | 6 | 86.0533 | 18.1572 | 2018-04-20 04:00 | 4 | 6 | 86.4347 | 17.6067 | 2018-04-20 04:00 | 4 | 6 | 0 | 0 | 2018-04-20 04:00 | 4 | 6 | 32.8452 | 6.8975
2018-04-20 05:00 | 5 | 6 | 86.2257 | 18.1936 | 2018-04-20 05:00 | 5 | 6 | 86.6117 | 17.6428 | 2018-04-20 05:00 | 5 | 6 | 0 | 0 | 2018-04-20 05:00 | 5 | 6 | 32.9124 | 6.9116
2018-04-20 06:00 | 6 | 6 | 86.4332 | 18.2374 | 2018-04-20 06:00 | 6 | 6 | 86.9352 | 17.7087 | 2018-04-20 06:00 | 6 | 6 | 0 | 0 | 2018-04-20 06:00 | 6 | 6 | 33.0354 | 6.9374
2018-04-20 07:00 | 7 | 6 | 86.5873 | 18.2699 | 2018-04-20 07:00 | 7 | 6 | 87.0619 | 17.7345 | 2018-04-20 07:00 | 7 | 6 | 0 | 0 | 2018-04-20 07:00 | 7 | 6 | 33.0835 | 6.9475
2018-04-20 08:00 | 8 | 6 | 86.3691 | 18.2239 | 2018-04-20 08:00 | 8 | 6 | 86.7811 | 17.6773 | 2018-04-20 08:00 | 8 | 6 | 0 | 0 | 2018-04-20 08:00 | 8 | 6 | 32.9768 | 6.9251
2018-04-20 09:00 | 9 | 6 | 86.334 | 18.2165 | 2018-04-20 09:00 | 9 | 6 | 86.7399 | 17.6689 | 2018-04-20 09:00 | 9 | 6 | 0 | 0 | 2018-04-20 09:00 | 9 | 6 | 32.9612 | 6.9218
2018-04-20 10:00 | 10 | 6 | 86.5126 | 18.2542 | 2018-04-20 10:00 | 10 | 6 | 86.862 | 17.6938 | 2018-04-20 10:00 | 10 | 6 | 0 | 0 | 2018-04-20 10:00 | 10 | 6 | 33.0076 | 6.9316
2018-04-20 11:00 | 11 | 6 | 86.5003 | 18.2516 | 2018-04-20 11:00 | 11 | 6 | 86.9306 | 17.7078 | 2018-04-20 11:00 | 11 | 6 | 0 | 0 | 2018-04-20 11:00 | 11 | 6 | 33.0336 | 6.9371
2018-04-20 12:00 | 12 | 6 | 86.7002 | 18.2937 | 2018-04-20 12:00 | 12 | 6 | 87.1412 | 17.7507 | 2018-04-20 12:00 | 12 | 6 | 0 | 0 | 2018-04-20 12:00 | 12 | 6 | 33.1137 | 6.9539
2018-04-20 13:00 | 13 | 6 | 86.363 | 18.2226 | 2018-04-20 13:00 | 13 | 6 | 86.8009 | 17.6813 | 2018-04-20 13:00 | 13 | 6 | 0 | 0 | 2018-04-20 13:00 | 13 | 6 | 32.9843 | 6.9267
2018-04-20 14:00 | 14 | 6 | 86.4408 | 18.239 | 2018-04-20 14:00 | 14 | 6 | 86.8635 | 17.6941 | 2018-04-20 14:00 | 14 | 6 | 0 | 0 | 2018-04-20 14:00 | 14 | 6 | 33.0081 | 6.9317
2018-04-20 15:00 | 15 | 6 | 86.2943 | 18.2081 | 2018-04-20 15:00 | 15 | 6 | 86.6743 | 17.6556 | 2018-04-20 15:00 | 15 | 6 | 0 | 0 | 2018-04-20 15:00 | 15 | 6 | 32.9362 | 6.9166
2018-04-20 16:00 | 16 | 6 | 86.3706 | 18.2242 | 2018-04-20 16:00 | 16 | 6 | 86.7491 | 17.6708 | 2018-04-20 16:00 | 16 | 6 | 0 | 0 | 2018-04-20 16:00 | 16 | 6 | 32.9647 | 6.9226
2018-04-20 17:00 | 17 | 6 | 86.2882 | 18.2068 | 2018-04-20 17:00 | 17 | 6 | 86.7445 | 17.6699 | 2018-04-20 17:00 | 17 | 6 | 0 | 0 | 2018-04-20 17:00 | 17 | 6 | 32.9629 | 6.9222
2018-04-20 18:00 | 18 | 6 | 86.1875 | 18.1856 | 2018-04-20 18:00 | 18 | 6 | 86.6667 | 17.654 | 2018-04-20 18:00 | 18 | 6 | 0 | 0 | 2018-04-20 18:00 | 18 | 6 | 32.9333 | 6.916
2018-04-20 19:00 | 19 | 6 | 86.099 | 18.1669 | 2018-04-20 19:00 | 19 | 6 | 86.5431 | 17.6288 | 2018-04-20 19:00 | 19 | 6 | 0 | 0 | 2018-04-20 19:00 | 19 | 6 | 32.8864 | 6.9061
2018-04-20 20:00 | 20 | 6 | 86.1997 | 18.1881 | 2018-04-20 20:00 | 20 | 6 | 86.5187 | 17.6239 | 2018-04-20 20:00 | 20 | 6 | 0 | 0 | 2018-04-20 20:00 | 20 | 6 | 32.8771 | 6.9042
2018-04-20 21:00 | 21 | 6 | 86.3767 | 18.2255 | 2018-04-20 21:00 | 21 | 6 | 86.7247 | 17.6658 | 2018-04-20 21:00 | 21 | 6 | 0 | 0 | 2018-04-20 21:00 | 21 | 6 | 32.9554 | 6.9206
2018-04-20 22:00 | 22 | 6 | 86.3691 | 18.2239 | 2018-04-20 22:00 | 22 | 6 | 86.7659 | 17.6742 | 2018-04-20 22:00 | 22 | 6 | 0 | 0 | 2018-04-20 22:00 | 22 | 6 | 32.971 | 6.9239
2018-04-20 23:00 | 23 | 6 | 86.4012 | 18.2307 | 2018-04-20 23:00 | 23 | 6 | 86.7918 | 17.6795 | 2018-04-20 23:00 | 23 | 6 | 0 | 0 | 2018-04-20 23:00 | 23 | 6 | 32.9809 | 6.926
2018-04-21 | 0 | 7 | 86.0121 | 18.1486 | 2018-04-21 | 0 | 7 | 0 | 0 | 2018-04-21 | 0 | 7 | 86.5507 | 18.3487 | 2018-04-21 | 0 | 7 | 32.8893 | 6.9067
2018-04-21 01:00 | 1 | 7 | 85.919 | 18.1289 | 2018-04-21 01:00 | 1 | 7 | 0 | 0 | 2018-04-21 01:00 | 1 | 7 | 86.5324 | 18.3449 | 2018-04-21 01:00 | 1 | 7 | 32.8823 | 6.9053
2018-04-21 02:00 | 2 | 7 | 86.0533 | 18.1572 | 2018-04-21 02:00 | 2 | 7 | 0 | 0 | 2018-04-21 02:00 | 2 | 7 | 86.6453 | 18.3688 | 2018-04-21 02:00 | 2 | 7 | 32.9252 | 6.9143
2018-04-21 03:00 | 3 | 7 | 86.1677 | 18.1814 | 2018-04-21 03:00 | 3 | 7 | 0 | 0 | 2018-04-21 03:00 | 3 | 7 | 86.7002 | 18.3804 | 2018-04-21 03:00 | 3 | 7 | 32.9461 | 6.9187
2018-04-21 04:00 | 4 | 7 | 86.3081 | 18.211 | 2018-04-21 04:00 | 4 | 7 | 0 | 0 | 2018-04-21 04:00 | 4 | 7 | 86.8513 | 18.4125 | 2018-04-21 04:00 | 4 | 7 | 33.0035 | 6.9307
2018-04-21 05:00 | 5 | 7 | 86.2562 | 18.2001 | 2018-04-21 05:00 | 5 | 7 | 0 | 0 | 2018-04-21 05:00 | 5 | 7 | 86.8605 | 18.4144 | 2018-04-21 05:00 | 5 | 7 | 33.007 | 6.9315
2018-04-21 06:00 | 6 | 7 | 86.1234 | 18.172 | 2018-04-21 06:00 | 6 | 7 | 0 | 0 | 2018-04-21 06:00 | 6 | 7 | 86.6682 | 18.3737 | 2018-04-21 06:00 | 6 | 7 | 32.9339 | 6.9161
2018-04-21 07:00 | 7 | 7 | 86.1906 | 18.1862 | 2018-04-21 07:00 | 7 | 7 | 0 | 0 | 2018-04-21 07:00 | 7 | 7 | 86.7247 | 18.3856 | 2018-04-21 07:00 | 7 | 7 | 32.9554 | 6.9206
2018-04-21 08:00 | 8 | 7 | 86.36 | 18.222 | 2018-04-21 08:00 | 8 | 7 | 0 | 0 | 2018-04-21 08:00 | 8 | 7 | 86.952 | 18.4338 | 2018-04-21 08:00 | 8 | 7 | 33.0418 | 6.9388
2018-04-21 09:00 | 9 | 7 | 86.4912 | 18.2496 | 2018-04-21 09:00 | 9 | 7 | 0 | 0 | 2018-04-21 09:00 | 9 | 7 | 87.0588 | 18.4565 | 2018-04-21 09:00 | 9 | 7 | 33.0823 | 6.9473
2018-04-21 10:00 | 10 | 7 | 86.1982 | 18.1878 | 2018-04-21 10:00 | 10 | 7 | 0 | 0 | 2018-04-21 10:00 | 10 | 7 | 86.6392 | 18.3675 | 2018-04-21 10:00 | 10 | 7 | 32.9229 | 6.9138
2018-04-21 11:00 | 11 | 7 | 86.1707 | 18.182 | 2018-04-21 11:00 | 11 | 7 | 0 | 0 | 2018-04-21 11:00 | 11 | 7 | 86.8849 | 18.4196 | 2018-04-21 11:00 | 11 | 7 | 33.0163 | 6.9334
2018-04-21 12:00 | 12 | 7 | 86.5019 | 18.2519 | 2018-04-21 12:00 | 12 | 7 | 0 | 0 | 2018-04-21 12:00 | 12 | 7 | 87.1504 | 18.4759 | 2018-04-21 12:00 | 12 | 7 | 33.1172 | 6.9546
2018-04-21 13:00 | 13 | 7 | 86.6148 | 18.2757 | 2018-04-21 13:00 | 13 | 7 | 0 | 0 | 2018-04-21 13:00 | 13 | 7 | 87.3167 | 18.5111 | 2018-04-21 13:00 | 13 | 7 | 33.1803 | 6.9679
2018-04-21 14:00 | 14 | 7 | 86.4439 | 18.2397 | 2018-04-21 14:00 | 14 | 7 | 0 | 0 | 2018-04-21 14:00 | 14 | 7 | 87.0832 | 18.4616 | 2018-04-21 14:00 | 14 | 7 | 33.0916 | 6.9492
2018-04-21 15:00 | 15 | 7 | 86.5522 | 18.2625 | 2018-04-21 15:00 | 15 | 7 | 0 | 0 | 2018-04-21 15:00 | 15 | 7 | 87.2938 | 18.5063 | 2018-04-21 15:00 | 15 | 7 | 33.1716 | 6.966
2018-04-21 16:00 | 16 | 7 | 86.5644 | 18.2651 | 2018-04-21 16:00 | 16 | 7 | 0 | 0 | 2018-04-21 16:00 | 16 | 7 | 87.3579 | 18.5199 | 2018-04-21 16:00 | 16 | 7 | 33.196 | 6.9712
2018-04-21 17:00 | 17 | 7 | 86.7445 | 18.3031 | 2018-04-21 17:00 | 17 | 7 | 0 | 0 | 2018-04-21 17:00 | 17 | 7 | 87.57 | 18.5648 | 2018-04-21 17:00 | 17 | 7 | 33.2766 | 6.9881
2018-04-21 18:00 | 18 | 7 | 86.4668 | 18.2445 | 2018-04-21 18:00 | 18 | 7 | 0 | 0 | 2018-04-21 18:00 | 18 | 7 | 87.3014 | 18.5079 | 2018-04-21 18:00 | 18 | 7 | 33.1745 | 6.9667
2018-04-21 19:00 | 19 | 7 | 86.3661 | 18.2232 | 2018-04-21 19:00 | 19 | 7 | 0 | 0 | 2018-04-21 19:00 | 19 | 7 | 87.0954 | 18.4642 | 2018-04-21 19:00 | 19 | 7 | 33.0963 | 6.9502
2018-04-21 20:00 | 20 | 7 | 86.1173 | 18.1708 | 2018-04-21 20:00 | 20 | 7 | 0 | 0 | 2018-04-21 20:00 | 20 | 7 | 86.891 | 18.4209 | 2018-04-21 20:00 | 20 | 7 | 33.0186 | 6.9339
2018-04-21 21:00 | 21 | 7 | 86.1555 | 18.1788 | 2018-04-21 21:00 | 21 | 7 | 0 | 0 | 2018-04-21 21:00 | 21 | 7 | 86.9245 | 18.428 | 2018-04-21 21:00 | 21 | 7 | 33.0313 | 6.9366
2018-04-21 22:00 | 22 | 7 | 86.2211 | 18.1927 | 2018-04-21 22:00 | 22 | 7 | 0 | 0 | 2018-04-21 22:00 | 22 | 7 | 87.0054 | 18.4451 | 2018-04-21 22:00 | 22 | 7 | 33.0621 | 6.943
2018-04-21 23:00 | 23 | 7 | 86.2226 | 18.193 | 2018-04-21 23:00 | 23 | 7 | 0 | 0 | 2018-04-21 23:00 | 23 | 7 | 87.0787 | 18.4607 | 2018-04-21 23:00 | 23 | 7 | 33.0899 | 6.9489
2018-04-22 | 0 | 1 | 86.2364 | 18.1959 | 2018-04-22 | 0 | 1 | 86.7994 | 17.681 | 2018-04-22 | 0 | 1 | 0 | 0 | 2018-04-22 | 0 | 1 | 32.9838 | 6.9266
2018-04-22 01:00 | 1 | 1 | 86.3188 | 18.2133 | 2018-04-22 01:00 | 1 | 1 | 86.952 | 17.7121 | 2018-04-22 01:00 | 1 | 1 | 0 | 0 | 2018-04-22 01:00 | 1 | 1 | 33.0418 | 6.9388
2018-04-22 02:00 | 2 | 1 | 86.2119 | 18.1907 | 2018-04-22 02:00 | 2 | 1 | 86.8177 | 17.6848 | 2018-04-22 02:00 | 2 | 1 | 0 | 0 | 2018-04-22 02:00 | 2 | 1 | 32.9907 | 6.9281
2018-04-22 03:00 | 3 | 1 | 86.1845 | 18.1849 | 2018-04-22 03:00 | 3 | 1 | 86.7857 | 17.6782 | 2018-04-22 03:00 | 3 | 1 | 0 | 0 | 2018-04-22 03:00 | 3 | 1 | 32.9786 | 6.9255
2018-04-22 04:00 | 4 | 1 | 86.2455 | 18.1978 | 2018-04-22 04:00 | 4 | 1 | 86.833 | 17.6879 | 2018-04-22 04:00 | 4 | 1 | 0 | 0 | 2018-04-22 04:00 | 4 | 1 | 32.9965 | 6.9293
2018-04-22 05:00 | 5 | 1 | 86.2333 | 18.1952 | 2018-04-22 05:00 | 5 | 1 | 86.833 | 17.6879 | 2018-04-22 05:00 | 5 | 1 | 0 | 0 | 2018-04-22 05:00 | 5 | 1 | 32.9965 | 6.9293
2018-04-22 06:00 | 6 | 1 | 86.2776 | 18.2046 | 2018-04-22 06:00 | 6 | 1 | 86.8528 | 17.6919 | 2018-04-22 06:00 | 6 | 1 | 0 | 0 | 2018-04-22 06:00 | 6 | 1 | 33.0041 | 6.9309
2018-04-22 07:00 | 7 | 1 | 86.2867 | 18.2065 | 2018-04-22 07:00 | 7 | 1 | 86.8452 | 17.6904 | 2018-04-22 07:00 | 7 | 1 | 0 | 0 | 2018-04-22 07:00 | 7 | 1 | 33.0012 | 6.9302
2018-04-22 08:00 | 8 | 1 | 86.2989 | 18.2091 | 2018-04-22 08:00 | 8 | 1 | 86.9032 | 17.7022 | 2018-04-22 08:00 | 8 | 1 | 0 | 0 | 2018-04-22 08:00 | 8 | 1 | 33.0232 | 6.9349
2018-04-22 09:00 | 9 | 1 | 86.2867 | 18.2065 | 2018-04-22 09:00 | 9 | 1 | 86.8162 | 17.6845 | 2018-04-22 09:00 | 9 | 1 | 0 | 0 | 2018-04-22 09:00 | 9 | 1 | 32.9902 | 6.9279
2018-04-22 10:00 | 10 | 1 | 86.2882 | 18.2068 | 2018-04-22 10:00 | 10 | 1 | 86.8528 | 17.6919 | 2018-04-22 10:00 | 10 | 1 | 0 | 0 | 2018-04-22 10:00 | 10 | 1 | 33.0041 | 6.9309
2018-04-22 11:00 | 11 | 1 | 86.1845 | 18.1849 | 2018-04-22 11:00 | 11 | 1 | 86.743 | 17.6695 | 2018-04-22 11:00 | 11 | 1 | 0 | 0 | 2018-04-22 11:00 | 11 | 1 | 32.9623 | 6.9221
2018-04-22 12:00 | 12 | 1 | 86.1418 | 18.1759 | 2018-04-22 12:00 | 12 | 1 | 86.714 | 17.6636 | 2018-04-22 12:00 | 12 | 1 | 0 | 0 | 2018-04-22 12:00 | 12 | 1 | 32.9513 | 6.9198
2018-04-22 13:00 | 13 | 1 | 86.1479 | 18.1772 | 2018-04-22 13:00 | 13 | 1 | 86.7659 | 17.6742 | 2018-04-22 13:00 | 13 | 1 | 0 | 0 | 2018-04-22 13:00 | 13 | 1 | 32.971 | 6.9239
2018-04-22 14:00 | 14 | 1 | 86.1112 | 18.1695 | 2018-04-22 14:00 | 14 | 1 | 86.7018 | 17.6612 | 2018-04-22 14:00 | 14 | 1 | 0 | 0 | 2018-04-22 14:00 | 14 | 1 | 32.9467 | 6.9188
2018-04-22 15:00 | 15 | 1 | 86.2455 | 18.1978 | 2018-04-22 15:00 | 15 | 1 | 86.8482 | 17.691 | 2018-04-22 15:00 | 15 | 1 | 0 | 0 | 2018-04-22 15:00 | 15 | 1 | 33.0023 | 6.9305
2018-04-22 16:00 | 16 | 1 | 86.3447 | 18.2187 | 2018-04-22 16:00 | 16 | 1 | 86.9398 | 17.7096 | 2018-04-22 16:00 | 16 | 1 | 0 | 0 | 2018-04-22 16:00 | 16 | 1 | 33.0371 | 6.9378
2018-04-22 17:00 | 17 | 1 | 86.4805 | 18.2474 | 2018-04-22 17:00 | 17 | 1 | 86.9856 | 17.719 | 2018-04-22 17:00 | 17 | 1 | 0 | 0 | 2018-04-22 17:00 | 17 | 1 | 33.0545 | 6.9415
2018-04-22 18:00 | 18 | 1 | 86.4332 | 18.2374 | 2018-04-22 18:00 | 18 | 1 | 86.92 | 17.7056 | 2018-04-22 18:00 | 18 | 1 | 0 | 0 | 2018-04-22 18:00 | 18 | 1 | 33.0296 | 6.9362
2018-04-22 19:00 | 19 | 1 | 85.6794 | 18.0784 | 2018-04-22 19:00 | 19 | 1 | 85.9266 | 17.5032 | 2018-04-22 19:00 | 19 | 1 | 0 | 0 | 2018-04-22 19:00 | 19 | 1 | 32.6521 | 6.8569
2018-04-22 20:00 | 20 | 1 | 86.3294 | 18.2155 | 2018-04-22 20:00 | 20 | 1 | 86.5888 | 17.6381 | 2018-04-22 20:00 | 20 | 1 | 0 | 0 | 2018-04-22 20:00 | 20 | 1 | 32.9037 | 6.9098
2018-04-22 21:00 | 21 | 1 | 86.3569 | 18.2213 | 2018-04-22 21:00 | 21 | 1 | 86.6728 | 17.6552 | 2018-04-22 21:00 | 21 | 1 | 0 | 0 | 2018-04-22 21:00 | 21 | 1 | 32.9357 | 6.9165
2018-04-22 22:00 | 22 | 1 | 86.4881 | 18.249 | 2018-04-22 22:00 | 22 | 1 | 86.8086 | 17.6829 | 2018-04-22 22:00 | 22 | 1 | 0 | 0 | 2018-04-22 22:00 | 22 | 1 | 32.9873 | 6.9273
2018-04-22 23:00 | 23 | 1 | 86.4332 | 18.2374 | 2018-04-22 23:00 | 23 | 1 | 86.7353 | 17.668 | 2018-04-22 23:00 | 23 | 1 | 0 | 0 | 2018-04-22 23:00 | 23 | 1 | 32.9594 | 6.9215
2018-04-23 | 0 | 2 | 86.4088 | 18.2323 | 2018-04-23 | 0 | 2 | 86.7002 | 17.6608 | 2018-04-23 | 0 | 2 | 86.9352 | 18.4303 | 2018-04-23 | 0 | 2 | 65.9815 | 13.8561
2018-04-23 01:00 | 1 | 2 | 86.0426 | 18.155 | 2018-04-23 01:00 | 1 | 2 | 86.3127 | 17.5819 | 2018-04-23 01:00 | 1 | 2 | 86.5278 | 18.3439 | 2018-04-23 01:00 | 1 | 2 | 65.6794 | 13.7927
2018-04-23 02:00 | 2 | 2 | 86.392 | 18.2287 | 2018-04-23 02:00 | 2 | 2 | 86.6392 | 17.6484 | 2018-04-23 02:00 | 2 | 2 | 86.8421 | 18.4105 | 2018-04-23 02:00 | 2 | 2 | 65.9229 | 13.8438
2018-04-23 03:00 | 3 | 2 | 86.2776 | 18.2046 | 2018-04-23 03:00 | 3 | 2 | 86.5766 | 17.6357 | 2018-04-23 03:00 | 3 | 2 | 86.7536 | 18.3918 | 2018-04-23 03:00 | 3 | 2 | 65.8655 | 13.8317
2018-04-23 04:00 | 4 | 2 | 86.5034 | 18.2522 | 2018-04-23 04:00 | 4 | 2 | 86.8849 | 17.6985 | 2018-04-23 04:00 | 4 | 2 | 87.0283 | 18.45 | 2018-04-23 04:00 | 4 | 2 | 66.087 | 13.8783
2018-04-23 05:00 | 5 | 2 | 86.3661 | 18.2232 | 2018-04-23 05:00 | 5 | 2 | 86.772 | 17.6755 | 2018-04-23 05:00 | 5 | 2 | 87.0054 | 18.4451 | 2018-04-23 05:00 | 5 | 2 | 66.0354 | 13.8674
2018-04-23 06:00 | 6 | 2 | 86.2898 | 18.2071 | 2018-04-23 06:00 | 6 | 2 | 86.6499 | 17.6506 | 2018-04-23 06:00 | 6 | 2 | 86.8147 | 18.4047 | 2018-04-23 06:00 | 6 | 2 | 65.9165 | 13.8425
2018-04-23 07:00 | 7 | 2 | 86.2043 | 18.1891 | 2018-04-23 07:00 | 7 | 2 | 86.5278 | 17.6257 | 2018-04-23 07:00 | 7 | 2 | 86.7079 | 18.3821 | 2018-04-23 07:00 | 7 | 2 | 65.8296 | 13.8242
2018-04-23 08:00 | 8 | 2 | 86.3355 | 18.2168 | 2018-04-23 08:00 | 8 | 2 | 86.5461 | 17.6294 | 2018-04-23 08:00 | 8 | 2 | 86.8025 | 18.4021 | 2018-04-23 08:00 | 8 | 2 | 65.8725 | 13.8332
2018-04-23 09:00 | 9 | 2 | 86.3798 | 18.2261 | 2018-04-23 09:00 | 9 | 2 | 86.7262 | 17.6661 | 2018-04-23 09:00 | 9 | 2 | 86.8711 | 18.4167 | 2018-04-23 09:00 | 9 | 2 | 65.967 | 13.8531
2018-04-23 10:00 | 10 | 2 | 86.2272 | 18.1939 | 2018-04-23 10:00 | 10 | 2 | 86.5156 | 17.6232 | 2018-04-23 10:00 | 10 | 2 | 86.714 | 18.3834 | 2018-04-23 10:00 | 10 | 2 | 65.8272 | 13.8237
2018-04-23 11:00 | 11 | 2 | 86.2119 | 18.1907 | 2018-04-23 11:00 | 11 | 2 | 86.5141 | 17.6229 | 2018-04-23 11:00 | 11 | 2 | 86.7201 | 18.3847 | 2018-04-23 11:00 | 11 | 2 | 65.829 | 13.8241
2018-04-23 12:00 | 12 | 2 | 86.389 | 18.2281 | 2018-04-23 12:00 | 12 | 2 | 86.6835 | 17.6574 | 2018-04-23 12:00 | 12 | 2 | 86.8574 | 18.4138 | 2018-04-23 12:00 | 12 | 2 | 65.9455 | 13.8486
2018-04-23 13:00 | 13 | 2 | 86.4027 | 18.231 | 2018-04-23 13:00 | 13 | 2 | 86.6224 | 17.645 | 2018-04-23 13:00 | 13 | 2 | 86.7475 | 18.3905 | 2018-04-23 13:00 | 13 | 2 | 65.8806 | 13.8349
2018-04-23 14:00 | 14 | 2 | 86.3783 | 18.2258 | 2018-04-23 14:00 | 14 | 2 | 86.6606 | 17.6528 | 2018-04-23 14:00 | 14 | 2 | 86.7903 | 18.3995 | 2018-04-23 14:00 | 14 | 2 | 65.9113 | 13.8414
2018-04-23 15:00 | 15 | 2 | 86.3355 | 18.2168 | 2018-04-23 15:00 | 15 | 2 | 86.5248 | 17.6251 | 2018-04-23 15:00 | 15 | 2 | 86.7384 | 18.3885 | 2018-04-23 15:00 | 15 | 2 | 65.84 | 13.8264
2018-04-23 16:00 | 16 | 2 | 86.3493 | 18.2197 | 2018-04-23 16:00 | 16 | 2 | 86.4912 | 17.6183 | 2018-04-23 16:00 | 16 | 2 | 86.685 | 18.3772 | 2018-04-23 16:00 | 16 | 2 | 65.807 | 13.8195
2018-04-23 17:00 | 17 | 2 | 86.244 | 18.1975 | 2018-04-23 17:00 | 17 | 2 | 86.4683 | 17.6136 | 2018-04-23 17:00 | 17 | 2 | 86.6743 | 18.375 | 2018-04-23 17:00 | 17 | 2 | 65.7942 | 13.8168
2018-04-23 18:00 | 18 | 2 | 86.3142 | 18.2123 | 2018-04-23 18:00 | 18 | 2 | 86.4378 | 17.6074 | 2018-04-23 18:00 | 18 | 2 | 86.5934 | 18.3578 | 2018-04-23 18:00 | 18 | 2 | 65.7519 | 13.8079
2018-04-23 19:00 | 19 | 2 | 86.2089 | 18.1901 | 2018-04-23 19:00 | 19 | 2 | 86.3508 | 17.5897 | 2018-04-23 19:00 | 19 | 2 | 86.5583 | 18.3504 | 2018-04-23 19:00 | 19 | 2 | 65.7055 | 13.7981
2018-04-23 20:00 | 20 | 2 | 86.2181 | 18.192 | 2018-04-23 20:00 | 20 | 2 | 86.4836 | 17.6167 | 2018-04-23 20:00 | 20 | 2 | 86.6896 | 18.3782 | 2018-04-23 20:00 | 20 | 2 | 65.8058 | 13.8192
2018-04-23 21:00 | 21 | 2 | 86.1494 | 18.1775 | 2018-04-23 21:00 | 21 | 2 | 86.4759 | 17.6151 | 2018-04-23 21:00 | 21 | 2 | 86.63 | 18.3656 | 2018-04-23 21:00 | 21 | 2 | 65.7802 | 13.8139
2018-04-23 22:00 | 22 | 2 | 86.2593 | 18.2007 | 2018-04-23 22:00 | 22 | 2 | 86.5522 | 17.6307 | 2018-04-23 22:00 | 22 | 2 | 86.6468 | 18.3691 | 2018-04-23 22:00 | 22 | 2 | 65.8156 | 13.8213
2018-04-23 23:00 | 23 | 2 | 86.4424 | 18.2393 | 2018-04-23 23:00 | 23 | 2 | 86.8055 | 17.6823 | 2018-04-23 23:00 | 23 | 2 | 86.8864 | 18.4199 | 2018-04-23 23:00 | 23 | 2 | 66.0029 | 13.8606
2018-04-24 | 0 | 3 | 86.4637 | 18.2438 | 2018-04-24 | 0 | 3 | 0 | 0 | 2018-04-24 | 0 | 3 | 0 | 0 | 2018-04-24 | 0 | 3 | 0 | 0
2018-04-24 01:00 | 1 | 3 | 86.5629 | 18.2648 | 2018-04-24 01:00 | 1 | 3 | 0 | 0 | 2018-04-24 01:00 | 1 | 3 | 0 | 0 | 2018-04-24 01:00 | 1 | 3 | 0 | 0
2018-04-24 02:00 | 2 | 3 | 86.3706 | 18.2242 | 2018-04-24 02:00 | 2 | 3 | 0 | 0 | 2018-04-24 02:00 | 2 | 3 | 0 | 0 | 2018-04-24 02:00 | 2 | 3 | 0 | 0
2018-04-24 03:00 | 3 | 3 | 86.3523 | 18.2203 | 2018-04-24 03:00 | 3 | 3 | 0 | 0 | 2018-04-24 03:00 | 3 | 3 | 0 | 0 | 2018-04-24 03:00 | 3 | 3 | 0 | 0
2018-04-24 04:00 | 4 | 3 | 86.3676 | 18.2236 | 2018-04-24 04:00 | 4 | 3 | 0 | 0 | 2018-04-24 04:00 | 4 | 3 | 0 | 0 | 2018-04-24 04:00 | 4 | 3 | 0 | 0
2018-04-24 05:00 | 5 | 3 | 86.4027 | 18.231 | 2018-04-24 05:00 | 5 | 3 | 0 | 0 | 2018-04-24 05:00 | 5 | 3 | 0 | 0 | 2018-04-24 05:00 | 5 | 3 | 0 | 0
2018-04-24 06:00 | 6 | 3 | 86.4652 | 18.2442 | 2018-04-24 06:00 | 6 | 3 | 0 | 0 | 2018-04-24 06:00 | 6 | 3 | 0 | 0 | 2018-04-24 06:00 | 6 | 3 | 0 | 0
2018-04-24 07:00 | 7 | 3 | 86.4012 | 18.2307 | 2018-04-24 07:00 | 7 | 3 | 0 | 0 | 2018-04-24 07:00 | 7 | 3 | 0 | 0 | 2018-04-24 07:00 | 7 | 3 | 0 | 0
2018-04-24 08:00 | 8 | 3 | 86.4515 | 18.2413 | 2018-04-24 08:00 | 8 | 3 | 0 | 0 | 2018-04-24 08:00 | 8 | 3 | 0 | 0 | 2018-04-24 08:00 | 8 | 3 | 0 | 0
2018-04-24 09:00 | 9 | 3 | 86.2028 | 18.1888 | 2018-04-24 09:00 | 9 | 3 | 0 | 0 | 2018-04-24 09:00 | 9 | 3 | 0 | 0 | 2018-04-24 09:00 | 9 | 3 | 0 | 0
2018-04-24 10:00 | 10 | 3 | 86.2715 | 18.2033 | 2018-04-24 10:00 | 10 | 3 | 0 | 0 | 2018-04-24 10:00 | 10 | 3 | 0 | 0 | 2018-04-24 10:00 | 10 | 3 | 0 | 0
2018-04-24 11:00 | 11 | 3 | 86.7567 | 18.3057 | 2018-04-24 11:00 | 11 | 3 | 0 | 0 | 2018-04-24 11:00 | 11 | 3 | 0 | 0 | 2018-04-24 11:00 | 11 | 3 | 0 | 0
2018-04-24 12:00 | 12 | 3 | 86.6194 | 18.2767 | 2018-04-24 12:00 | 12 | 3 | 0 | 0 | 2018-04-24 12:00 | 12 | 3 | 0 | 0 | 2018-04-24 12:00 | 12 | 3 | 0 | 0
2018-04-24 13:00 | 13 | 3 | 86.6377 | 18.2806 | 2018-04-24 13:00 | 13 | 3 | 0 | 0 | 2018-04-24 13:00 | 13 | 3 | 0 | 0 | 2018-04-24 13:00 | 13 | 3 | 0 | 0
2018-04-24 14:00 | 14 | 3 | 86.8757 | 18.3308 | 2018-04-24 14:00 | 14 | 3 | 0 | 0 | 2018-04-24 14:00 | 14 | 3 | 0 | 0 | 2018-04-24 14:00 | 14 | 3 | 0 | 0
2018-04-24 15:00 | 15 | 3 | 86.7994 | 18.3147 | 2018-04-24 15:00 | 15 | 3 | 0 | 0 | 2018-04-24 15:00 | 15 | 3 | 0 | 0 | 2018-04-24 15:00 | 15 | 3 | 0 | 0
2018-04-24 16:00 | 16 | 3 | 86.7674 | 18.3079 | 2018-04-24 16:00 | 16 | 3 | 0 | 0 | 2018-04-24 16:00 | 16 | 3 | 0 | 0 | 2018-04-24 16:00 | 16 | 3 | 0 | 0
2018-04-24 17:00 | 17 | 3 | 86.7384 | 18.3018 | 2018-04-24 17:00 | 17 | 3 | 0 | 0 | 2018-04-24 17:00 | 17 | 3 | 0 | 0 | 2018-04-24 17:00 | 17 | 3 | 0 | 0
2018-04-24 18:00 | 18 | 3 | 86.7124 | 18.2963 | 2018-04-24 18:00 | 18 | 3 | 0 | 0 | 2018-04-24 18:00 | 18 | 3 | 0 | 0 | 2018-04-24 18:00 | 18 | 3 | 0 | 0
2018-04-24 19:00 | 19 | 3 | 86.8376 | 18.3227 | 2018-04-24 19:00 | 19 | 3 | 0 | 0 | 2018-04-24 19:00 | 19 | 3 | 0 | 0 | 2018-04-24 19:00 | 19 | 3 | 0 | 0
2018-04-24 20:00 | 20 | 3 | 86.627 | 18.2783 | 2018-04-24 20:00 | 20 | 3 | 0 | 0 | 2018-04-24 20:00 | 20 | 3 | 0 | 0 | 2018-04-24 20:00 | 20 | 3 | 0 | 0
2018-04-24 21:00 | 21 | 3 | 86.6239 | 18.2776 | 2018-04-24 21:00 | 21 | 3 | 0 | 0 | 2018-04-24 21:00 | 21 | 3 | 0 | 0 | 2018-04-24 21:00 | 21 | 3 | 0 | 0
2018-04-24 22:00 | 22 | 3 | 86.714 | 18.2967 | 2018-04-24 22:00 | 22 | 3 | 0 | 0 | 2018-04-24 22:00 | 22 | 3 | 0 | 0 | 2018-04-24 22:00 | 22 | 3 | 0 | 0
2018-04-24 23:00 | 23 | 3 | 86.8971 | 18.3353 | 2018-04-24 23:00 | 23 | 3 | 0 | 0 | 2018-04-24 23:00 | 23 | 3 | 0 | 0 | 2018-04-24 23:00 | 23 | 3 | 0 | 0
2018-04-25 | 0 | 4 | 0 | 0 | 2018-04-25 | 0 | 4 | 0 | 0 | 2018-04-25 | 0 | 4 | 86.6712 | 18.3743 | 2018-04-25 | 0 | 4 | 32.9351 | 6.9164
2018-04-25 01:00 | 1 | 4 | 0 | 0 | 2018-04-25 01:00 | 1 | 4 | 0 | 0 | 2018-04-25 01:00 | 1 | 4 | 86.511 | 18.3403 | 2018-04-25 01:00 | 1 | 4 | 32.8742 | 6.9036
2018-04-25 02:00 | 2 | 4 | 0 | 0 | 2018-04-25 02:00 | 2 | 4 | 0 | 0 | 2018-04-25 02:00 | 2 | 4 | 86.7628 | 18.3937 | 2018-04-25 02:00 | 2 | 4 | 32.9699 | 6.9237
2018-04-25 03:00 | 3 | 4 | 0 | 0 | 2018-04-25 03:00 | 3 | 4 | 0 | 0 | 2018-04-25 03:00 | 3 | 4 | 86.7384 | 18.3885 | 2018-04-25 03:00 | 3 | 4 | 32.9606 | 6.9217
2018-04-25 04:00 | 4 | 4 | 0 | 0 | 2018-04-25 04:00 | 4 | 4 | 0 | 0 | 2018-04-25 04:00 | 4 | 4 | 86.8376 | 18.4096 | 2018-04-25 04:00 | 4 | 4 | 32.9983 | 6.9296
2018-04-25 05:00 | 5 | 4 | 0 | 0 | 2018-04-25 05:00 | 5 | 4 | 0 | 0 | 2018-04-25 05:00 | 5 | 4 | 87.0222 | 18.4487 | 2018-04-25 05:00 | 5 | 4 | 33.0684 | 6.9444
2018-04-25 06:00 | 6 | 4 | 0 | 0 | 2018-04-25 06:00 | 6 | 4 | 0 | 0 | 2018-04-25 06:00 | 6 | 4 | 86.9627 | 18.4361 | 2018-04-25 06:00 | 6 | 4 | 33.0458 | 6.9396
2018-04-25 07:00 | 7 | 4 | 0 | 0 | 2018-04-25 07:00 | 7 | 4 | 0 | 0 | 2018-04-25 07:00 | 7 | 4 | 87.1321 | 18.472 | 2018-04-25 07:00 | 7 | 4 | 33.1102 | 6.9531
2018-04-25 08:00 | 8 | 4 | 0 | 0 | 2018-04-25 08:00 | 8 | 4 | 0 | 0 | 2018-04-25 08:00 | 8 | 4 | 87.1931 | 18.4849 | 2018-04-25 08:00 | 8 | 4 | 33.1334 | 6.958
2018-04-25 09:00 | 9 | 4 | 0 | 0 | 2018-04-25 09:00 | 9 | 4 | 0 | 0 | 2018-04-25 09:00 | 9 | 4 | 86.7155 | 18.3837 | 2018-04-25 09:00 | 9 | 4 | 32.9519 | 6.9199
2018-04-25 10:00 | 10 | 4 | 0 | 0 | 2018-04-25 10:00 | 10 | 4 | 0 | 0 | 2018-04-25 10:00 | 10 | 4 | 86.6743 | 18.375 | 2018-04-25 10:00 | 10 | 4 | 32.9362 | 6.9166
2018-04-25 11:00 | 11 | 4 | 0 | 0 | 2018-04-25 11:00 | 11 | 4 | 0 | 0 | 2018-04-25 11:00 | 11 | 4 | 86.8956 | 18.4219 | 2018-04-25 11:00 | 11 | 4 | 33.0203 | 6.9343
2018-04-25 12:00 | 12 | 4 | 0 | 0 | 2018-04-25 12:00 | 12 | 4 | 0 | 0 | 2018-04-25 12:00 | 12 | 4 | 86.9276 | 18.4287 | 2018-04-25 12:00 | 12 | 4 | 33.0325 | 6.9368
2018-04-25 13:00 | 13 | 4 | 0 | 0 | 2018-04-25 13:00 | 13 | 4 | 0 | 0 | 2018-04-25 13:00 | 13 | 4 | 87.2541 | 18.4979 | 2018-04-25 13:00 | 13 | 4 | 33.1566 | 6.9629
2018-04-25 14:00 | 14 | 4 | 0 | 0 | 2018-04-25 14:00 | 14 | 4 | 0 | 0 | 2018-04-25 14:00 | 14 | 4 | 87.4037 | 18.5296 | 2018-04-25 14:00 | 14 | 4 | 33.2134 | 6.9748
2018-04-25 15:00 | 15 | 4 | 0 | 0 | 2018-04-25 15:00 | 15 | 4 | 0 | 0 | 2018-04-25 15:00 | 15 | 4 | 87.2129 | 18.4891 | 2018-04-25 15:00 | 15 | 4 | 33.1409 | 6.9596
2018-04-25 16:00 | 16 | 4 | 0 | 0 | 2018-04-25 16:00 | 16 | 4 | 0 | 0 | 2018-04-25 16:00 | 16 | 4 | 86.9718 | 18.438 | 2018-04-25 16:00 | 16 | 4 | 33.0493 | 6.9403
2018-04-25 17:00 | 17 | 4 | 0 | 0 | 2018-04-25 17:00 | 17 | 4 | 0 | 0 | 2018-04-25 17:00 | 17 | 4 | 87.1397 | 18.4736 | 2018-04-25 17:00 | 17 | 4 | 33.1131 | 6.9537
2018-04-25 18:00 | 18 | 4 | 0 | 0 | 2018-04-25 18:00 | 18 | 4 | 0 | 0 | 2018-04-25 18:00 | 18 | 4 | 87.2435 | 18.4956 | 2018-04-25 18:00 | 18 | 4 | 33.1525 | 6.962
2018-04-25 19:00 | 19 | 4 | 0 | 0 | 2018-04-25 19:00 | 19 | 4 | 0 | 0 | 2018-04-25 19:00 | 19 | 4 | 86.8894 | 18.4206 | 2018-04-25 19:00 | 19 | 4 | 33.018 | 6.9338
2018-04-25 20:00 | 20 | 4 | 0 | 0 | 2018-04-25 20:00 | 20 | 4 | 0 | 0 | 2018-04-25 20:00 | 20 | 4 | 87.1839 | 18.483 | 2018-04-25 20:00 | 20 | 4 | 33.1299 | 6.9573
2018-04-25 21:00 | 21 | 4 | 0 | 0 | 2018-04-25 21:00 | 21 | 4 | 0 | 0 | 2018-04-25 21:00 | 21 | 4 | 87.2419 | 18.4953 | 2018-04-25 21:00 | 21 | 4 | 33.1519 | 6.9619
2018-04-25 22:00 | 22 | 4 | 0 | 0 | 2018-04-25 22:00 | 22 | 4 | 0 | 0 | 2018-04-25 22:00 | 22 | 4 | 87.1733 | 18.4807 | 2018-04-25 22:00 | 22 | 4 | 33.1259 | 6.9564
2018-04-25 23:00 | 23 | 4 | 0 | 0 | 2018-04-25 23:00 | 23 | 4 | 0 | 0 | 2018-04-25 23:00 | 23 | 4 | 87.2557 | 18.4982 | 2018-04-25 23:00 | 23 | 4 | 33.1572 | 6.963
2018-04-26 | 0 | 5 | 86.5492 | 18.2619 | 2018-04-26 | 0 | 5 | 0 | 0 | 2018-04-26 | 0 | 5 | 0 | 0 | 2018-04-26 | 0 | 5 | 0 | 0
2018-04-26 01:00 | 1 | 5 | 86.7201 | 18.2979 | 2018-04-26 01:00 | 1 | 5 | 0 | 0 | 2018-04-26 01:00 | 1 | 5 | 0 | 0 | 2018-04-26 01:00 | 1 | 5 | 0 | 0
2018-04-26 02:00 | 2 | 5 | 86.5095 | 18.2535 | 2018-04-26 02:00 | 2 | 5 | 0 | 0 | 2018-04-26 02:00 | 2 | 5 | 0 | 0 | 2018-04-26 02:00 | 2 | 5 | 0 | 0
2018-04-26 03:00 | 3 | 5 | 86.4576 | 18.2426 | 2018-04-26 03:00 | 3 | 5 | 0 | 0 | 2018-04-26 03:00 | 3 | 5 | 0 | 0 | 2018-04-26 03:00 | 3 | 5 | 0 | 0
2018-04-26 04:00 | 4 | 5 | 86.6316 | 18.2793 | 2018-04-26 04:00 | 4 | 5 | 0 | 0 | 2018-04-26 04:00 | 4 | 5 | 0 | 0 | 2018-04-26 04:00 | 4 | 5 | 0 | 0
2018-04-26 05:00 | 5 | 5 | 86.569 | 18.2661 | 2018-04-26 05:00 | 5 | 5 | 0 | 0 | 2018-04-26 05:00 | 5 | 5 | 0 | 0 | 2018-04-26 05:00 | 5 | 5 | 0 | 0
2018-04-26 06:00 | 6 | 5 | 86.6468 | 18.2825 | 2018-04-26 06:00 | 6 | 5 | 0 | 0 | 2018-04-26 06:00 | 6 | 5 | 0 | 0 | 2018-04-26 06:00 | 6 | 5 | 0 | 0
2018-04-26 07:00 | 7 | 5 | 86.6361 | 18.2802 | 2018-04-26 07:00 | 7 | 5 | 0 | 0 | 2018-04-26 07:00 | 7 | 5 | 0 | 0 | 2018-04-26 07:00 | 7 | 5 | 0 | 0
2018-04-26 08:00 | 8 | 5 | 86.6819 | 18.2899 | 2018-04-26 08:00 | 8 | 5 | 0 | 0 | 2018-04-26 08:00 | 8 | 5 | 0 | 0 | 2018-04-26 08:00 | 8 | 5 | 0 | 0
2018-04-26 09:00 | 9 | 5 | 86.7094 | 18.2957 | 2018-04-26 09:00 | 9 | 5 | 0 | 0 | 2018-04-26 09:00 | 9 | 5 | 0 | 0 | 2018-04-26 09:00 | 9 | 5 | 0 | 0
2018-04-26 10:00 | 10 | 5 | 86.7933 | 18.3134 | 2018-04-26 10:00 | 10 | 5 | 0 | 0 | 2018-04-26 10:00 | 10 | 5 | 0 | 0 | 2018-04-26 10:00 | 10 | 5 | 0 | 0
2018-04-26 11:00 | 11 | 5 | 86.8009 | 18.315 | 2018-04-26 11:00 | 11 | 5 | 0 | 0 | 2018-04-26 11:00 | 11 | 5 | 0 | 0 | 2018-04-26 11:00 | 11 | 5 | 0 | 0
2018-04-26 12:00 | 12 | 5 | 86.6728 | 18.288 | 2018-04-26 12:00 | 12 | 5 | 0 | 0 | 2018-04-26 12:00 | 12 | 5 | 0 | 0 | 2018-04-26 12:00 | 12 | 5 | 0 | 0
2018-04-26 13:00 | 13 | 5 | 86.6316 | 18.2793 | 2018-04-26 13:00 | 13 | 5 | 0 | 0 | 2018-04-26 13:00 | 13 | 5 | 0 | 0 | 2018-04-26 13:00 | 13 | 5 | 0 | 0
2018-04-26 14:00 | 14 | 5 | 86.6316 | 18.2793 | 2018-04-26 14:00 | 14 | 5 | 0 | 0 | 2018-04-26 14:00 | 14 | 5 | 0 | 0 | 2018-04-26 14:00 | 14 | 5 | 0 | 0
2018-04-26 15:00 | 15 | 5 | 86.6636 | 18.286 | 2018-04-26 15:00 | 15 | 5 | 0 | 0 | 2018-04-26 15:00 | 15 | 5 | 0 | 0 | 2018-04-26 15:00 | 15 | 5 | 0 | 0
2018-04-26 16:00 | 16 | 5 | 86.5568 | 18.2635 | 2018-04-26 16:00 | 16 | 5 | 0 | 0 | 2018-04-26 16:00 | 16 | 5 | 0 | 0 | 2018-04-26 16:00 | 16 | 5 | 0 | 0
2018-04-26 17:00 | 17 | 5 | 86.6865 | 18.2909 | 2018-04-26 17:00 | 17 | 5 | 0 | 0 | 2018-04-26 17:00 | 17 | 5 | 0 | 0 | 2018-04-26 17:00 | 17 | 5 | 0 | 0
2018-04-26 18:00 | 18 | 5 | 86.7262 | 18.2992 | 2018-04-26 18:00 | 18 | 5 | 0 | 0 | 2018-04-26 18:00 | 18 | 5 | 0 | 0 | 2018-04-26 18:00 | 18 | 5 | 0 | 0
2018-04-26 19:00 | 19 | 5 | 86.5187 | 18.2554 | 2018-04-26 19:00 | 19 | 5 | 0 | 0 | 2018-04-26 19:00 | 19 | 5 | 0 | 0 | 2018-04-26 19:00 | 19 | 5 | 0 | 0
2018-04-26 20:00 | 20 | 5 | 86.5766 | 18.2677 | 2018-04-26 20:00 | 20 | 5 | 0 | 0 | 2018-04-26 20:00 | 20 | 5 | 0 | 0 | 2018-04-26 20:00 | 20 | 5 | 0 | 0
2018-04-26 21:00 | 21 | 5 | 86.6194 | 18.2767 | 2018-04-26 21:00 | 21 | 5 | 0 | 0 | 2018-04-26 21:00 | 21 | 5 | 0 | 0 | 2018-04-26 21:00 | 21 | 5 | 0 | 0
2018-04-26 22:00 | 22 | 5 | 86.6743 | 18.2883 | 2018-04-26 22:00 | 22 | 5 | 0 | 0 | 2018-04-26 22:00 | 22 | 5 | 0 | 0 | 2018-04-26 22:00 | 22 | 5 | 0 | 0
2018-04-26 23:00 | 23 | 5 | 86.5644 | 18.2651 | 2018-04-26 23:00 | 23 | 5 | 0 | 0 | 2018-04-26 23:00 | 23 | 5 | 0 | 0 | 2018-04-26 23:00 | 23 | 5 | 0 | 0
2018-04-27 | 0 | 6 | 86.2226 | 18.193 | 2018-04-27 | 0 | 6 | 86.688 | 17.6583 | 2018-04-27 | 0 | 6 | 0 | 0 | 2018-04-27 | 0 | 6 | 32.9414 | 6.9177
2018-04-27 01:00 | 1 | 6 | 86.1128 | 18.1698 | 2018-04-27 01:00 | 1 | 6 | 86.5232 | 17.6248 | 2018-04-27 01:00 | 1 | 6 | 0 | 0 | 2018-04-27 01:00 | 1 | 6 | 32.8788 | 6.9046
2018-04-27 02:00 | 2 | 6 | 86.2791 | 18.2049 | 2018-04-27 02:00 | 2 | 6 | 86.6896 | 17.6587 | 2018-04-27 02:00 | 2 | 6 | 0 | 0 | 2018-04-27 02:00 | 2 | 6 | 32.942 | 6.9178
2018-04-27 03:00 | 3 | 6 | 86.0014 | 18.1463 | 2018-04-27 03:00 | 3 | 6 | 86.4485 | 17.6096 | 2018-04-27 03:00 | 3 | 6 | 0 | 0 | 2018-04-27 03:00 | 3 | 6 | 32.8504 | 6.8986
2018-04-27 04:00 | 4 | 6 | 86.0533 | 18.1572 | 2018-04-27 04:00 | 4 | 6 | 86.4347 | 17.6067 | 2018-04-27 04:00 | 4 | 6 | 0 | 0 | 2018-04-27 04:00 | 4 | 6 | 32.8452 | 6.8975
2018-04-27 05:00 | 5 | 6 | 86.2257 | 18.1936 | 2018-04-27 05:00 | 5 | 6 | 86.6117 | 17.6428 | 2018-04-27 05:00 | 5 | 6 | 0 | 0 | 2018-04-27 05:00 | 5 | 6 | 32.9124 | 6.9116
2018-04-27 06:00 | 6 | 6 | 86.4332 | 18.2374 | 2018-04-27 06:00 | 6 | 6 | 86.9352 | 17.7087 | 2018-04-27 06:00 | 6 | 6 | 0 | 0 | 2018-04-27 06:00 | 6 | 6 | 33.0354 | 6.9374
2018-04-27 07:00 | 7 | 6 | 86.5873 | 18.2699 | 2018-04-27 07:00 | 7 | 6 | 87.0619 | 17.7345 | 2018-04-27 07:00 | 7 | 6 | 0 | 0 | 2018-04-27 07:00 | 7 | 6 | 33.0835 | 6.9475
2018-04-27 08:00 | 8 | 6 | 86.3691 | 18.2239 | 2018-04-27 08:00 | 8 | 6 | 86.7811 | 17.6773 | 2018-04-27 08:00 | 8 | 6 | 0 | 0 | 2018-04-27 08:00 | 8 | 6 | 32.9768 | 6.9251
2018-04-27 09:00 | 9 | 6 | 86.334 | 18.2165 | 2018-04-27 09:00 | 9 | 6 | 86.7399 | 17.6689 | 2018-04-27 09:00 | 9 | 6 | 0 | 0 | 2018-04-27 09:00 | 9 | 6 | 32.9612 | 6.9218
2018-04-27 10:00 | 10 | 6 | 86.5126 | 18.2542 | 2018-04-27 10:00 | 10 | 6 | 86.862 | 17.6938 | 2018-04-27 10:00 | 10 | 6 | 0 | 0 | 2018-04-27 10:00 | 10 | 6 | 33.0076 | 6.9316
2018-04-27 11:00 | 11 | 6 | 86.5003 | 18.2516 | 2018-04-27 11:00 | 11 | 6 | 86.9306 | 17.7078 | 2018-04-27 11:00 | 11 | 6 | 0 | 0 | 2018-04-27 11:00 | 11 | 6 | 33.0336 | 6.9371
2018-04-27 12:00 | 12 | 6 | 86.7002 | 18.2937 | 2018-04-27 12:00 | 12 | 6 | 87.1412 | 17.7507 | 2018-04-27 12:00 | 12 | 6 | 0 | 0 | 2018-04-27 12:00 | 12 | 6 | 33.1137 | 6.9539
2018-04-27 13:00 | 13 | 6 | 86.363 | 18.2226 | 2018-04-27 13:00 | 13 | 6 | 86.8009 | 17.6813 | 2018-04-27 13:00 | 13 | 6 | 0 | 0 | 2018-04-27 13:00 | 13 | 6 | 32.9843 | 6.9267
2018-04-27 14:00 | 14 | 6 | 86.4408 | 18.239 | 2018-04-27 14:00 | 14 | 6 | 86.8635 | 17.6941 | 2018-04-27 14:00 | 14 | 6 | 0 | 0 | 2018-04-27 14:00 | 14 | 6 | 33.0081 | 6.9317
2018-04-27 15:00 | 15 | 6 | 86.2943 | 18.2081 | 2018-04-27 15:00 | 15 | 6 | 86.6743 | 17.6556 | 2018-04-27 15:00 | 15 | 6 | 0 | 0 | 2018-04-27 15:00 | 15 | 6 | 32.9362 | 6.9166
2018-04-27 16:00 | 16 | 6 | 86.3706 | 18.2242 | 2018-04-27 16:00 | 16 | 6 | 86.7491 | 17.6708 | 2018-04-27 16:00 | 16 | 6 | 0 | 0 | 2018-04-27 16:00 | 16 | 6 | 32.9647 | 6.9226
2018-04-27 17:00 | 17 | 6 | 86.2882 | 18.2068 | 2018-04-27 17:00 | 17 | 6 | 86.7445 | 17.6699 | 2018-04-27 17:00 | 17 | 6 | 0 | 0 | 2018-04-27 17:00 | 17 | 6 | 32.9629 | 6.9222
2018-04-27 18:00 | 18 | 6 | 86.1875 | 18.1856 | 2018-04-27 18:00 | 18 | 6 | 86.6667 | 17.654 | 2018-04-27 18:00 | 18 | 6 | 0 | 0 | 2018-04-27 18:00 | 18 | 6 | 32.9333 | 6.916
2018-04-27 19:00 | 19 | 6 | 86.099 | 18.1669 | 2018-04-27 19:00 | 19 | 6 | 86.5431 | 17.6288 | 2018-04-27 19:00 | 19 | 6 | 0 | 0 | 2018-04-27 19:00 | 19 | 6 | 32.8864 | 6.9061
2018-04-27 20:00 | 20 | 6 | 86.1997 | 18.1881 | 2018-04-27 20:00 | 20 | 6 | 86.5187 | 17.6239 | 2018-04-27 20:00 | 20 | 6 | 0 | 0 | 2018-04-27 20:00 | 20 | 6 | 32.8771 | 6.9042
2018-04-27 21:00 | 21 | 6 | 86.3767 | 18.2255 | 2018-04-27 21:00 | 21 | 6 | 86.7247 | 17.6658 | 2018-04-27 21:00 | 21 | 6 | 0 | 0 | 2018-04-27 21:00 | 21 | 6 | 32.9554 | 6.9206
2018-04-27 22:00 | 22 | 6 | 86.3691 | 18.2239 | 2018-04-27 22:00 | 22 | 6 | 86.7659 | 17.6742 | 2018-04-27 22:00 | 22 | 6 | 0 | 0 | 2018-04-27 22:00 | 22 | 6 | 32.971 | 6.9239
2018-04-27 23:00 | 23 | 6 | 86.4012 | 18.2307 | 2018-04-27 23:00 | 23 | 6 | 86.7918 | 17.6795 | 2018-04-27 23:00 | 23 | 6 | 0 | 0 | 2018-04-27 23:00 | 23 | 6 | 32.9809 | 6.926
2018-04-28 | 0 | 7 | 86.0121 | 18.1486 | 2018-04-28 | 0 | 7 | 0 | 0 | 2018-04-28 | 0 | 7 | 86.5507 | 18.3487 | 2018-04-28 | 0 | 7 | 32.8893 | 6.9067
2018-04-28 01:00 | 1 | 7 | 85.919 | 18.1289 | 2018-04-28 01:00 | 1 | 7 | 0 | 0 | 2018-04-28 01:00 | 1 | 7 | 86.5324 | 18.3449 | 2018-04-28 01:00 | 1 | 7 | 32.8823 | 6.9053
2018-04-28 02:00 | 2 | 7 | 86.0533 | 18.1572 | 2018-04-28 02:00 | 2 | 7 | 0 | 0 | 2018-04-28 02:00 | 2 | 7 | 86.6453 | 18.3688 | 2018-04-28 02:00 | 2 | 7 | 32.9252 | 6.9143
2018-04-28 03:00 | 3 | 7 | 86.1677 | 18.1814 | 2018-04-28 03:00 | 3 | 7 | 0 | 0 | 2018-04-28 03:00 | 3 | 7 | 86.7002 | 18.3804 | 2018-04-28 03:00 | 3 | 7 | 32.9461 | 6.9187
2018-04-28 04:00 | 4 | 7 | 86.3081 | 18.211 | 2018-04-28 04:00 | 4 | 7 | 0 | 0 | 2018-04-28 04:00 | 4 | 7 | 86.8513 | 18.4125 | 2018-04-28 04:00 | 4 | 7 | 33.0035 | 6.9307
2018-04-28 05:00 | 5 | 7 | 86.2562 | 18.2001 | 2018-04-28 05:00 | 5 | 7 | 0 | 0 | 2018-04-28 05:00 | 5 | 7 | 86.8605 | 18.4144 | 2018-04-28 05:00 | 5 | 7 | 33.007 | 6.9315
2018-04-28 06:00 | 6 | 7 | 86.1234 | 18.172 | 2018-04-28 06:00 | 6 | 7 | 0 | 0 | 2018-04-28 06:00 | 6 | 7 | 86.6682 | 18.3737 | 2018-04-28 06:00 | 6 | 7 | 32.9339 | 6.9161
2018-04-28 07:00 | 7 | 7 | 86.1906 | 18.1862 | 2018-04-28 07:00 | 7 | 7 | 0 | 0 | 2018-04-28 07:00 | 7 | 7 | 86.7247 | 18.3856 | 2018-04-28 07:00 | 7 | 7 | 32.9554 | 6.9206
2018-04-28 08:00 | 8 | 7 | 86.36 | 18.222 | 2018-04-28 08:00 | 8 | 7 | 0 | 0 | 2018-04-28 08:00 | 8 | 7 | 86.952 | 18.4338 | 2018-04-28 08:00 | 8 | 7 | 33.0418 | 6.9388
2018-04-28 09:00 | 9 | 7 | 86.4912 | 18.2496 | 2018-04-28 09:00 | 9 | 7 | 0 | 0 | 2018-04-28 09:00 | 9 | 7 | 87.0588 | 18.4565 | 2018-04-28 09:00 | 9 | 7 | 33.0823 | 6.9473
2018-04-28 10:00 | 10 | 7 | 86.1982 | 18.1878 | 2018-04-28 10:00 | 10 | 7 | 0 | 0 | 2018-04-28 10:00 | 10 | 7 | 86.6392 | 18.3675 | 2018-04-28 10:00 | 10 | 7 | 32.9229 | 6.9138
2018-04-28 11:00 | 11 | 7 | 86.1707 | 18.182 | 2018-04-28 11:00 | 11 | 7 | 0 | 0 | 2018-04-28 11:00 | 11 | 7 | 86.8849 | 18.4196 | 2018-04-28 11:00 | 11 | 7 | 33.0163 | 6.9334
2018-04-28 12:00 | 12 | 7 | 86.5019 | 18.2519 | 2018-04-28 12:00 | 12 | 7 | 0 | 0 | 2018-04-28 12:00 | 12 | 7 | 87.1504 | 18.4759 | 2018-04-28 12:00 | 12 | 7 | 33.1172 | 6.9546
2018-04-28 13:00 | 13 | 7 | 86.6148 | 18.2757 | 2018-04-28 13:00 | 13 | 7 | 0 | 0 | 2018-04-28 13:00 | 13 | 7 | 87.3167 | 18.5111 | 2018-04-28 13:00 | 13 | 7 | 33.1803 | 6.9679
2018-04-28 14:00 | 14 | 7 | 86.4439 | 18.2397 | 2018-04-28 14:00 | 14 | 7 | 0 | 0 | 2018-04-28 14:00 | 14 | 7 | 87.0832 | 18.4616 | 2018-04-28 14:00 | 14 | 7 | 33.0916 | 6.9492
2018-04-28 15:00 | 15 | 7 | 86.5522 | 18.2625 | 2018-04-28 15:00 | 15 | 7 | 0 | 0 | 2018-04-28 15:00 | 15 | 7 | 87.2938 | 18.5063 | 2018-04-28 15:00 | 15 | 7 | 33.1716 | 6.966
2018-04-28 16:00 | 16 | 7 | 86.5644 | 18.2651 | 2018-04-28 16:00 | 16 | 7 | 0 | 0 | 2018-04-28 16:00 | 16 | 7 | 87.3579 | 18.5199 | 2018-04-28 16:00 | 16 | 7 | 33.196 | 6.9712
2018-04-28 17:00 | 17 | 7 | 86.7445 | 18.3031 | 2018-04-28 17:00 | 17 | 7 | 0 | 0 | 2018-04-28 17:00 | 17 | 7 | 87.57 | 18.5648 | 2018-04-28 17:00 | 17 | 7 | 33.2766 | 6.9881
2018-04-28 18:00 | 18 | 7 | 86.4668 | 18.2445 | 2018-04-28 18:00 | 18 | 7 | 0 | 0 | 2018-04-28 18:00 | 18 | 7 | 87.3014 | 18.5079 | 2018-04-28 18:00 | 18 | 7 | 33.1745 | 6.9667
2018-04-28 19:00 | 19 | 7 | 86.3661 | 18.2232 | 2018-04-28 19:00 | 19 | 7 | 0 | 0 | 2018-04-28 19:00 | 19 | 7 | 87.0954 | 18.4642 | 2018-04-28 19:00 | 19 | 7 | 33.0963 | 6.9502
2018-04-28 20:00 | 20 | 7 | 86.1173 | 18.1708 | 2018-04-28 20:00 | 20 | 7 | 0 | 0 | 2018-04-28 20:00 | 20 | 7 | 86.891 | 18.4209 | 2018-04-28 20:00 | 20 | 7 | 33.0186 | 6.9339
2018-04-28 21:00 | 21 | 7 | 86.1555 | 18.1788 | 2018-04-28 21:00 | 21 | 7 | 0 | 0 | 2018-04-28 21:00 | 21 | 7 | 86.9245 | 18.428 | 2018-04-28 21:00 | 21 | 7 | 33.0313 | 6.9366
2018-04-28 22:00 | 22 | 7 | 86.2211 | 18.1927 | 2018-04-28 22:00 | 22 | 7 | 0 | 0 | 2018-04-28 22:00 | 22 | 7 | 87.0054 | 18.4451 | 2018-04-28 22:00 | 22 | 7 | 33.0621 | 6.943
2018-04-28 23:00 | 23 | 7 | 86.2226 | 18.193 | 2018-04-28 23:00 | 23 | 7 | 0 | 0 | 2018-04-28 23:00 | 23 | 7 | 87.0787 | 18.4607 | 2018-04-28 23:00 | 23 | 7 | 33.0899 | 6.9489
2018-04-29 | 0 | 1 | 86.2364 | 18.1959 | 2018-04-29 | 0 | 1 | 86.7994 | 17.681 | 2018-04-29 | 0 | 1 | 0 | 0 | 2018-04-29 | 0 | 1 | 32.9838 | 6.9266
2018-04-29 01:00 | 1 | 1 | 86.3188 | 18.2133 | 2018-04-29 01:00 | 1 | 1 | 86.952 | 17.7121 | 2018-04-29 01:00 | 1 | 1 | 0 | 0 | 2018-04-29 01:00 | 1 | 1 | 33.0418 | 6.9388
2018-04-29 02:00 | 2 | 1 | 86.2119 | 18.1907 | 2018-04-29 02:00 | 2 | 1 | 86.8177 | 17.6848 | 2018-04-29 02:00 | 2 | 1 | 0 | 0 | 2018-04-29 02:00 | 2 | 1 | 32.9907 | 6.9281
2018-04-29 03:00 | 3 | 1 | 86.1845 | 18.1849 | 2018-04-29 03:00 | 3 | 1 | 86.7857 | 17.6782 | 2018-04-29 03:00 | 3 | 1 | 0 | 0 | 2018-04-29 03:00 | 3 | 1 | 32.9786 | 6.9255
2018-04-29 04:00 | 4 | 1 | 86.2455 | 18.1978 | 2018-04-29 04:00 | 4 | 1 | 86.833 | 17.6879 | 2018-04-29 04:00 | 4 | 1 | 0 | 0 | 2018-04-29 04:00 | 4 | 1 | 32.9965 | 6.9293
2018-04-29 05:00 | 5 | 1 | 86.2333 | 18.1952 | 2018-04-29 05:00 | 5 | 1 | 86.833 | 17.6879 | 2018-04-29 05:00 | 5 | 1 | 0 | 0 | 2018-04-29 05:00 | 5 | 1 | 32.9965 | 6.9293
2018-04-29 06:00 | 6 | 1 | 86.2776 | 18.2046 | 2018-04-29 06:00 | 6 | 1 | 86.8528 | 17.6919 | 2018-04-29 06:00 | 6 | 1 | 0 | 0 | 2018-04-29 06:00 | 6 | 1 | 33.0041 | 6.9309
2018-04-29 07:00 | 7 | 1 | 86.2867 | 18.2065 | 2018-04-29 07:00 | 7 | 1 | 86.8452 | 17.6904 | 2018-04-29 07:00 | 7 | 1 | 0 | 0 | 2018-04-29 07:00 | 7 | 1 | 33.0012 | 6.9302
2018-04-29 08:00 | 8 | 1 | 86.2989 | 18.2091 | 2018-04-29 08:00 | 8 | 1 | 86.9032 | 17.7022 | 2018-04-29 08:00 | 8 | 1 | 0 | 0 | 2018-04-29 08:00 | 8 | 1 | 33.0232 | 6.9349
2018-04-29 09:00 | 9 | 1 | 86.2867 | 18.2065 | 2018-04-29 09:00 | 9 | 1 | 86.8162 | 17.6845 | 2018-04-29 09:00 | 9 | 1 | 0 | 0 | 2018-04-29 09:00 | 9 | 1 | 32.9902 | 6.9279
2018-04-29 10:00 | 10 | 1 | 86.2882 | 18.2068 | 2018-04-29 10:00 | 10 | 1 | 86.8528 | 17.6919 | 2018-04-29 10:00 | 10 | 1 | 0 | 0 | 2018-04-29 10:00 | 10 | 1 | 33.0041 | 6.9309
2018-04-29 11:00 | 11 | 1 | 86.1845 | 18.1849 | 2018-04-29 11:00 | 11 | 1 | 86.743 | 17.6695 | 2018-04-29 11:00 | 11 | 1 | 0 | 0 | 2018-04-29 11:00 | 11 | 1 | 32.9623 | 6.9221
2018-04-29 12:00 | 12 | 1 | 86.1418 | 18.1759 | 2018-04-29 12:00 | 12 | 1 | 86.714 | 17.6636 | 2018-04-29 12:00 | 12 | 1 | 0 | 0 | 2018-04-29 12:00 | 12 | 1 | 32.9513 | 6.9198
2018-04-29 13:00 | 13 | 1 | 86.1479 | 18.1772 | 2018-04-29 13:00 | 13 | 1 | 86.7659 | 17.6742 | 2018-04-29 13:00 | 13 | 1 | 0 | 0 | 2018-04-29 13:00 | 13 | 1 | 32.971 | 6.9239
2018-04-29 14:00 | 14 | 1 | 86.1112 | 18.1695 | 2018-04-29 14:00 | 14 | 1 | 86.7018 | 17.6612 | 2018-04-29 14:00 | 14 | 1 | 0 | 0 | 2018-04-29 14:00 | 14 | 1 | 32.9467 | 6.9188
2018-04-29 15:00 | 15 | 1 | 86.2455 | 18.1978 | 2018-04-29 15:00 | 15 | 1 | 86.8482 | 17.691 | 2018-04-29 15:00 | 15 | 1 | 0 | 0 | 2018-04-29 15:00 | 15 | 1 | 33.0023 | 6.9305
2018-04-29 16:00 | 16 | 1 | 86.3447 | 18.2187 | 2018-04-29 16:00 | 16 | 1 | 86.9398 | 17.7096 | 2018-04-29 16:00 | 16 | 1 | 0 | 0 | 2018-04-29 16:00 | 16 | 1 | 33.0371 | 6.9378
2018-04-29 17:00 | 17 | 1 | 86.4805 | 18.2474 | 2018-04-29 17:00 | 17 | 1 | 86.9856 | 17.719 | 2018-04-29 17:00 | 17 | 1 | 0 | 0 | 2018-04-29 17:00 | 17 | 1 | 33.0545 | 6.9415
2018-04-29 18:00 | 18 | 1 | 86.4332 | 18.2374 | 2018-04-29 18:00 | 18 | 1 | 86.92 | 17.7056 | 2018-04-29 18:00 | 18 | 1 | 0 | 0 | 2018-04-29 18:00 | 18 | 1 | 33.0296 | 6.9362
2018-04-29 19:00 | 19 | 1 | 85.6794 | 18.0784 | 2018-04-29 19:00 | 19 | 1 | 85.9266 | 17.5032 | 2018-04-29 19:00 | 19 | 1 | 0 | 0 | 2018-04-29 19:00 | 19 | 1 | 32.6521 | 6.8569
2018-04-29 20:00 | 20 | 1 | 86.3294 | 18.2155 | 2018-04-29 20:00 | 20 | 1 | 86.5888 | 17.6381 | 2018-04-29 20:00 | 20 | 1 | 0 | 0 | 2018-04-29 20:00 | 20 | 1 | 32.9037 | 6.9098
2018-04-29 21:00 | 21 | 1 | 86.3569 | 18.2213 | 2018-04-29 21:00 | 21 | 1 | 86.6728 | 17.6552 | 2018-04-29 21:00 | 21 | 1 | 0 | 0 | 2018-04-29 21:00 | 21 | 1 | 32.9357 | 6.9165
2018-04-29 22:00 | 22 | 1 | 86.4881 | 18.249 | 2018-04-29 22:00 | 22 | 1 | 86.8086 | 17.6829 | 2018-04-29 22:00 | 22 | 1 | 0 | 0 | 2018-04-29 22:00 | 22 | 1 | 32.9873 | 6.9273
2018-04-29 23:00 | 23 | 1 | 86.4332 | 18.2374 | 2018-04-29 23:00 | 23 | 1 | 86.7353 | 17.668 | 2018-04-29 23:00 | 23 | 1 | 0 | 0 | 2018-04-29 23:00 | 23 | 1 | 32.9594 | 6.9215
2018-04-30 | 0 | 2 | 86.4088 | 18.2323 | 2018-04-30 | 0 | 2 | 86.7002 | 17.6608 | 2018-04-30 | 0 | 2 | 86.9352 | 18.4303 | 2018-04-30 | 0 | 2 | 65.9815 | 13.8561
2018-04-30 01:00 | 1 | 2 | 86.0426 | 18.155 | 2018-04-30 01:00 | 1 | 2 | 86.3127 | 17.5819 | 2018-04-30 01:00 | 1 | 2 | 86.5278 | 18.3439 | 2018-04-30 01:00 | 1 | 2 | 65.6794 | 13.7927
2018-04-30 02:00 | 2 | 2 | 86.392 | 18.2287 | 2018-04-30 02:00 | 2 | 2 | 86.6392 | 17.6484 | 2018-04-30 02:00 | 2 | 2 | 86.8421 | 18.4105 | 2018-04-30 02:00 | 2 | 2 | 65.9229 | 13.8438
2018-04-30 03:00 | 3 | 2 | 86.2776 | 18.2046 | 2018-04-30 03:00 | 3 | 2 | 86.5766 | 17.6357 | 2018-04-30 03:00 | 3 | 2 | 86.7536 | 18.3918 | 2018-04-30 03:00 | 3 | 2 | 65.8655 | 13.8317
2018-04-30 04:00 | 4 | 2 | 86.5034 | 18.2522 | 2018-04-30 04:00 | 4 | 2 | 86.8849 | 17.6985 | 2018-04-30 04:00 | 4 | 2 | 87.0283 | 18.45 | 2018-04-30 04:00 | 4 | 2 | 66.087 | 13.8783
2018-04-30 05:00 | 5 | 2 | 86.3661 | 18.2232 | 2018-04-30 05:00 | 5 | 2 | 86.772 | 17.6755 | 2018-04-30 05:00 | 5 | 2 | 87.0054 | 18.4451 | 2018-04-30 05:00 | 5 | 2 | 66.0354 | 13.8674
2018-04-30 06:00 | 6 | 2 | 86.2898 | 18.2071 | 2018-04-30 06:00 | 6 | 2 | 86.6499 | 17.6506 | 2018-04-30 06:00 | 6 | 2 | 86.8147 | 18.4047 | 2018-04-30 06:00 | 6 | 2 | 65.9165 | 13.8425
2018-04-30 07:00 | 7 | 2 | 86.2043 | 18.1891 | 2018-04-30 07:00 | 7 | 2 | 86.5278 | 17.6257 | 2018-04-30 07:00 | 7 | 2 | 86.7079 | 18.3821 | 2018-04-30 07:00 | 7 | 2 | 65.8296 | 13.8242
2018-04-30 08:00 | 8 | 2 | 86.3355 | 18.2168 | 2018-04-30 08:00 | 8 | 2 | 86.5461 | 17.6294 | 2018-04-30 08:00 | 8 | 2 | 86.8025 | 18.4021 | 2018-04-30 08:00 | 8 | 2 | 65.8725 | 13.8332
2018-04-30 09:00 | 9 | 2 | 86.3798 | 18.2261 | 2018-04-30 09:00 | 9 | 2 | 86.7262 | 17.6661 | 2018-04-30 09:00 | 9 | 2 | 86.8711 | 18.4167 | 2018-04-30 09:00 | 9 | 2 | 65.967 | 13.8531
2018-04-30 10:00 | 10 | 2 | 86.2272 | 18.1939 | 2018-04-30 10:00 | 10 | 2 | 86.5156 | 17.6232 | 2018-04-30 10:00 | 10 | 2 | 86.714 | 18.3834 | 2018-04-30 10:00 | 10 | 2 | 65.8272 | 13.8237
2018-04-30 11:00 | 11 | 2 | 86.2119 | 18.1907 | 2018-04-30 11:00 | 11 | 2 | 86.5141 | 17.6229 | 2018-04-30 11:00 | 11 | 2 | 86.7201 | 18.3847 | 2018-04-30 11:00 | 11 | 2 | 65.829 | 13.8241
2018-04-30 12:00 | 12 | 2 | 86.389 | 18.2281 | 2018-04-30 12:00 | 12 | 2 | 86.6835 | 17.6574 | 2018-04-30 12:00 | 12 | 2 | 86.8574 | 18.4138 | 2018-04-30 12:00 | 12 | 2 | 65.9455 | 13.8486
2018-04-30 13:00 | 13 | 2 | 86.4027 | 18.231 | 2018-04-30 13:00 | 13 | 2 | 86.6224 | 17.645 | 2018-04-30 13:00 | 13 | 2 | 86.7475 | 18.3905 | 2018-04-30 13:00 | 13 | 2 | 65.8806 | 13.8349
2018-04-30 14:00 | 14 | 2 | 86.3783 | 18.2258 | 2018-04-30 14:00 | 14 | 2 | 86.6606 | 17.6528 | 2018-04-30 14:00 | 14 | 2 | 86.7903 | 18.3995 | 2018-04-30 14:00 | 14 | 2 | 65.9113 | 13.8414
2018-04-30 15:00 | 15 | 2 | 86.3355 | 18.2168 | 2018-04-30 15:00 | 15 | 2 | 86.5248 | 17.6251 | 2018-04-30 15:00 | 15 | 2 | 86.7384 | 18.3885 | 2018-04-30 15:00 | 15 | 2 | 65.84 | 13.8264
2018-04-30 16:00 | 16 | 2 | 86.3493 | 18.2197 | 2018-04-30 16:00 | 16 | 2 | 86.4912 | 17.6183 | 2018-04-30 16:00 | 16 | 2 | 86.685 | 18.3772 | 2018-04-30 16:00 | 16 | 2 | 65.807 | 13.8195
2018-04-30 17:00 | 17 | 2 | 86.244 | 18.1975 | 2018-04-30 17:00 | 17 | 2 | 86.4683 | 17.6136 | 2018-04-30 17:00 | 17 | 2 | 86.6743 | 18.375 | 2018-04-30 17:00 | 17 | 2 | 65.7942 | 13.8168
2018-04-30 18:00 | 18 | 2 | 86.3142 | 18.2123 | 2018-04-30 18:00 | 18 | 2 | 86.4378 | 17.6074 | 2018-04-30 18:00 | 18 | 2 | 86.5934 | 18.3578 | 2018-04-30 18:00 | 18 | 2 | 65.7519 | 13.8079
2018-04-30 19:00 | 19 | 2 | 86.2089 | 18.1901 | 2018-04-30 19:00 | 19 | 2 | 86.3508 | 17.5897 | 2018-04-30 19:00 | 19 | 2 | 86.5583 | 18.3504 | 2018-04-30 19:00 | 19 | 2 | 65.7055 | 13.7981
2018-04-30 20:00 | 20 | 2 | 86.2181 | 18.192 | 2018-04-30 20:00 | 20 | 2 | 86.4836 | 17.6167 | 2018-04-30 20:00 | 20 | 2 | 86.6896 | 18.3782 | 2018-04-30 20:00 | 20 | 2 | 65.8058 | 13.8192
2018-04-30 21:00 | 21 | 2 | 86.1494 | 18.1775 | 2018-04-30 21:00 | 21 | 2 | 86.4759 | 17.6151 | 2018-04-30 21:00 | 21 | 2 | 86.63 | 18.3656 | 2018-04-30 21:00 | 21 | 2 | 65.7802 | 13.8139
2018-04-30 22:00 | 22 | 2 | 86.2593 | 18.2007 | 2018-04-30 22:00 | 22 | 2 | 86.5522 | 17.6307 | 2018-04-30 22:00 | 22 | 2 | 86.6468 | 18.3691 | 2018-04-30 22:00 | 22 | 2 | 65.8156 | 13.8213
2018-04-30 23:00 | 23 | 2 | 86.4424 | 18.2393 | 2018-04-30 23:00 | 23 | 2 | 86.8055 | 17.6823 | 2018-04-30 23:00 | 23 | 2 | 86.8864 | 18.4199 | 2018-04-30 23:00 | 23 | 2 | 66.0029 | 13.8606
2018-05-01 | 0 | 3 | 86.4637 | 18.2438 | 2018-05-01 | 0 | 3 | 0 | 0 | 2018-05-01 | 0 | 3 | 0 | 0 | 2018-05-01 | 0 | 3 | 0 | 0
2018-05-01 01:00 | 1 | 3 | 86.5629 | 18.2648 | 2018-05-01 01:00 | 1 | 3 | 0 | 0 | 2018-05-01 01:00 | 1 | 3 | 0 | 0 | 2018-05-01 01:00 | 1 | 3 | 0 | 0
2018-05-01 02:00 | 2 | 3 | 86.3706 | 18.2242 | 2018-05-01 02:00 | 2 | 3 | 0 | 0 | 2018-05-01 02:00 | 2 | 3 | 0 | 0 | 2018-05-01 02:00 | 2 | 3 | 0 | 0
2018-05-01 03:00 | 3 | 3 | 86.3523 | 18.2203 | 2018-05-01 03:00 | 3 | 3 | 0 | 0 | 2018-05-01 03:00 | 3 | 3 | 0 | 0 | 2018-05-01 03:00 | 3 | 3 | 0 | 0
2018-05-01 04:00 | 4 | 3 | 86.3676 | 18.2236 | 2018-05-01 04:00 | 4 | 3 | 0 | 0 | 2018-05-01 04:00 | 4 | 3 | 0 | 0 | 2018-05-01 04:00 | 4 | 3 | 0 | 0
2018-05-01 05:00 | 5 | 3 | 86.4027 | 18.231 | 2018-05-01 05:00 | 5 | 3 | 0 | 0 | 2018-05-01 05:00 | 5 | 3 | 0 | 0 | 2018-05-01 05:00 | 5 | 3 | 0 | 0
2018-05-01 06:00 | 6 | 3 | 86.4652 | 18.2442 | 2018-05-01 06:00 | 6 | 3 | 0 | 0 | 2018-05-01 06:00 | 6 | 3 | 0 | 0 | 2018-05-01 06:00 | 6 | 3 | 0 | 0
2018-05-01 07:00 | 7 | 3 | 86.4012 | 18.2307 | 2018-05-01 07:00 | 7 | 3 | 0 | 0 | 2018-05-01 07:00 | 7 | 3 | 0 | 0 | 2018-05-01 07:00 | 7 | 3 | 0 | 0
2018-05-01 08:00 | 8 | 3 | 86.4515 | 18.2413 | 2018-05-01 08:00 | 8 | 3 | 0 | 0 | 2018-05-01 08:00 | 8 | 3 | 0 | 0 | 2018-05-01 08:00 | 8 | 3 | 0 | 0
2018-05-01 09:00 | 9 | 3 | 86.2028 | 18.1888 | 2018-05-01 09:00 | 9 | 3 | 0 | 0 | 2018-05-01 09:00 | 9 | 3 | 0 | 0 | 2018-05-01 09:00 | 9 | 3 | 0 | 0
2018-05-01 10:00 | 10 | 3 | 86.2715 | 18.2033 | 2018-05-01 10:00 | 10 | 3 | 0 | 0 | 2018-05-01 10:00 | 10 | 3 | 0 | 0 | 2018-05-01 10:00 | 10 | 3 | 0 | 0
2018-05-01 11:00 | 11 | 3 | 86.7567 | 18.3057 | 2018-05-01 11:00 | 11 | 3 | 0 | 0 | 2018-05-01 11:00 | 11 | 3 | 0 | 0 | 2018-05-01 11:00 | 11 | 3 | 0 | 0
2018-05-01 12:00 | 12 | 3 | 86.6194 | 18.2767 | 2018-05-01 12:00 | 12 | 3 | 0 | 0 | 2018-05-01 12:00 | 12 | 3 | 0 | 0 | 2018-05-01 12:00 | 12 | 3 | 0 | 0
2018-05-01 13:00 | 13 | 3 | 86.6377 | 18.2806 | 2018-05-01 13:00 | 13 | 3 | 0 | 0 | 2018-05-01 13:00 | 13 | 3 | 0 | 0 | 2018-05-01 13:00 | 13 | 3 | 0 | 0
2018-05-01 14:00 | 14 | 3 | 86.8757 | 18.3308 | 2018-05-01 14:00 | 14 | 3 | 0 | 0 | 2018-05-01 14:00 | 14 | 3 | 0 | 0 | 2018-05-01 14:00 | 14 | 3 | 0 | 0
2018-05-01 15:00 | 15 | 3 | 86.7994 | 18.3147 | 2018-05-01 15:00 | 15 | 3 | 0 | 0 | 2018-05-01 15:00 | 15 | 3 | 0 | 0 | 2018-05-01 15:00 | 15 | 3 | 0 | 0
2018-05-01 16:00 | 16 | 3 | 86.7674 | 18.3079 | 2018-05-01 16:00 | 16 | 3 | 0 | 0 | 2018-05-01 16:00 | 16 | 3 | 0 | 0 | 2018-05-01 16:00 | 16 | 3 | 0 | 0
2018-05-01 17:00 | 17 | 3 | 86.7384 | 18.3018 | 2018-05-01 17:00 | 17 | 3 | 0 | 0 | 2018-05-01 17:00 | 17 | 3 | 0 | 0 | 2018-05-01 17:00 | 17 | 3 | 0 | 0
2018-05-01 18:00 | 18 | 3 | 86.7124 | 18.2963 | 2018-05-01 18:00 | 18 | 3 | 0 | 0 | 2018-05-01 18:00 | 18 | 3 | 0 | 0 | 2018-05-01 18:00 | 18 | 3 | 0 | 0
2018-05-01 19:00 | 19 | 3 | 86.8376 | 18.3227 | 2018-05-01 19:00 | 19 | 3 | 0 | 0 | 2018-05-01 19:00 | 19 | 3 | 0 | 0 | 2018-05-01 19:00 | 19 | 3 | 0 | 0
2018-05-01 20:00 | 20 | 3 | 86.627 | 18.2783 | 2018-05-01 20:00 | 20 | 3 | 0 | 0 | 2018-05-01 20:00 | 20 | 3 | 0 | 0 | 2018-05-01 20:00 | 20 | 3 | 0 | 0
2018-05-01 21:00 | 21 | 3 | 86.6239 | 18.2776 | 2018-05-01 21:00 | 21 | 3 | 0 | 0 | 2018-05-01 21:00 | 21 | 3 | 0 | 0 | 2018-05-01 21:00 | 21 | 3 | 0 | 0
2018-05-01 22:00 | 22 | 3 | 86.714 | 18.2967 | 2018-05-01 22:00 | 22 | 3 | 0 | 0 | 2018-05-01 22:00 | 22 | 3 | 0 | 0 | 2018-05-01 22:00 | 22 | 3 | 0 | 0
2018-05-01 23:00 | 23 | 3 | 86.8971 | 18.3353 | 2018-05-01 23:00 | 23 | 3 | 0 | 0 | 2018-05-01 23:00 | 23 | 3 | 0 | 0 | 2018-05-01 23:00 | 23 | 3 | 0 | 0
2018-05-02 | 0 | 4 | 0 | 0 | 2018-05-02 | 0 | 4 | 0 | 0 | 2018-05-02 | 0 | 4 | 86.6712 | 18.3743 | 2018-05-02 | 0 | 4 | 32.9351 | 6.9164
2018-05-02 01:00 | 1 | 4 | 0 | 0 | 2018-05-02 01:00 | 1 | 4 | 0 | 0 | 2018-05-02 01:00 | 1 | 4 | 86.511 | 18.3403 | 2018-05-02 01:00 | 1 | 4 | 32.8742 | 6.9036
2018-05-02 02:00 | 2 | 4 | 0 | 0 | 2018-05-02 02:00 | 2 | 4 | 0 | 0 | 2018-05-02 02:00 | 2 | 4 | 86.7628 | 18.3937 | 2018-05-02 02:00 | 2 | 4 | 32.9699 | 6.9237
2018-05-02 03:00 | 3 | 4 | 0 | 0 | 2018-05-02 03:00 | 3 | 4 | 0 | 0 | 2018-05-02 03:00 | 3 | 4 | 86.7384 | 18.3885 | 2018-05-02 03:00 | 3 | 4 | 32.9606 | 6.9217
2018-05-02 04:00 | 4 | 4 | 0 | 0 | 2018-05-02 04:00 | 4 | 4 | 0 | 0 | 2018-05-02 04:00 | 4 | 4 | 86.8376 | 18.4096 | 2018-05-02 04:00 | 4 | 4 | 32.9983 | 6.9296
2018-05-02 05:00 | 5 | 4 | 0 | 0 | 2018-05-02 05:00 | 5 | 4 | 0 | 0 | 2018-05-02 05:00 | 5 | 4 | 87.0222 | 18.4487 | 2018-05-02 05:00 | 5 | 4 | 33.0684 | 6.9444
2018-05-02 06:00 | 6 | 4 | 0 | 0 | 2018-05-02 06:00 | 6 | 4 | 0 | 0 | 2018-05-02 06:00 | 6 | 4 | 86.9627 | 18.4361 | 2018-05-02 06:00 | 6 | 4 | 33.0458 | 6.9396
2018-05-02 07:00 | 7 | 4 | 0 | 0 | 2018-05-02 07:00 | 7 | 4 | 0 | 0 | 2018-05-02 07:00 | 7 | 4 | 87.1321 | 18.472 | 2018-05-02 07:00 | 7 | 4 | 33.1102 | 6.9531
2018-05-02 08:00 | 8 | 4 | 0 | 0 | 2018-05-02 08:00 | 8 | 4 | 0 | 0 | 2018-05-02 08:00 | 8 | 4 | 87.1931 | 18.4849 | 2018-05-02 08:00 | 8 | 4 | 33.1334 | 6.958
2018-05-02 09:00 | 9 | 4 | 0 | 0 | 2018-05-02 09:00 | 9 | 4 | 0 | 0 | 2018-05-02 09:00 | 9 | 4 | 86.7155 | 18.3837 | 2018-05-02 09:00 | 9 | 4 | 32.9519 | 6.9199
2018-05-02 10:00 | 10 | 4 | 0 | 0 | 2018-05-02 10:00 | 10 | 4 | 0 | 0 | 2018-05-02 10:00 | 10 | 4 | 86.6743 | 18.375 | 2018-05-02 10:00 | 10 | 4 | 32.9362 | 6.9166
2018-05-02 11:00 | 11 | 4 | 0 | 0 | 2018-05-02 11:00 | 11 | 4 | 0 | 0 | 2018-05-02 11:00 | 11 | 4 | 86.8956 | 18.4219 | 2018-05-02 11:00 | 11 | 4 | 33.0203 | 6.9343
2018-05-02 12:00 | 12 | 4 | 0 | 0 | 2018-05-02 12:00 | 12 | 4 | 0 | 0 | 2018-05-02 12:00 | 12 | 4 | 86.9276 | 18.4287 | 2018-05-02 12:00 | 12 | 4 | 33.0325 | 6.9368
2018-05-02 13:00 | 13 | 4 | 0 | 0 | 2018-05-02 13:00 | 13 | 4 | 0 | 0 | 2018-05-02 13:00 | 13 | 4 | 87.2541 | 18.4979 | 2018-05-02 13:00 | 13 | 4 | 33.1566 | 6.9629
2018-05-02 14:00 | 14 | 4 | 0 | 0 | 2018-05-02 14:00 | 14 | 4 | 0 | 0 | 2018-05-02 14:00 | 14 | 4 | 87.4037 | 18.5296 | 2018-05-02 14:00 | 14 | 4 | 33.2134 | 6.9748
2018-05-02 15:00 | 15 | 4 | 0 | 0 | 2018-05-02 15:00 | 15 | 4 | 0 | 0 | 2018-05-02 15:00 | 15 | 4 | 87.2129 | 18.4891 | 2018-05-02 15:00 | 15 | 4 | 33.1409 | 6.9596
2018-05-02 16:00 | 16 | 4 | 0 | 0 | 2018-05-02 16:00 | 16 | 4 | 0 | 0 | 2018-05-02 16:00 | 16 | 4 | 86.9718 | 18.438 | 2018-05-02 16:00 | 16 | 4 | 33.0493 | 6.9403
2018-05-02 17:00 | 17 | 4 | 0 | 0 | 2018-05-02 17:00 | 17 | 4 | 0 | 0 | 2018-05-02 17:00 | 17 | 4 | 87.1397 | 18.4736 | 2018-05-02 17:00 | 17 | 4 | 33.1131 | 6.9537
2018-05-02 18:00 | 18 | 4 | 0 | 0 | 2018-05-02 18:00 | 18 | 4 | 0 | 0 | 2018-05-02 18:00 | 18 | 4 | 87.2435 | 18.4956 | 2018-05-02 18:00 | 18 | 4 | 33.1525 | 6.962
2018-05-02 19:00 | 19 | 4 | 0 | 0 | 2018-05-02 19:00 | 19 | 4 | 0 | 0 | 2018-05-02 19:00 | 19 | 4 | 86.8894 | 18.4206 | 2018-05-02 19:00 | 19 | 4 | 33.018 | 6.9338
2018-05-02 20:00 | 20 | 4 | 0 | 0 | 2018-05-02 20:00 | 20 | 4 | 0 | 0 | 2018-05-02 20:00 | 20 | 4 | 87.1839 | 18.483 | 2018-05-02 20:00 | 20 | 4 | 33.1299 | 6.9573
2018-05-02 21:00 | 21 | 4 | 0 | 0 | 2018-05-02 21:00 | 21 | 4 | 0 | 0 | 2018-05-02 21:00 | 21 | 4 | 87.2419 | 18.4953 | 2018-05-02 21:00 | 21 | 4 | 33.1519 | 6.9619
2018-05-02 22:00 | 22 | 4 | 0 | 0 | 2018-05-02 22:00 | 22 | 4 | 0 | 0 | 2018-05-02 22:00 | 22 | 4 | 87.1733 | 18.4807 | 2018-05-02 22:00 | 22 | 4 | 33.1259 | 6.9564
2018-05-02 23:00 | 23 | 4 | 0 | 0 | 2018-05-02 23:00 | 23 | 4 | 0 | 0 | 2018-05-02 23:00 | 23 | 4 | 87.2557 | 18.4982 | 2018-05-02 23:00 | 23 | 4 | 33.1572 | 6.963
2018-05-03 | 0 | 5 | 86.5492 | 18.2619 | 2018-05-03 | 0 | 5 | 0 | 0 | 2018-05-03 | 0 | 5 | 0 | 0 | 2018-05-03 | 0 | 5 | 0 | 0
2018-05-03 01:00 | 1 | 5 | 86.7201 | 18.2979 | 2018-05-03 01:00 | 1 | 5 | 0 | 0 | 2018-05-03 01:00 | 1 | 5 | 0 | 0 | 2018-05-03 01:00 | 1 | 5 | 0 | 0
2018-05-03 02:00 | 2 | 5 | 86.5095 | 18.2535 | 2018-05-03 02:00 | 2 | 5 | 0 | 0 | 2018-05-03 02:00 | 2 | 5 | 0 | 0 | 2018-05-03 02:00 | 2 | 5 | 0 | 0
2018-05-03 03:00 | 3 | 5 | 86.4576 | 18.2426 | 2018-05-03 03:00 | 3 | 5 | 0 | 0 | 2018-05-03 03:00 | 3 | 5 | 0 | 0 | 2018-05-03 03:00 | 3 | 5 | 0 | 0
2018-05-03 04:00 | 4 | 5 | 86.6316 | 18.2793 | 2018-05-03 04:00 | 4 | 5 | 0 | 0 | 2018-05-03 04:00 | 4 | 5 | 0 | 0 | 2018-05-03 04:00 | 4 | 5 | 0 | 0
2018-05-03 05:00 | 5 | 5 | 86.569 | 18.2661 | 2018-05-03 05:00 | 5 | 5 | 0 | 0 | 2018-05-03 05:00 | 5 | 5 | 0 | 0 | 2018-05-03 05:00 | 5 | 5 | 0 | 0
2018-05-03 06:00 | 6 | 5 | 86.6468 | 18.2825 | 2018-05-03 06:00 | 6 | 5 | 0 | 0 | 2018-05-03 06:00 | 6 | 5 | 0 | 0 | 2018-05-03 06:00 | 6 | 5 | 0 | 0
2018-05-03 07:00 | 7 | 5 | 86.6361 | 18.2802 | 2018-05-03 07:00 | 7 | 5 | 0 | 0 | 2018-05-03 07:00 | 7 | 5 | 0 | 0 | 2018-05-03 07:00 | 7 | 5 | 0 | 0
2018-05-03 08:00 | 8 | 5 | 86.6819 | 18.2899 | 2018-05-03 08:00 | 8 | 5 | 0 | 0 | 2018-05-03 08:00 | 8 | 5 | 0 | 0 | 2018-05-03 08:00 | 8 | 5 | 0 | 0
2018-05-03 09:00 | 9 | 5 | 86.7094 | 18.2957 | 2018-05-03 09:00 | 9 | 5 | 0 | 0 | 2018-05-03 09:00 | 9 | 5 | 0 | 0 | 2018-05-03 09:00 | 9 | 5 | 0 | 0
2018-05-03 10:00 | 10 | 5 | 86.7933 | 18.3134 | 2018-05-03 10:00 | 10 | 5 | 0 | 0 | 2018-05-03 10:00 | 10 | 5 | 0 | 0 | 2018-05-03 10:00 | 10 | 5 | 0 | 0
2018-05-03 11:00 | 11 | 5 | 86.8009 | 18.315 | 2018-05-03 11:00 | 11 | 5 | 0 | 0 | 2018-05-03 11:00 | 11 | 5 | 0 | 0 | 2018-05-03 11:00 | 11 | 5 | 0 | 0
2018-05-03 12:00 | 12 | 5 | 86.6728 | 18.288 | 2018-05-03 12:00 | 12 | 5 | 0 | 0 | 2018-05-03 12:00 | 12 | 5 | 0 | 0 | 2018-05-03 12:00 | 12 | 5 | 0 | 0
2018-05-03 13:00 | 13 | 5 | 86.6316 | 18.2793 | 2018-05-03 13:00 | 13 | 5 | 0 | 0 | 2018-05-03 13:00 | 13 | 5 | 0 | 0 | 2018-05-03 13:00 | 13 | 5 | 0 | 0
2018-05-03 14:00 | 14 | 5 | 86.6316 | 18.2793 | 2018-05-03 14:00 | 14 | 5 | 0 | 0 | 2018-05-03 14:00 | 14 | 5 | 0 | 0 | 2018-05-03 14:00 | 14 | 5 | 0 | 0
2018-05-03 15:00 | 15 | 5 | 86.6636 | 18.286 | 2018-05-03 15:00 | 15 | 5 | 0 | 0 | 2018-05-03 15:00 | 15 | 5 | 0 | 0 | 2018-05-03 15:00 | 15 | 5 | 0 | 0
2018-05-03 16:00 | 16 | 5 | 86.5568 | 18.2635 | 2018-05-03 16:00 | 16 | 5 | 0 | 0 | 2018-05-03 16:00 | 16 | 5 | 0 | 0 | 2018-05-03 16:00 | 16 | 5 | 0 | 0
2018-05-03 17:00 | 17 | 5 | 86.6865 | 18.2909 | 2018-05-03 17:00 | 17 | 5 | 0 | 0 | 2018-05-03 17:00 | 17 | 5 | 0 | 0 | 2018-05-03 17:00 | 17 | 5 | 0 | 0
2018-05-03 18:00 | 18 | 5 | 86.7262 | 18.2992 | 2018-05-03 18:00 | 18 | 5 | 0 | 0 | 2018-05-03 18:00 | 18 | 5 | 0 | 0 | 2018-05-03 18:00 | 18 | 5 | 0 | 0
2018-05-03 19:00 | 19 | 5 | 86.5187 | 18.2554 | 2018-05-03 19:00 | 19 | 5 | 0 | 0 | 2018-05-03 19:00 | 19 | 5 | 0 | 0 | 2018-05-03 19:00 | 19 | 5 | 0 | 0
2018-05-03 20:00 | 20 | 5 | 86.5766 | 18.2677 | 2018-05-03 20:00 | 20 | 5 | 0 | 0 | 2018-05-03 20:00 | 20 | 5 | 0 | 0 | 2018-05-03 20:00 | 20 | 5 | 0 | 0
2018-05-03 21:00 | 21 | 5 | 86.6194 | 18.2767 | 2018-05-03 21:00 | 21 | 5 | 0 | 0 | 2018-05-03 21:00 | 21 | 5 | 0 | 0 | 2018-05-03 21:00 | 21 | 5 | 0 | 0
2018-05-03 22:00 | 22 | 5 | 86.6743 | 18.2883 | 2018-05-03 22:00 | 22 | 5 | 0 | 0 | 2018-05-03 22:00 | 22 | 5 | 0 | 0 | 2018-05-03 22:00 | 22 | 5 | 0 | 0
2018-05-03 23:00 | 23 | 5 | 86.5644 | 18.2651 | 2018-05-03 23:00 | 23 | 5 | 0 | 0 | 2018-05-03 23:00 | 23 | 5 | 0 | 0 | 2018-05-03 23:00 | 23 | 5 | 0 | 0
2018-05-04 | 0 | 6 | 86.2226 | 18.193 | 2018-05-04 | 0 | 6 | 86.688 | 17.6583 | 2018-05-04 | 0 | 6 | 0 | 0 | 2018-05-04 | 0 | 6 | 32.9414 | 6.9177
2018-05-04 01:00 | 1 | 6 | 86.1128 | 18.1698 | 2018-05-04 01:00 | 1 | 6 | 86.5232 | 17.6248 | 2018-05-04 01:00 | 1 | 6 | 0 | 0 | 2018-05-04 01:00 | 1 | 6 | 32.8788 | 6.9046
2018-05-04 02:00 | 2 | 6 | 86.2791 | 18.2049 | 2018-05-04 02:00 | 2 | 6 | 86.6896 | 17.6587 | 2018-05-04 02:00 | 2 | 6 | 0 | 0 | 2018-05-04 02:00 | 2 | 6 | 32.942 | 6.9178
2018-05-04 03:00 | 3 | 6 | 86.0014 | 18.1463 | 2018-05-04 03:00 | 3 | 6 | 86.4485 | 17.6096 | 2018-05-04 03:00 | 3 | 6 | 0 | 0 | 2018-05-04 03:00 | 3 | 6 | 32.8504 | 6.8986
2018-05-04 04:00 | 4 | 6 | 86.0533 | 18.1572 | 2018-05-04 04:00 | 4 | 6 | 86.4347 | 17.6067 | 2018-05-04 04:00 | 4 | 6 | 0 | 0 | 2018-05-04 04:00 | 4 | 6 | 32.8452 | 6.8975
2018-05-04 05:00 | 5 | 6 | 86.2257 | 18.1936 | 2018-05-04 05:00 | 5 | 6 | 86.6117 | 17.6428 | 2018-05-04 05:00 | 5 | 6 | 0 | 0 | 2018-05-04 05:00 | 5 | 6 | 32.9124 | 6.9116
2018-05-04 06:00 | 6 | 6 | 86.4332 | 18.2374 | 2018-05-04 06:00 | 6 | 6 | 86.9352 | 17.7087 | 2018-05-04 06:00 | 6 | 6 | 0 | 0 | 2018-05-04 06:00 | 6 | 6 | 33.0354 | 6.9374
2018-05-04 07:00 | 7 | 6 | 86.5873 | 18.2699 | 2018-05-04 07:00 | 7 | 6 | 87.0619 | 17.7345 | 2018-05-04 07:00 | 7 | 6 | 0 | 0 | 2018-05-04 07:00 | 7 | 6 | 33.0835 | 6.9475
2018-05-04 08:00 | 8 | 6 | 86.3691 | 18.2239 | 2018-05-04 08:00 | 8 | 6 | 86.7811 | 17.6773 | 2018-05-04 08:00 | 8 | 6 | 0 | 0 | 2018-05-04 08:00 | 8 | 6 | 32.9768 | 6.9251
2018-05-04 09:00 | 9 | 6 | 86.334 | 18.2165 | 2018-05-04 09:00 | 9 | 6 | 86.7399 | 17.6689 | 2018-05-04 09:00 | 9 | 6 | 0 | 0 | 2018-05-04 09:00 | 9 | 6 | 32.9612 | 6.9218
2018-05-04 10:00 | 10 | 6 | 86.5126 | 18.2542 | 2018-05-04 10:00 | 10 | 6 | 86.862 | 17.6938 | 2018-05-04 10:00 | 10 | 6 | 0 | 0 | 2018-05-04 10:00 | 10 | 6 | 33.0076 | 6.9316
2018-05-04 11:00 | 11 | 6 | 86.5003 | 18.2516 | 2018-05-04 11:00 | 11 | 6 | 86.9306 | 17.7078 | 2018-05-04 11:00 | 11 | 6 | 0 | 0 | 2018-05-04 11:00 | 11 | 6 | 33.0336 | 6.9371
2018-05-04 12:00 | 12 | 6 | 86.7002 | 18.2937 | 2018-05-04 12:00 | 12 | 6 | 87.1412 | 17.7507 | 2018-05-04 12:00 | 12 | 6 | 0 | 0 | 2018-05-04 12:00 | 12 | 6 | 33.1137 | 6.9539
2018-05-04 13:00 | 13 | 6 | 86.363 | 18.2226 | 2018-05-04 13:00 | 13 | 6 | 86.8009 | 17.6813 | 2018-05-04 13:00 | 13 | 6 | 0 | 0 | 2018-05-04 13:00 | 13 | 6 | 32.9843 | 6.9267
2018-05-04 14:00 | 14 | 6 | 86.4408 | 18.239 | 2018-05-04 14:00 | 14 | 6 | 86.8635 | 17.6941 | 2018-05-04 14:00 | 14 | 6 | 0 | 0 | 2018-05-04 14:00 | 14 | 6 | 33.0081 | 6.9317
2018-05-04 15:00 | 15 | 6 | 86.2943 | 18.2081 | 2018-05-04 15:00 | 15 | 6 | 86.6743 | 17.6556 | 2018-05-04 15:00 | 15 | 6 | 0 | 0 | 2018-05-04 15:00 | 15 | 6 | 32.9362 | 6.9166
2018-05-04 16:00 | 16 | 6 | 86.3706 | 18.2242 | 2018-05-04 16:00 | 16 | 6 | 86.7491 | 17.6708 | 2018-05-04 16:00 | 16 | 6 | 0 | 0 | 2018-05-04 16:00 | 16 | 6 | 32.9647 | 6.9226
2018-05-04 17:00 | 17 | 6 | 86.2882 | 18.2068 | 2018-05-04 17:00 | 17 | 6 | 86.7445 | 17.6699 | 2018-05-04 17:00 | 17 | 6 | 0 | 0 | 2018-05-04 17:00 | 17 | 6 | 32.9629 | 6.9222
2018-05-04 18:00 | 18 | 6 | 86.1875 | 18.1856 | 2018-05-04 18:00 | 18 | 6 | 86.6667 | 17.654 | 2018-05-04 18:00 | 18 | 6 | 0 | 0 | 2018-05-04 18:00 | 18 | 6 | 32.9333 | 6.916
2018-05-04 19:00 | 19 | 6 | 86.099 | 18.1669 | 2018-05-04 19:00 | 19 | 6 | 86.5431 | 17.6288 | 2018-05-04 19:00 | 19 | 6 | 0 | 0 | 2018-05-04 19:00 | 19 | 6 | 32.8864 | 6.9061
2018-05-04 20:00 | 20 | 6 | 86.1997 | 18.1881 | 2018-05-04 20:00 | 20 | 6 | 86.5187 | 17.6239 | 2018-05-04 20:00 | 20 | 6 | 0 | 0 | 2018-05-04 20:00 | 20 | 6 | 32.8771 | 6.9042
2018-05-04 21:00 | 21 | 6 | 86.3767 | 18.2255 | 2018-05-04 21:00 | 21 | 6 | 86.7247 | 17.6658 | 2018-05-04 21:00 | 21 | 6 | 0 | 0 | 2018-05-04 21:00 | 21 | 6 | 32.9554 | 6.9206
2018-05-04 22:00 | 22 | 6 | 86.3691 | 18.2239 | 2018-05-04 22:00 | 22 | 6 | 86.7659 | 17.6742 | 2018-05-04 22:00 | 22 | 6 | 0 | 0 | 2018-05-04 22:00 | 22 | 6 | 32.971 | 6.9239
2018-05-04 23:00 | 23 | 6 | 86.4012 | 18.2307 | 2018-05-04 23:00 | 23 | 6 | 86.7918 | 17.6795 | 2018-05-04 23:00 | 23 | 6 | 0 | 0 | 2018-05-04 23:00 | 23 | 6 | 32.9809 | 6.926
2018-05-05 | 0 | 7 | 86.0121 | 18.1486 | 2018-05-05 | 0 | 7 | 0 | 0 | 2018-05-05 | 0 | 7 | 86.5507 | 18.3487 | 2018-05-05 | 0 | 7 | 32.8893 | 6.9067
2018-05-05 01:00 | 1 | 7 | 85.919 | 18.1289 | 2018-05-05 01:00 | 1 | 7 | 0 | 0 | 2018-05-05 01:00 | 1 | 7 | 86.5324 | 18.3449 | 2018-05-05 01:00 | 1 | 7 | 32.8823 | 6.9053
2018-05-05 02:00 | 2 | 7 | 86.0533 | 18.1572 | 2018-05-05 02:00 | 2 | 7 | 0 | 0 | 2018-05-05 02:00 | 2 | 7 | 86.6453 | 18.3688 | 2018-05-05 02:00 | 2 | 7 | 32.9252 | 6.9143
2018-05-05 03:00 | 3 | 7 | 86.1677 | 18.1814 | 2018-05-05 03:00 | 3 | 7 | 0 | 0 | 2018-05-05 03:00 | 3 | 7 | 86.7002 | 18.3804 | 2018-05-05 03:00 | 3 | 7 | 32.9461 | 6.9187
2018-05-05 04:00 | 4 | 7 | 86.3081 | 18.211 | 2018-05-05 04:00 | 4 | 7 | 0 | 0 | 2018-05-05 04:00 | 4 | 7 | 86.8513 | 18.4125 | 2018-05-05 04:00 | 4 | 7 | 33.0035 | 6.9307
2018-05-05 05:00 | 5 | 7 | 86.2562 | 18.2001 | 2018-05-05 05:00 | 5 | 7 | 0 | 0 | 2018-05-05 05:00 | 5 | 7 | 86.8605 | 18.4144 | 2018-05-05 05:00 | 5 | 7 | 33.007 | 6.9315
2018-05-05 06:00 | 6 | 7 | 86.1234 | 18.172 | 2018-05-05 06:00 | 6 | 7 | 0 | 0 | 2018-05-05 06:00 | 6 | 7 | 86.6682 | 18.3737 | 2018-05-05 06:00 | 6 | 7 | 32.9339 | 6.9161
2018-05-05 07:00 | 7 | 7 | 86.1906 | 18.1862 | 2018-05-05 07:00 | 7 | 7 | 0 | 0 | 2018-05-05 07:00 | 7 | 7 | 86.7247 | 18.3856 | 2018-05-05 07:00 | 7 | 7 | 32.9554 | 6.9206
2018-05-05 08:00 | 8 | 7 | 86.36 | 18.222 | 2018-05-05 08:00 | 8 | 7 | 0 | 0 | 2018-05-05 08:00 | 8 | 7 | 86.952 | 18.4338 | 2018-05-05 08:00 | 8 | 7 | 33.0418 | 6.9388
2018-05-05 09:00 | 9 | 7 | 86.4912 | 18.2496 | 2018-05-05 09:00 | 9 | 7 | 0 | 0 | 2018-05-05 09:00 | 9 | 7 | 87.0588 | 18.4565 | 2018-05-05 09:00 | 9 | 7 | 33.0823 | 6.9473
2018-05-05 10:00 | 10 | 7 | 86.1982 | 18.1878 | 2018-05-05 10:00 | 10 | 7 | 0 | 0 | 2018-05-05 10:00 | 10 | 7 | 86.6392 | 18.3675 | 2018-05-05 10:00 | 10 | 7 | 32.9229 | 6.9138
2018-05-05 11:00 | 11 | 7 | 86.1707 | 18.182 | 2018-05-05 11:00 | 11 | 7 | 0 | 0 | 2018-05-05 11:00 | 11 | 7 | 86.8849 | 18.4196 | 2018-05-05 11:00 | 11 | 7 | 33.0163 | 6.9334
2018-05-05 12:00 | 12 | 7 | 86.5019 | 18.2519 | 2018-05-05 12:00 | 12 | 7 | 0 | 0 | 2018-05-05 12:00 | 12 | 7 | 87.1504 | 18.4759 | 2018-05-05 12:00 | 12 | 7 | 33.1172 | 6.9546
2018-05-05 13:00 | 13 | 7 | 86.6148 | 18.2757 | 2018-05-05 13:00 | 13 | 7 | 0 | 0 | 2018-05-05 13:00 | 13 | 7 | 87.3167 | 18.5111 | 2018-05-05 13:00 | 13 | 7 | 33.1803 | 6.9679
2018-05-05 14:00 | 14 | 7 | 86.4439 | 18.2397 | 2018-05-05 14:00 | 14 | 7 | 0 | 0 | 2018-05-05 14:00 | 14 | 7 | 87.0832 | 18.4616 | 2018-05-05 14:00 | 14 | 7 | 33.0916 | 6.9492
2018-05-05 15:00 | 15 | 7 | 86.5522 | 18.2625 | 2018-05-05 15:00 | 15 | 7 | 0 | 0 | 2018-05-05 15:00 | 15 | 7 | 87.2938 | 18.5063 | 2018-05-05 15:00 | 15 | 7 | 33.1716 | 6.966
2018-05-05 16:00 | 16 | 7 | 86.5644 | 18.2651 | 2018-05-05 16:00 | 16 | 7 | 0 | 0 | 2018-05-05 16:00 | 16 | 7 | 87.3579 | 18.5199 | 2018-05-05 16:00 | 16 | 7 | 33.196 | 6.9712
2018-05-05 17:00 | 17 | 7 | 86.7445 | 18.3031 | 2018-05-05 17:00 | 17 | 7 | 0 | 0 | 2018-05-05 17:00 | 17 | 7 | 87.57 | 18.5648 | 2018-05-05 17:00 | 17 | 7 | 33.2766 | 6.9881
2018-05-05 18:00 | 18 | 7 | 86.4668 | 18.2445 | 2018-05-05 18:00 | 18 | 7 | 0 | 0 | 2018-05-05 18:00 | 18 | 7 | 87.3014 | 18.5079 | 2018-05-05 18:00 | 18 | 7 | 33.1745 | 6.9667
2018-05-05 19:00 | 19 | 7 | 86.3661 | 18.2232 | 2018-05-05 19:00 | 19 | 7 | 0 | 0 | 2018-05-05 19:00 | 19 | 7 | 87.0954 | 18.4642 | 2018-05-05 19:00 | 19 | 7 | 33.0963 | 6.9502
2018-05-05 20:00 | 20 | 7 | 86.1173 | 18.1708 | 2018-05-05 20:00 | 20 | 7 | 0 | 0 | 2018-05-05 20:00 | 20 | 7 | 86.891 | 18.4209 | 2018-05-05 20:00 | 20 | 7 | 33.0186 | 6.9339
2018-05-05 21:00 | 21 | 7 | 86.1555 | 18.1788 | 2018-05-05 21:00 | 21 | 7 | 0 | 0 | 2018-05-05 21:00 | 21 | 7 | 86.9245 | 18.428 | 2018-05-05 21:00 | 21 | 7 | 33.0313 | 6.9366
2018-05-05 22:00 | 22 | 7 | 86.2211 | 18.1927 | 2018-05-05 22:00 | 22 | 7 | 0 | 0 | 2018-05-05 22:00 | 22 | 7 | 87.0054 | 18.4451 | 2018-05-05 22:00 | 22 | 7 | 33.0621 | 6.943
2018-05-05 23:00 | 23 | 7 | 86.2226 | 18.193 | 2018-05-05 23:00 | 23 | 7 | 0 | 0 | 2018-05-05 23:00 | 23 | 7 | 87.0787 | 18.4607 | 2018-05-05 23:00 | 23 | 7 | 33.0899 | 6.9489
2018-05-06 | 0 | 1 | 86.2364 | 18.1959 | 2018-05-06 | 0 | 1 | 86.7994 | 17.681 | 2018-05-06 | 0 | 1 | 0 | 0 | 2018-05-06 | 0 | 1 | 32.9838 | 6.9266
2018-05-06 01:00 | 1 | 1 | 86.3188 | 18.2133 | 2018-05-06 01:00 | 1 | 1 | 86.952 | 17.7121 | 2018-05-06 01:00 | 1 | 1 | 0 | 0 | 2018-05-06 01:00 | 1 | 1 | 33.0418 | 6.9388
2018-05-06 02:00 | 2 | 1 | 86.2119 | 18.1907 | 2018-05-06 02:00 | 2 | 1 | 86.8177 | 17.6848 | 2018-05-06 02:00 | 2 | 1 | 0 | 0 | 2018-05-06 02:00 | 2 | 1 | 32.9907 | 6.9281
2018-05-06 03:00 | 3 | 1 | 86.1845 | 18.1849 | 2018-05-06 03:00 | 3 | 1 | 86.7857 | 17.6782 | 2018-05-06 03:00 | 3 | 1 | 0 | 0 | 2018-05-06 03:00 | 3 | 1 | 32.9786 | 6.9255
2018-05-06 04:00 | 4 | 1 | 86.2455 | 18.1978 | 2018-05-06 04:00 | 4 | 1 | 86.833 | 17.6879 | 2018-05-06 04:00 | 4 | 1 | 0 | 0 | 2018-05-06 04:00 | 4 | 1 | 32.9965 | 6.9293
2018-05-06 05:00 | 5 | 1 | 86.2333 | 18.1952 | 2018-05-06 05:00 | 5 | 1 | 86.833 | 17.6879 | 2018-05-06 05:00 | 5 | 1 | 0 | 0 | 2018-05-06 05:00 | 5 | 1 | 32.9965 | 6.9293
2018-05-06 06:00 | 6 | 1 | 86.2776 | 18.2046 | 2018-05-06 06:00 | 6 | 1 | 86.8528 | 17.6919 | 2018-05-06 06:00 | 6 | 1 | 0 | 0 | 2018-05-06 06:00 | 6 | 1 | 33.0041 | 6.9309
2018-05-06 07:00 | 7 | 1 | 86.2867 | 18.2065 | 2018-05-06 07:00 | 7 | 1 | 86.8452 | 17.6904 | 2018-05-06 07:00 | 7 | 1 | 0 | 0 | 2018-05-06 07:00 | 7 | 1 | 33.0012 | 6.9302
2018-05-06 08:00 | 8 | 1 | 86.2989 | 18.2091 | 2018-05-06 08:00 | 8 | 1 | 86.9032 | 17.7022 | 2018-05-06 08:00 | 8 | 1 | 0 | 0 | 2018-05-06 08:00 | 8 | 1 | 33.0232 | 6.9349
2018-05-06 09:00 | 9 | 1 | 86.2867 | 18.2065 | 2018-05-06 09:00 | 9 | 1 | 86.8162 | 17.6845 | 2018-05-06 09:00 | 9 | 1 | 0 | 0 | 2018-05-06 09:00 | 9 | 1 | 32.9902 | 6.9279
2018-05-06 10:00 | 10 | 1 | 86.2882 | 18.2068 | 2018-05-06 10:00 | 10 | 1 | 86.8528 | 17.6919 | 2018-05-06 10:00 | 10 | 1 | 0 | 0 | 2018-05-06 10:00 | 10 | 1 | 33.0041 | 6.9309
2018-05-06 11:00 | 11 | 1 | 86.1845 | 18.1849 | 2018-05-06 11:00 | 11 | 1 | 86.743 | 17.6695 | 2018-05-06 11:00 | 11 | 1 | 0 | 0 | 2018-05-06 11:00 | 11 | 1 | 32.9623 | 6.9221
2018-05-06 12:00 | 12 | 1 | 86.1418 | 18.1759 | 2018-05-06 12:00 | 12 | 1 | 86.714 | 17.6636 | 2018-05-06 12:00 | 12 | 1 | 0 | 0 | 2018-05-06 12:00 | 12 | 1 | 32.9513 | 6.9198
2018-05-06 13:00 | 13 | 1 | 86.1479 | 18.1772 | 2018-05-06 13:00 | 13 | 1 | 86.7659 | 17.6742 | 2018-05-06 13:00 | 13 | 1 | 0 | 0 | 2018-05-06 13:00 | 13 | 1 | 32.971 | 6.9239
2018-05-06 14:00 | 14 | 1 | 86.1112 | 18.1695 | 2018-05-06 14:00 | 14 | 1 | 86.7018 | 17.6612 | 2018-05-06 14:00 | 14 | 1 | 0 | 0 | 2018-05-06 14:00 | 14 | 1 | 32.9467 | 6.9188
2018-05-06 15:00 | 15 | 1 | 86.2455 | 18.1978 | 2018-05-06 15:00 | 15 | 1 | 86.8482 | 17.691 | 2018-05-06 15:00 | 15 | 1 | 0 | 0 | 2018-05-06 15:00 | 15 | 1 | 33.0023 | 6.9305
2018-05-06 16:00 | 16 | 1 | 86.3447 | 18.2187 | 2018-05-06 16:00 | 16 | 1 | 86.9398 | 17.7096 | 2018-05-06 16:00 | 16 | 1 | 0 | 0 | 2018-05-06 16:00 | 16 | 1 | 33.0371 | 6.9378
2018-05-06 17:00 | 17 | 1 | 86.4805 | 18.2474 | 2018-05-06 17:00 | 17 | 1 | 86.9856 | 17.719 | 2018-05-06 17:00 | 17 | 1 | 0 | 0 | 2018-05-06 17:00 | 17 | 1 | 33.0545 | 6.9415
2018-05-06 18:00 | 18 | 1 | 86.4332 | 18.2374 | 2018-05-06 18:00 | 18 | 1 | 86.92 | 17.7056 | 2018-05-06 18:00 | 18 | 1 | 0 | 0 | 2018-05-06 18:00 | 18 | 1 | 33.0296 | 6.9362
2018-05-06 19:00 | 19 | 1 | 85.6794 | 18.0784 | 2018-05-06 19:00 | 19 | 1 | 85.9266 | 17.5032 | 2018-05-06 19:00 | 19 | 1 | 0 | 0 | 2018-05-06 19:00 | 19 | 1 | 32.6521 | 6.8569
2018-05-06 20:00 | 20 | 1 | 86.3294 | 18.2155 | 2018-05-06 20:00 | 20 | 1 | 86.5888 | 17.6381 | 2018-05-06 20:00 | 20 | 1 | 0 | 0 | 2018-05-06 20:00 | 20 | 1 | 32.9037 | 6.9098
2018-05-06 21:00 | 21 | 1 | 86.3569 | 18.2213 | 2018-05-06 21:00 | 21 | 1 | 86.6728 | 17.6552 | 2018-05-06 21:00 | 21 | 1 | 0 | 0 | 2018-05-06 21:00 | 21 | 1 | 32.9357 | 6.9165
2018-05-06 22:00 | 22 | 1 | 86.4881 | 18.249 | 2018-05-06 22:00 | 22 | 1 | 86.8086 | 17.6829 | 2018-05-06 22:00 | 22 | 1 | 0 | 0 | 2018-05-06 22:00 | 22 | 1 | 32.9873 | 6.9273
2018-05-06 23:00 | 23 | 1 | 86.4332 | 18.2374 | 2018-05-06 23:00 | 23 | 1 | 86.7353 | 17.668 | 2018-05-06 23:00 | 23 | 1 | 0 | 0 | 2018-05-06 23:00 | 23 | 1 | 32.9594 | 6.9215
2018-05-07 | 0 | 2 | 86.4088 | 18.2323 | 2018-05-07 | 0 | 2 | 86.7002 | 17.6608 | 2018-05-07 | 0 | 2 | 86.9352 | 18.4303 | 2018-05-07 | 0 | 2 | 65.9815 | 13.8561
2018-05-07 01:00 | 1 | 2 | 86.0426 | 18.155 | 2018-05-07 01:00 | 1 | 2 | 86.3127 | 17.5819 | 2018-05-07 01:00 | 1 | 2 | 86.5278 | 18.3439 | 2018-05-07 01:00 | 1 | 2 | 65.6794 | 13.7927
2018-05-07 02:00 | 2 | 2 | 86.392 | 18.2287 | 2018-05-07 02:00 | 2 | 2 | 86.6392 | 17.6484 | 2018-05-07 02:00 | 2 | 2 | 86.8421 | 18.4105 | 2018-05-07 02:00 | 2 | 2 | 65.9229 | 13.8438
2018-05-07 03:00 | 3 | 2 | 86.2776 | 18.2046 | 2018-05-07 03:00 | 3 | 2 | 86.5766 | 17.6357 | 2018-05-07 03:00 | 3 | 2 | 86.7536 | 18.3918 | 2018-05-07 03:00 | 3 | 2 | 65.8655 | 13.8317
2018-05-07 04:00 | 4 | 2 | 86.5034 | 18.2522 | 2018-05-07 04:00 | 4 | 2 | 86.8849 | 17.6985 | 2018-05-07 04:00 | 4 | 2 | 87.0283 | 18.45 | 2018-05-07 04:00 | 4 | 2 | 66.087 | 13.8783
2018-05-07 05:00 | 5 | 2 | 86.3661 | 18.2232 | 2018-05-07 05:00 | 5 | 2 | 86.772 | 17.6755 | 2018-05-07 05:00 | 5 | 2 | 87.0054 | 18.4451 | 2018-05-07 05:00 | 5 | 2 | 66.0354 | 13.8674
2018-05-07 06:00 | 6 | 2 | 86.2898 | 18.2071 | 2018-05-07 06:00 | 6 | 2 | 86.6499 | 17.6506 | 2018-05-07 06:00 | 6 | 2 | 86.8147 | 18.4047 | 2018-05-07 06:00 | 6 | 2 | 65.9165 | 13.8425
2018-05-07 07:00 | 7 | 2 | 86.2043 | 18.1891 | 2018-05-07 07:00 | 7 | 2 | 86.5278 | 17.6257 | 2018-05-07 07:00 | 7 | 2 | 86.7079 | 18.3821 | 2018-05-07 07:00 | 7 | 2 | 65.8296 | 13.8242
2018-05-07 08:00 | 8 | 2 | 86.3355 | 18.2168 | 2018-05-07 08:00 | 8 | 2 | 86.5461 | 17.6294 | 2018-05-07 08:00 | 8 | 2 | 86.8025 | 18.4021 | 2018-05-07 08:00 | 8 | 2 | 65.8725 | 13.8332
2018-05-07 09:00 | 9 | 2 | 86.3798 | 18.2261 | 2018-05-07 09:00 | 9 | 2 | 86.7262 | 17.6661 | 2018-05-07 09:00 | 9 | 2 | 86.8711 | 18.4167 | 2018-05-07 09:00 | 9 | 2 | 65.967 | 13.8531
2018-05-07 10:00 | 10 | 2 | 86.2272 | 18.1939 | 2018-05-07 10:00 | 10 | 2 | 86.5156 | 17.6232 | 2018-05-07 10:00 | 10 | 2 | 86.714 | 18.3834 | 2018-05-07 10:00 | 10 | 2 | 65.8272 | 13.8237
2018-05-07 11:00 | 11 | 2 | 86.2119 | 18.1907 | 2018-05-07 11:00 | 11 | 2 | 86.5141 | 17.6229 | 2018-05-07 11:00 | 11 | 2 | 86.7201 | 18.3847 | 2018-05-07 11:00 | 11 | 2 | 65.829 | 13.8241
2018-05-07 12:00 | 12 | 2 | 86.389 | 18.2281 | 2018-05-07 12:00 | 12 | 2 | 86.6835 | 17.6574 | 2018-05-07 12:00 | 12 | 2 | 86.8574 | 18.4138 | 2018-05-07 12:00 | 12 | 2 | 65.9455 | 13.8486
2018-05-07 13:00 | 13 | 2 | 86.4027 | 18.231 | 2018-05-07 13:00 | 13 | 2 | 86.6224 | 17.645 | 2018-05-07 13:00 | 13 | 2 | 86.7475 | 18.3905 | 2018-05-07 13:00 | 13 | 2 | 65.8806 | 13.8349
2018-05-07 14:00 | 14 | 2 | 86.3783 | 18.2258 | 2018-05-07 14:00 | 14 | 2 | 86.6606 | 17.6528 | 2018-05-07 14:00 | 14 | 2 | 86.7903 | 18.3995 | 2018-05-07 14:00 | 14 | 2 | 65.9113 | 13.8414
2018-05-07 15:00 | 15 | 2 | 86.3355 | 18.2168 | 2018-05-07 15:00 | 15 | 2 | 86.5248 | 17.6251 | 2018-05-07 15:00 | 15 | 2 | 86.7384 | 18.3885 | 2018-05-07 15:00 | 15 | 2 | 65.84 | 13.8264
2018-05-07 16:00 | 16 | 2 | 86.3493 | 18.2197 | 2018-05-07 16:00 | 16 | 2 | 86.4912 | 17.6183 | 2018-05-07 16:00 | 16 | 2 | 86.685 | 18.3772 | 2018-05-07 16:00 | 16 | 2 | 65.807 | 13.8195
2018-05-07 17:00 | 17 | 2 | 86.244 | 18.1975 | 2018-05-07 17:00 | 17 | 2 | 86.4683 | 17.6136 | 2018-05-07 17:00 | 17 | 2 | 86.6743 | 18.375 | 2018-05-07 17:00 | 17 | 2 | 65.7942 | 13.8168
2018-05-07 18:00 | 18 | 2 | 86.3142 | 18.2123 | 2018-05-07 18:00 | 18 | 2 | 86.4378 | 17.6074 | 2018-05-07 18:00 | 18 | 2 | 86.5934 | 18.3578 | 2018-05-07 18:00 | 18 | 2 | 65.7519 | 13.8079
2018-05-07 19:00 | 19 | 2 | 86.2089 | 18.1901 | 2018-05-07 19:00 | 19 | 2 | 86.3508 | 17.5897 | 2018-05-07 19:00 | 19 | 2 | 86.5583 | 18.3504 | 2018-05-07 19:00 | 19 | 2 | 65.7055 | 13.7981
2018-05-07 20:00 | 20 | 2 | 86.2181 | 18.192 | 2018-05-07 20:00 | 20 | 2 | 86.4836 | 17.6167 | 2018-05-07 20:00 | 20 | 2 | 86.6896 | 18.3782 | 2018-05-07 20:00 | 20 | 2 | 65.8058 | 13.8192
2018-05-07 21:00 | 21 | 2 | 86.1494 | 18.1775 | 2018-05-07 21:00 | 21 | 2 | 86.4759 | 17.6151 | 2018-05-07 21:00 | 21 | 2 | 86.63 | 18.3656 | 2018-05-07 21:00 | 21 | 2 | 65.7802 | 13.8139
2018-05-07 22:00 | 22 | 2 | 86.2593 | 18.2007 | 2018-05-07 22:00 | 22 | 2 | 86.5522 | 17.6307 | 2018-05-07 22:00 | 22 | 2 | 86.6468 | 18.3691 | 2018-05-07 22:00 | 22 | 2 | 65.8156 | 13.8213
2018-05-07 23:00 | 23 | 2 | 86.4424 | 18.2393 | 2018-05-07 23:00 | 23 | 2 | 86.8055 | 17.6823 | 2018-05-07 23:00 | 23 | 2 | 86.8864 | 18.4199 | 2018-05-07 23:00 | 23 | 2 | 66.0029 | 13.8606
2018-05-08 | 0 | 3 | 86.4637 | 18.2438 | 2018-05-08 | 0 | 3 | 0 | 0 | 2018-05-08 | 0 | 3 | 0 | 0 | 2018-05-08 | 0 | 3 | 0 | 0
2018-05-08 01:00 | 1 | 3 | 86.5629 | 18.2648 | 2018-05-08 01:00 | 1 | 3 | 0 | 0 | 2018-05-08 01:00 | 1 | 3 | 0 | 0 | 2018-05-08 01:00 | 1 | 3 | 0 | 0
2018-05-08 02:00 | 2 | 3 | 86.3706 | 18.2242 | 2018-05-08 02:00 | 2 | 3 | 0 | 0 | 2018-05-08 02:00 | 2 | 3 | 0 | 0 | 2018-05-08 02:00 | 2 | 3 | 0 | 0
2018-05-08 03:00 | 3 | 3 | 86.3523 | 18.2203 | 2018-05-08 03:00 | 3 | 3 | 0 | 0 | 2018-05-08 03:00 | 3 | 3 | 0 | 0 | 2018-05-08 03:00 | 3 | 3 | 0 | 0
2018-05-08 04:00 | 4 | 3 | 86.3676 | 18.2236 | 2018-05-08 04:00 | 4 | 3 | 0 | 0 | 2018-05-08 04:00 | 4 | 3 | 0 | 0 | 2018-05-08 04:00 | 4 | 3 | 0 | 0
2018-05-08 05:00 | 5 | 3 | 86.4027 | 18.231 | 2018-05-08 05:00 | 5 | 3 | 0 | 0 | 2018-05-08 05:00 | 5 | 3 | 0 | 0 | 2018-05-08 05:00 | 5 | 3 | 0 | 0
2018-05-08 06:00 | 6 | 3 | 86.4652 | 18.2442 | 2018-05-08 06:00 | 6 | 3 | 0 | 0 | 2018-05-08 06:00 | 6 | 3 | 0 | 0 | 2018-05-08 06:00 | 6 | 3 | 0 | 0
2018-05-08 07:00 | 7 | 3 | 86.4012 | 18.2307 | 2018-05-08 07:00 | 7 | 3 | 0 | 0 | 2018-05-08 07:00 | 7 | 3 | 0 | 0 | 2018-05-08 07:00 | 7 | 3 | 0 | 0
2018-05-08 08:00 | 8 | 3 | 86.4515 | 18.2413 | 2018-05-08 08:00 | 8 | 3 | 0 | 0 | 2018-05-08 08:00 | 8 | 3 | 0 | 0 | 2018-05-08 08:00 | 8 | 3 | 0 | 0
2018-05-08 09:00 | 9 | 3 | 86.2028 | 18.1888 | 2018-05-08 09:00 | 9 | 3 | 0 | 0 | 2018-05-08 09:00 | 9 | 3 | 0 | 0 | 2018-05-08 09:00 | 9 | 3 | 0 | 0
2018-05-08 10:00 | 10 | 3 | 86.2715 | 18.2033 | 2018-05-08 10:00 | 10 | 3 | 0 | 0 | 2018-05-08 10:00 | 10 | 3 | 0 | 0 | 2018-05-08 10:00 | 10 | 3 | 0 | 0
2018-05-08 11:00 | 11 | 3 | 86.7567 | 18.3057 | 2018-05-08 11:00 | 11 | 3 | 0 | 0 | 2018-05-08 11:00 | 11 | 3 | 0 | 0 | 2018-05-08 11:00 | 11 | 3 | 0 | 0
2018-05-08 12:00 | 12 | 3 | 86.6194 | 18.2767 | 2018-05-08 12:00 | 12 | 3 | 0 | 0 | 2018-05-08 12:00 | 12 | 3 | 0 | 0 | 2018-05-08 12:00 | 12 | 3 | 0 | 0
2018-05-08 13:00 | 13 | 3 | 86.6377 | 18.2806 | 2018-05-08 13:00 | 13 | 3 | 0 | 0 | 2018-05-08 13:00 | 13 | 3 | 0 | 0 | 2018-05-08 13:00 | 13 | 3 | 0 | 0
2018-05-08 14:00 | 14 | 3 | 86.8757 | 18.3308 | 2018-05-08 14:00 | 14 | 3 | 0 | 0 | 2018-05-08 14:00 | 14 | 3 | 0 | 0 | 2018-05-08 14:00 | 14 | 3 | 0 | 0
2018-05-08 15:00 | 15 | 3 | 86.7994 | 18.3147 | 2018-05-08 15:00 | 15 | 3 | 0 | 0 | 2018-05-08 15:00 | 15 | 3 | 0 | 0 | 2018-05-08 15:00 | 15 | 3 | 0 | 0
2018-05-08 16:00 | 16 | 3 | 86.7674 | 18.3079 | 2018-05-08 16:00 | 16 | 3 | 0 | 0 | 2018-05-08 16:00 | 16 | 3 | 0 | 0 | 2018-05-08 16:00 | 16 | 3 | 0 | 0
2018-05-08 17:00 | 17 | 3 | 86.7384 | 18.3018 | 2018-05-08 17:00 | 17 | 3 | 0 | 0 | 2018-05-08 17:00 | 17 | 3 | 0 | 0 | 2018-05-08 17:00 | 17 | 3 | 0 | 0
2018-05-08 18:00 | 18 | 3 | 86.7124 | 18.2963 | 2018-05-08 18:00 | 18 | 3 | 0 | 0 | 2018-05-08 18:00 | 18 | 3 | 0 | 0 | 2018-05-08 18:00 | 18 | 3 | 0 | 0
2018-05-08 19:00 | 19 | 3 | 86.8376 | 18.3227 | 2018-05-08 19:00 | 19 | 3 | 0 | 0 | 2018-05-08 19:00 | 19 | 3 | 0 | 0 | 2018-05-08 19:00 | 19 | 3 | 0 | 0
2018-05-08 20:00 | 20 | 3 | 86.627 | 18.2783 | 2018-05-08 20:00 | 20 | 3 | 0 | 0 | 2018-05-08 20:00 | 20 | 3 | 0 | 0 | 2018-05-08 20:00 | 20 | 3 | 0 | 0
2018-05-08 21:00 | 21 | 3 | 86.6239 | 18.2776 | 2018-05-08 21:00 | 21 | 3 | 0 | 0 | 2018-05-08 21:00 | 21 | 3 | 0 | 0 | 2018-05-08 21:00 | 21 | 3 | 0 | 0
2018-05-08 22:00 | 22 | 3 | 86.714 | 18.2967 | 2018-05-08 22:00 | 22 | 3 | 0 | 0 | 2018-05-08 22:00 | 22 | 3 | 0 | 0 | 2018-05-08 22:00 | 22 | 3 | 0 | 0
2018-05-08 23:00 | 23 | 3 | 86.8971 | 18.3353 | 2018-05-08 23:00 | 23 | 3 | 0 | 0 | 2018-05-08 23:00 | 23 | 3 | 0 | 0 | 2018-05-08 23:00 | 23 | 3 | 0 | 0
2018-05-09 | 0 | 4 | 0 | 0 | 2018-05-09 | 0 | 4 | 0 | 0 | 2018-05-09 | 0 | 4 | 86.6712 | 18.3743 | 2018-05-09 | 0 | 4 | 32.9351 | 6.9164
2018-05-09 01:00 | 1 | 4 | 0 | 0 | 2018-05-09 01:00 | 1 | 4 | 0 | 0 | 2018-05-09 01:00 | 1 | 4 | 86.511 | 18.3403 | 2018-05-09 01:00 | 1 | 4 | 32.8742 | 6.9036
2018-05-09 02:00 | 2 | 4 | 0 | 0 | 2018-05-09 02:00 | 2 | 4 | 0 | 0 | 2018-05-09 02:00 | 2 | 4 | 86.7628 | 18.3937 | 2018-05-09 02:00 | 2 | 4 | 32.9699 | 6.9237
2018-05-09 03:00 | 3 | 4 | 0 | 0 | 2018-05-09 03:00 | 3 | 4 | 0 | 0 | 2018-05-09 03:00 | 3 | 4 | 86.7384 | 18.3885 | 2018-05-09 03:00 | 3 | 4 | 32.9606 | 6.9217
2018-05-09 04:00 | 4 | 4 | 0 | 0 | 2018-05-09 04:00 | 4 | 4 | 0 | 0 | 2018-05-09 04:00 | 4 | 4 | 86.8376 | 18.4096 | 2018-05-09 04:00 | 4 | 4 | 32.9983 | 6.9296
2018-05-09 05:00 | 5 | 4 | 0 | 0 | 2018-05-09 05:00 | 5 | 4 | 0 | 0 | 2018-05-09 05:00 | 5 | 4 | 87.0222 | 18.4487 | 2018-05-09 05:00 | 5 | 4 | 33.0684 | 6.9444
2018-05-09 06:00 | 6 | 4 | 0 | 0 | 2018-05-09 06:00 | 6 | 4 | 0 | 0 | 2018-05-09 06:00 | 6 | 4 | 86.9627 | 18.4361 | 2018-05-09 06:00 | 6 | 4 | 33.0458 | 6.9396
2018-05-09 07:00 | 7 | 4 | 0 | 0 | 2018-05-09 07:00 | 7 | 4 | 0 | 0 | 2018-05-09 07:00 | 7 | 4 | 87.1321 | 18.472 | 2018-05-09 07:00 | 7 | 4 | 33.1102 | 6.9531
2018-05-09 08:00 | 8 | 4 | 0 | 0 | 2018-05-09 08:00 | 8 | 4 | 0 | 0 | 2018-05-09 08:00 | 8 | 4 | 87.1931 | 18.4849 | 2018-05-09 08:00 | 8 | 4 | 33.1334 | 6.958
2018-05-09 09:00 | 9 | 4 | 0 | 0 | 2018-05-09 09:00 | 9 | 4 | 0 | 0 | 2018-05-09 09:00 | 9 | 4 | 86.7155 | 18.3837 | 2018-05-09 09:00 | 9 | 4 | 32.9519 | 6.9199
2018-05-09 10:00 | 10 | 4 | 0 | 0 | 2018-05-09 10:00 | 10 | 4 | 0 | 0 | 2018-05-09 10:00 | 10 | 4 | 86.6743 | 18.375 | 2018-05-09 10:00 | 10 | 4 | 32.9362 | 6.9166
2018-05-09 11:00 | 11 | 4 | 0 | 0 | 2018-05-09 11:00 | 11 | 4 | 0 | 0 | 2018-05-09 11:00 | 11 | 4 | 86.8956 | 18.4219 | 2018-05-09 11:00 | 11 | 4 | 33.0203 | 6.9343
2018-05-09 12:00 | 12 | 4 | 0 | 0 | 2018-05-09 12:00 | 12 | 4 | 0 | 0 | 2018-05-09 12:00 | 12 | 4 | 86.9276 | 18.4287 | 2018-05-09 12:00 | 12 | 4 | 33.0325 | 6.9368
2018-05-09 13:00 | 13 | 4 | 0 | 0 | 2018-05-09 13:00 | 13 | 4 | 0 | 0 | 2018-05-09 13:00 | 13 | 4 | 87.2541 | 18.4979 | 2018-05-09 13:00 | 13 | 4 | 33.1566 | 6.9629
2018-05-09 14:00 | 14 | 4 | 0 | 0 | 2018-05-09 14:00 | 14 | 4 | 0 | 0 | 2018-05-09 14:00 | 14 | 4 | 87.4037 | 18.5296 | 2018-05-09 14:00 | 14 | 4 | 33.2134 | 6.9748
2018-05-09 15:00 | 15 | 4 | 0 | 0 | 2018-05-09 15:00 | 15 | 4 | 0 | 0 | 2018-05-09 15:00 | 15 | 4 | 87.2129 | 18.4891 | 2018-05-09 15:00 | 15 | 4 | 33.1409 | 6.9596
2018-05-09 16:00 | 16 | 4 | 0 | 0 | 2018-05-09 16:00 | 16 | 4 | 0 | 0 | 2018-05-09 16:00 | 16 | 4 | 86.9718 | 18.438 | 2018-05-09 16:00 | 16 | 4 | 33.0493 | 6.9403
2018-05-09 17:00 | 17 | 4 | 0 | 0 | 2018-05-09 17:00 | 17 | 4 | 0 | 0 | 2018-05-09 17:00 | 17 | 4 | 87.1397 | 18.4736 | 2018-05-09 17:00 | 17 | 4 | 33.1131 | 6.9537
2018-05-09 18:00 | 18 | 4 | 0 | 0 | 2018-05-09 18:00 | 18 | 4 | 0 | 0 | 2018-05-09 18:00 | 18 | 4 | 87.2435 | 18.4956 | 2018-05-09 18:00 | 18 | 4 | 33.1525 | 6.962
2018-05-09 19:00 | 19 | 4 | 0 | 0 | 2018-05-09 19:00 | 19 | 4 | 0 | 0 | 2018-05-09 19:00 | 19 | 4 | 86.8894 | 18.4206 | 2018-05-09 19:00 | 19 | 4 | 33.018 | 6.9338
2018-05-09 20:00 | 20 | 4 | 0 | 0 | 2018-05-09 20:00 | 20 | 4 | 0 | 0 | 2018-05-09 20:00 | 20 | 4 | 87.1839 | 18.483 | 2018-05-09 20:00 | 20 | 4 | 33.1299 | 6.9573
2018-05-09 21:00 | 21 | 4 | 0 | 0 | 2018-05-09 21:00 | 21 | 4 | 0 | 0 | 2018-05-09 21:00 | 21 | 4 | 87.2419 | 18.4953 | 2018-05-09 21:00 | 21 | 4 | 33.1519 | 6.9619
2018-05-09 22:00 | 22 | 4 | 0 | 0 | 2018-05-09 22:00 | 22 | 4 | 0 | 0 | 2018-05-09 22:00 | 22 | 4 | 87.1733 | 18.4807 | 2018-05-09 22:00 | 22 | 4 | 33.1259 | 6.9564
2018-05-09 23:00 | 23 | 4 | 0 | 0 | 2018-05-09 23:00 | 23 | 4 | 0 | 0 | 2018-05-09 23:00 | 23 | 4 | 87.2557 | 18.4982 | 2018-05-09 23:00 | 23 | 4 | 33.1572 | 6.963
2018-05-10 | 0 | 5 | 86.5492 | 18.2619 | 2018-05-10 | 0 | 5 | 0 | 0 | 2018-05-10 | 0 | 5 | 0 | 0 | 2018-05-10 | 0 | 5 | 0 | 0
2018-05-10 01:00 | 1 | 5 | 86.7201 | 18.2979 | 2018-05-10 01:00 | 1 | 5 | 0 | 0 | 2018-05-10 01:00 | 1 | 5 | 0 | 0 | 2018-05-10 01:00 | 1 | 5 | 0 | 0
2018-05-10 02:00 | 2 | 5 | 86.5095 | 18.2535 | 2018-05-10 02:00 | 2 | 5 | 0 | 0 | 2018-05-10 02:00 | 2 | 5 | 0 | 0 | 2018-05-10 02:00 | 2 | 5 | 0 | 0
2018-05-10 03:00 | 3 | 5 | 86.4576 | 18.2426 | 2018-05-10 03:00 | 3 | 5 | 0 | 0 | 2018-05-10 03:00 | 3 | 5 | 0 | 0 | 2018-05-10 03:00 | 3 | 5 | 0 | 0
2018-05-10 04:00 | 4 | 5 | 86.6316 | 18.2793 | 2018-05-10 04:00 | 4 | 5 | 0 | 0 | 2018-05-10 04:00 | 4 | 5 | 0 | 0 | 2018-05-10 04:00 | 4 | 5 | 0 | 0
2018-05-10 05:00 | 5 | 5 | 86.569 | 18.2661 | 2018-05-10 05:00 | 5 | 5 | 0 | 0 | 2018-05-10 05:00 | 5 | 5 | 0 | 0 | 2018-05-10 05:00 | 5 | 5 | 0 | 0
2018-05-10 06:00 | 6 | 5 | 86.6468 | 18.2825 | 2018-05-10 06:00 | 6 | 5 | 0 | 0 | 2018-05-10 06:00 | 6 | 5 | 0 | 0 | 2018-05-10 06:00 | 6 | 5 | 0 | 0
2018-05-10 07:00 | 7 | 5 | 86.6361 | 18.2802 | 2018-05-10 07:00 | 7 | 5 | 0 | 0 | 2018-05-10 07:00 | 7 | 5 | 0 | 0 | 2018-05-10 07:00 | 7 | 5 | 0 | 0
2018-05-10 08:00 | 8 | 5 | 86.6819 | 18.2899 | 2018-05-10 08:00 | 8 | 5 | 0 | 0 | 2018-05-10 08:00 | 8 | 5 | 0 | 0 | 2018-05-10 08:00 | 8 | 5 | 0 | 0
2018-05-10 09:00 | 9 | 5 | 86.7094 | 18.2957 | 2018-05-10 09:00 | 9 | 5 | 0 | 0 | 2018-05-10 09:00 | 9 | 5 | 0 | 0 | 2018-05-10 09:00 | 9 | 5 | 0 | 0
2018-05-10 10:00 | 10 | 5 | 86.7933 | 18.3134 | 2018-05-10 10:00 | 10 | 5 | 0 | 0 | 2018-05-10 10:00 | 10 | 5 | 0 | 0 | 2018-05-10 10:00 | 10 | 5 | 0 | 0
2018-05-10 11:00 | 11 | 5 | 86.8009 | 18.315 | 2018-05-10 11:00 | 11 | 5 | 0 | 0 | 2018-05-10 11:00 | 11 | 5 | 0 | 0 | 2018-05-10 11:00 | 11 | 5 | 0 | 0
2018-05-10 12:00 | 12 | 5 | 86.6728 | 18.288 | 2018-05-10 12:00 | 12 | 5 | 0 | 0 | 2018-05-10 12:00 | 12 | 5 | 0 | 0 | 2018-05-10 12:00 | 12 | 5 | 0 | 0
2018-05-10 13:00 | 13 | 5 | 86.6316 | 18.2793 | 2018-05-10 13:00 | 13 | 5 | 0 | 0 | 2018-05-10 13:00 | 13 | 5 | 0 | 0 | 2018-05-10 13:00 | 13 | 5 | 0 | 0
2018-05-10 14:00 | 14 | 5 | 86.6316 | 18.2793 | 2018-05-10 14:00 | 14 | 5 | 0 | 0 | 2018-05-10 14:00 | 14 | 5 | 0 | 0 | 2018-05-10 14:00 | 14 | 5 | 0 | 0
2018-05-10 15:00 | 15 | 5 | 86.6636 | 18.286 | 2018-05-10 15:00 | 15 | 5 | 0 | 0 | 2018-05-10 15:00 | 15 | 5 | 0 | 0 | 2018-05-10 15:00 | 15 | 5 | 0 | 0
2018-05-10 16:00 | 16 | 5 | 86.5568 | 18.2635 | 2018-05-10 16:00 | 16 | 5 | 0 | 0 | 2018-05-10 16:00 | 16 | 5 | 0 | 0 | 2018-05-10 16:00 | 16 | 5 | 0 | 0
2018-05-10 17:00 | 17 | 5 | 86.6865 | 18.2909 | 2018-05-10 17:00 | 17 | 5 | 0 | 0 | 2018-05-10 17:00 | 17 | 5 | 0 | 0 | 2018-05-10 17:00 | 17 | 5 | 0 | 0
2018-05-10 18:00 | 18 | 5 | 86.7262 | 18.2992 | 2018-05-10 18:00 | 18 | 5 | 0 | 0 | 2018-05-10 18:00 | 18 | 5 | 0 | 0 | 2018-05-10 18:00 | 18 | 5 | 0 | 0
2018-05-10 19:00 | 19 | 5 | 86.5187 | 18.2554 | 2018-05-10 19:00 | 19 | 5 | 0 | 0 | 2018-05-10 19:00 | 19 | 5 | 0 | 0 | 2018-05-10 19:00 | 19 | 5 | 0 | 0
2018-05-10 20:00 | 20 | 5 | 86.5766 | 18.2677 | 2018-05-10 20:00 | 20 | 5 | 0 | 0 | 2018-05-10 20:00 | 20 | 5 | 0 | 0 | 2018-05-10 20:00 | 20 | 5 | 0 | 0
2018-05-10 21:00 | 21 | 5 | 86.6194 | 18.2767 | 2018-05-10 21:00 | 21 | 5 | 0 | 0 | 2018-05-10 21:00 | 21 | 5 | 0 | 0 | 2018-05-10 21:00 | 21 | 5 | 0 | 0
2018-05-10 22:00 | 22 | 5 | 86.6743 | 18.2883 | 2018-05-10 22:00 | 22 | 5 | 0 | 0 | 2018-05-10 22:00 | 22 | 5 | 0 | 0 | 2018-05-10 22:00 | 22 | 5 | 0 | 0
2018-05-10 23:00 | 23 | 5 | 86.5644 | 18.2651 | 2018-05-10 23:00 | 23 | 5 | 0 | 0 | 2018-05-10 23:00 | 23 | 5 | 0 | 0 | 2018-05-10 23:00 | 23 | 5 | 0 | 0
2018-05-11 | 0 | 6 | 86.2226 | 18.193 | 2018-05-11 | 0 | 6 | 86.688 | 17.6583 | 2018-05-11 | 0 | 6 | 0 | 0 | 2018-05-11 | 0 | 6 | 32.9414 | 6.9177
2018-05-11 01:00 | 1 | 6 | 86.1128 | 18.1698 | 2018-05-11 01:00 | 1 | 6 | 86.5232 | 17.6248 | 2018-05-11 01:00 | 1 | 6 | 0 | 0 | 2018-05-11 01:00 | 1 | 6 | 32.8788 | 6.9046
2018-05-11 02:00 | 2 | 6 | 86.2791 | 18.2049 | 2018-05-11 02:00 | 2 | 6 | 86.6896 | 17.6587 | 2018-05-11 02:00 | 2 | 6 | 0 | 0 | 2018-05-11 02:00 | 2 | 6 | 32.942 | 6.9178
2018-05-11 03:00 | 3 | 6 | 86.0014 | 18.1463 | 2018-05-11 03:00 | 3 | 6 | 86.4485 | 17.6096 | 2018-05-11 03:00 | 3 | 6 | 0 | 0 | 2018-05-11 03:00 | 3 | 6 | 32.8504 | 6.8986
2018-05-11 04:00 | 4 | 6 | 86.0533 | 18.1572 | 2018-05-11 04:00 | 4 | 6 | 86.4347 | 17.6067 | 2018-05-11 04:00 | 4 | 6 | 0 | 0 | 2018-05-11 04:00 | 4 | 6 | 32.8452 | 6.8975
2018-05-11 05:00 | 5 | 6 | 86.2257 | 18.1936 | 2018-05-11 05:00 | 5 | 6 | 86.6117 | 17.6428 | 2018-05-11 05:00 | 5 | 6 | 0 | 0 | 2018-05-11 05:00 | 5 | 6 | 32.9124 | 6.9116
2018-05-11 06:00 | 6 | 6 | 86.4332 | 18.2374 | 2018-05-11 06:00 | 6 | 6 | 86.9352 | 17.7087 | 2018-05-11 06:00 | 6 | 6 | 0 | 0 | 2018-05-11 06:00 | 6 | 6 | 33.0354 | 6.9374
2018-05-11 07:00 | 7 | 6 | 86.5873 | 18.2699 | 2018-05-11 07:00 | 7 | 6 | 87.0619 | 17.7345 | 2018-05-11 07:00 | 7 | 6 | 0 | 0 | 2018-05-11 07:00 | 7 | 6 | 33.0835 | 6.9475
2018-05-11 08:00 | 8 | 6 | 86.3691 | 18.2239 | 2018-05-11 08:00 | 8 | 6 | 86.7811 | 17.6773 | 2018-05-11 08:00 | 8 | 6 | 0 | 0 | 2018-05-11 08:00 | 8 | 6 | 32.9768 | 6.9251
2018-05-11 09:00 | 9 | 6 | 86.334 | 18.2165 | 2018-05-11 09:00 | 9 | 6 | 86.7399 | 17.6689 | 2018-05-11 09:00 | 9 | 6 | 0 | 0 | 2018-05-11 09:00 | 9 | 6 | 32.9612 | 6.9218
2018-05-11 10:00 | 10 | 6 | 86.5126 | 18.2542 | 2018-05-11 10:00 | 10 | 6 | 86.862 | 17.6938 | 2018-05-11 10:00 | 10 | 6 | 0 | 0 | 2018-05-11 10:00 | 10 | 6 | 33.0076 | 6.9316
2018-05-11 11:00 | 11 | 6 | 86.5003 | 18.2516 | 2018-05-11 11:00 | 11 | 6 | 86.9306 | 17.7078 | 2018-05-11 11:00 | 11 | 6 | 0 | 0 | 2018-05-11 11:00 | 11 | 6 | 33.0336 | 6.9371
2018-05-11 12:00 | 12 | 6 | 86.7002 | 18.2937 | 2018-05-11 12:00 | 12 | 6 | 87.1412 | 17.7507 | 2018-05-11 12:00 | 12 | 6 | 0 | 0 | 2018-05-11 12:00 | 12 | 6 | 33.1137 | 6.9539
2018-05-11 13:00 | 13 | 6 | 86.363 | 18.2226 | 2018-05-11 13:00 | 13 | 6 | 86.8009 | 17.6813 | 2018-05-11 13:00 | 13 | 6 | 0 | 0 | 2018-05-11 13:00 | 13 | 6 | 32.9843 | 6.9267
2018-05-11 14:00 | 14 | 6 | 86.4408 | 18.239 | 2018-05-11 14:00 | 14 | 6 | 86.8635 | 17.6941 | 2018-05-11 14:00 | 14 | 6 | 0 | 0 | 2018-05-11 14:00 | 14 | 6 | 33.0081 | 6.9317
2018-05-11 15:00 | 15 | 6 | 86.2943 | 18.2081 | 2018-05-11 15:00 | 15 | 6 | 86.6743 | 17.6556 | 2018-05-11 15:00 | 15 | 6 | 0 | 0 | 2018-05-11 15:00 | 15 | 6 | 32.9362 | 6.9166
2018-05-11 16:00 | 16 | 6 | 86.3706 | 18.2242 | 2018-05-11 16:00 | 16 | 6 | 86.7491 | 17.6708 | 2018-05-11 16:00 | 16 | 6 | 0 | 0 | 2018-05-11 16:00 | 16 | 6 | 32.9647 | 6.9226
2018-05-11 17:00 | 17 | 6 | 86.2882 | 18.2068 | 2018-05-11 17:00 | 17 | 6 | 86.7445 | 17.6699 | 2018-05-11 17:00 | 17 | 6 | 0 | 0 | 2018-05-11 17:00 | 17 | 6 | 32.9629 | 6.9222
2018-05-11 18:00 | 18 | 6 | 86.1875 | 18.1856 | 2018-05-11 18:00 | 18 | 6 | 86.6667 | 17.654 | 2018-05-11 18:00 | 18 | 6 | 0 | 0 | 2018-05-11 18:00 | 18 | 6 | 32.9333 | 6.916
2018-05-11 19:00 | 19 | 6 | 86.099 | 18.1669 | 2018-05-11 19:00 | 19 | 6 | 86.5431 | 17.6288 | 2018-05-11 19:00 | 19 | 6 | 0 | 0 | 2018-05-11 19:00 | 19 | 6 | 32.8864 | 6.9061
2018-05-11 20:00 | 20 | 6 | 86.1997 | 18.1881 | 2018-05-11 20:00 | 20 | 6 | 86.5187 | 17.6239 | 2018-05-11 20:00 | 20 | 6 | 0 | 0 | 2018-05-11 20:00 | 20 | 6 | 32.8771 | 6.9042
2018-05-11 21:00 | 21 | 6 | 86.3767 | 18.2255 | 2018-05-11 21:00 | 21 | 6 | 86.7247 | 17.6658 | 2018-05-11 21:00 | 21 | 6 | 0 | 0 | 2018-05-11 21:00 | 21 | 6 | 32.9554 | 6.9206
2018-05-11 22:00 | 22 | 6 | 86.3691 | 18.2239 | 2018-05-11 22:00 | 22 | 6 | 86.7659 | 17.6742 | 2018-05-11 22:00 | 22 | 6 | 0 | 0 | 2018-05-11 22:00 | 22 | 6 | 32.971 | 6.9239
2018-05-11 23:00 | 23 | 6 | 86.4012 | 18.2307 | 2018-05-11 23:00 | 23 | 6 | 86.7918 | 17.6795 | 2018-05-11 23:00 | 23 | 6 | 0 | 0 | 2018-05-11 23:00 | 23 | 6 | 32.9809 | 6.926
2018-05-12 | 0 | 7 | 86.0121 | 18.1486 | 2018-05-12 | 0 | 7 | 0 | 0 | 2018-05-12 | 0 | 7 | 86.5507 | 18.3487 | 2018-05-12 | 0 | 7 | 32.8893 | 6.9067
2018-05-12 01:00 | 1 | 7 | 85.919 | 18.1289 | 2018-05-12 01:00 | 1 | 7 | 0 | 0 | 2018-05-12 01:00 | 1 | 7 | 86.5324 | 18.3449 | 2018-05-12 01:00 | 1 | 7 | 32.8823 | 6.9053
2018-05-12 02:00 | 2 | 7 | 86.0533 | 18.1572 | 2018-05-12 02:00 | 2 | 7 | 0 | 0 | 2018-05-12 02:00 | 2 | 7 | 86.6453 | 18.3688 | 2018-05-12 02:00 | 2 | 7 | 32.9252 | 6.9143
2018-05-12 03:00 | 3 | 7 | 86.1677 | 18.1814 | 2018-05-12 03:00 | 3 | 7 | 0 | 0 | 2018-05-12 03:00 | 3 | 7 | 86.7002 | 18.3804 | 2018-05-12 03:00 | 3 | 7 | 32.9461 | 6.9187
2018-05-12 04:00 | 4 | 7 | 86.3081 | 18.211 | 2018-05-12 04:00 | 4 | 7 | 0 | 0 | 2018-05-12 04:00 | 4 | 7 | 86.8513 | 18.4125 | 2018-05-12 04:00 | 4 | 7 | 33.0035 | 6.9307
2018-05-12 05:00 | 5 | 7 | 86.2562 | 18.2001 | 2018-05-12 05:00 | 5 | 7 | 0 | 0 | 2018-05-12 05:00 | 5 | 7 | 86.8605 | 18.4144 | 2018-05-12 05:00 | 5 | 7 | 33.007 | 6.9315
2018-05-12 06:00 | 6 | 7 | 86.1234 | 18.172 | 2018-05-12 06:00 | 6 | 7 | 0 | 0 | 2018-05-12 06:00 | 6 | 7 | 86.6682 | 18.3737 | 2018-05-12 06:00 | 6 | 7 | 32.9339 | 6.9161
2018-05-12 07:00 | 7 | 7 | 86.1906 | 18.1862 | 2018-05-12 07:00 | 7 | 7 | 0 | 0 | 2018-05-12 07:00 | 7 | 7 | 86.7247 | 18.3856 | 2018-05-12 07:00 | 7 | 7 | 32.9554 | 6.9206
2018-05-12 08:00 | 8 | 7 | 86.36 | 18.222 | 2018-05-12 08:00 | 8 | 7 | 0 | 0 | 2018-05-12 08:00 | 8 | 7 | 86.952 | 18.4338 | 2018-05-12 08:00 | 8 | 7 | 33.0418 | 6.9388
2018-05-12 09:00 | 9 | 7 | 86.4912 | 18.2496 | 2018-05-12 09:00 | 9 | 7 | 0 | 0 | 2018-05-12 09:00 | 9 | 7 | 87.0588 | 18.4565 | 2018-05-12 09:00 | 9 | 7 | 33.0823 | 6.9473
2018-05-12 10:00 | 10 | 7 | 86.1982 | 18.1878 | 2018-05-12 10:00 | 10 | 7 | 0 | 0 | 2018-05-12 10:00 | 10 | 7 | 86.6392 | 18.3675 | 2018-05-12 10:00 | 10 | 7 | 32.9229 | 6.9138
2018-05-12 11:00 | 11 | 7 | 86.1707 | 18.182 | 2018-05-12 11:00 | 11 | 7 | 0 | 0 | 2018-05-12 11:00 | 11 | 7 | 86.8849 | 18.4196 | 2018-05-12 11:00 | 11 | 7 | 33.0163 | 6.9334
2018-05-12 12:00 | 12 | 7 | 86.5019 | 18.2519 | 2018-05-12 12:00 | 12 | 7 | 0 | 0 | 2018-05-12 12:00 | 12 | 7 | 87.1504 | 18.4759 | 2018-05-12 12:00 | 12 | 7 | 33.1172 | 6.9546
2018-05-12 13:00 | 13 | 7 | 86.6148 | 18.2757 | 2018-05-12 13:00 | 13 | 7 | 0 | 0 | 2018-05-12 13:00 | 13 | 7 | 87.3167 | 18.5111 | 2018-05-12 13:00 | 13 | 7 | 33.1803 | 6.9679
2018-05-12 14:00 | 14 | 7 | 86.4439 | 18.2397 | 2018-05-12 14:00 | 14 | 7 | 0 | 0 | 2018-05-12 14:00 | 14 | 7 | 87.0832 | 18.4616 | 2018-05-12 14:00 | 14 | 7 | 33.0916 | 6.9492
2018-05-12 15:00 | 15 | 7 | 86.5522 | 18.2625 | 2018-05-12 15:00 | 15 | 7 | 0 | 0 | 2018-05-12 15:00 | 15 | 7 | 87.2938 | 18.5063 | 2018-05-12 15:00 | 15 | 7 | 33.1716 | 6.966
2018-05-12 16:00 | 16 | 7 | 86.5644 | 18.2651 | 2018-05-12 16:00 | 16 | 7 | 0 | 0 | 2018-05-12 16:00 | 16 | 7 | 87.3579 | 18.5199 | 2018-05-12 16:00 | 16 | 7 | 33.196 | 6.9712
2018-05-12 17:00 | 17 | 7 | 86.7445 | 18.3031 | 2018-05-12 17:00 | 17 | 7 | 0 | 0 | 2018-05-12 17:00 | 17 | 7 | 87.57 | 18.5648 | 2018-05-12 17:00 | 17 | 7 | 33.2766 | 6.9881
2018-05-12 18:00 | 18 | 7 | 86.4668 | 18.2445 | 2018-05-12 18:00 | 18 | 7 | 0 | 0 | 2018-05-12 18:00 | 18 | 7 | 87.3014 | 18.5079 | 2018-05-12 18:00 | 18 | 7 | 33.1745 | 6.9667
2018-05-12 19:00 | 19 | 7 | 86.3661 | 18.2232 | 2018-05-12 19:00 | 19 | 7 | 0 | 0 | 2018-05-12 19:00 | 19 | 7 | 87.0954 | 18.4642 | 2018-05-12 19:00 | 19 | 7 | 33.0963 | 6.9502
2018-05-12 20:00 | 20 | 7 | 86.1173 | 18.1708 | 2018-05-12 20:00 | 20 | 7 | 0 | 0 | 2018-05-12 20:00 | 20 | 7 | 86.891 | 18.4209 | 2018-05-12 20:00 | 20 | 7 | 33.0186 | 6.9339
2018-05-12 21:00 | 21 | 7 | 86.1555 | 18.1788 | 2018-05-12 21:00 | 21 | 7 | 0 | 0 | 2018-05-12 21:00 | 21 | 7 | 86.9245 | 18.428 | 2018-05-12 21:00 | 21 | 7 | 33.0313 | 6.9366
2018-05-12 22:00 | 22 | 7 | 86.2211 | 18.1927 | 2018-05-12 22:00 | 22 | 7 | 0 | 0 | 2018-05-12 22:00 | 22 | 7 | 87.0054 | 18.4451 | 2018-05-12 22:00 | 22 | 7 | 33.0621 | 6.943
2018-05-12 23:00 | 23 | 7 | 86.2226 | 18.193 | 2018-05-12 23:00 | 23 | 7 | 0 | 0 | 2018-05-12 23:00 | 23 | 7 | 87.0787 | 18.4607 | 2018-05-12 23:00 | 23 | 7 | 33.0899 | 6.9489
2018-05-13 | 0 | 1 | 86.2364 | 18.1959 | 2018-05-13 | 0 | 1 | 86.7994 | 17.681 | 2018-05-13 | 0 | 1 | 0 | 0 | 2018-05-13 | 0 | 1 | 32.9838 | 6.9266
2018-05-13 01:00 | 1 | 1 | 86.3188 | 18.2133 | 2018-05-13 01:00 | 1 | 1 | 86.952 | 17.7121 | 2018-05-13 01:00 | 1 | 1 | 0 | 0 | 2018-05-13 01:00 | 1 | 1 | 33.0418 | 6.9388
2018-05-13 02:00 | 2 | 1 | 86.2119 | 18.1907 | 2018-05-13 02:00 | 2 | 1 | 86.8177 | 17.6848 | 2018-05-13 02:00 | 2 | 1 | 0 | 0 | 2018-05-13 02:00 | 2 | 1 | 32.9907 | 6.9281
2018-05-13 03:00 | 3 | 1 | 86.1845 | 18.1849 | 2018-05-13 03:00 | 3 | 1 | 86.7857 | 17.6782 | 2018-05-13 03:00 | 3 | 1 | 0 | 0 | 2018-05-13 03:00 | 3 | 1 | 32.9786 | 6.9255
2018-05-13 04:00 | 4 | 1 | 86.2455 | 18.1978 | 2018-05-13 04:00 | 4 | 1 | 86.833 | 17.6879 | 2018-05-13 04:00 | 4 | 1 | 0 | 0 | 2018-05-13 04:00 | 4 | 1 | 32.9965 | 6.9293
2018-05-13 05:00 | 5 | 1 | 86.2333 | 18.1952 | 2018-05-13 05:00 | 5 | 1 | 86.833 | 17.6879 | 2018-05-13 05:00 | 5 | 1 | 0 | 0 | 2018-05-13 05:00 | 5 | 1 | 32.9965 | 6.9293
2018-05-13 06:00 | 6 | 1 | 86.2776 | 18.2046 | 2018-05-13 06:00 | 6 | 1 | 86.8528 | 17.6919 | 2018-05-13 06:00 | 6 | 1 | 0 | 0 | 2018-05-13 06:00 | 6 | 1 | 33.0041 | 6.9309
2018-05-13 07:00 | 7 | 1 | 86.2867 | 18.2065 | 2018-05-13 07:00 | 7 | 1 | 86.8452 | 17.6904 | 2018-05-13 07:00 | 7 | 1 | 0 | 0 | 2018-05-13 07:00 | 7 | 1 | 33.0012 | 6.9302
2018-05-13 08:00 | 8 | 1 | 86.2989 | 18.2091 | 2018-05-13 08:00 | 8 | 1 | 86.9032 | 17.7022 | 2018-05-13 08:00 | 8 | 1 | 0 | 0 | 2018-05-13 08:00 | 8 | 1 | 33.0232 | 6.9349
2018-05-13 09:00 | 9 | 1 | 86.2867 | 18.2065 | 2018-05-13 09:00 | 9 | 1 | 86.8162 | 17.6845 | 2018-05-13 09:00 | 9 | 1 | 0 | 0 | 2018-05-13 09:00 | 9 | 1 | 32.9902 | 6.9279
2018-05-13 10:00 | 10 | 1 | 86.2882 | 18.2068 | 2018-05-13 10:00 | 10 | 1 | 86.8528 | 17.6919 | 2018-05-13 10:00 | 10 | 1 | 0 | 0 | 2018-05-13 10:00 | 10 | 1 | 33.0041 | 6.9309
2018-05-13 11:00 | 11 | 1 | 86.1845 | 18.1849 | 2018-05-13 11:00 | 11 | 1 | 86.743 | 17.6695 | 2018-05-13 11:00 | 11 | 1 | 0 | 0 | 2018-05-13 11:00 | 11 | 1 | 32.9623 | 6.9221
2018-05-13 12:00 | 12 | 1 | 86.1418 | 18.1759 | 2018-05-13 12:00 | 12 | 1 | 86.714 | 17.6636 | 2018-05-13 12:00 | 12 | 1 | 0 | 0 | 2018-05-13 12:00 | 12 | 1 | 32.9513 | 6.9198
2018-05-13 13:00 | 13 | 1 | 86.1479 | 18.1772 | 2018-05-13 13:00 | 13 | 1 | 86.7659 | 17.6742 | 2018-05-13 13:00 | 13 | 1 | 0 | 0 | 2018-05-13 13:00 | 13 | 1 | 32.971 | 6.9239
2018-05-13 14:00 | 14 | 1 | 86.1112 | 18.1695 | 2018-05-13 14:00 | 14 | 1 | 86.7018 | 17.6612 | 2018-05-13 14:00 | 14 | 1 | 0 | 0 | 2018-05-13 14:00 | 14 | 1 | 32.9467 | 6.9188
2018-05-13 15:00 | 15 | 1 | 86.2455 | 18.1978 | 2018-05-13 15:00 | 15 | 1 | 86.8482 | 17.691 | 2018-05-13 15:00 | 15 | 1 | 0 | 0 | 2018-05-13 15:00 | 15 | 1 | 33.0023 | 6.9305
2018-05-13 16:00 | 16 | 1 | 86.3447 | 18.2187 | 2018-05-13 16:00 | 16 | 1 | 86.9398 | 17.7096 | 2018-05-13 16:00 | 16 | 1 | 0 | 0 | 2018-05-13 16:00 | 16 | 1 | 33.0371 | 6.9378
2018-05-13 17:00 | 17 | 1 | 86.4805 | 18.2474 | 2018-05-13 17:00 | 17 | 1 | 86.9856 | 17.719 | 2018-05-13 17:00 | 17 | 1 | 0 | 0 | 2018-05-13 17:00 | 17 | 1 | 33.0545 | 6.9415
2018-05-13 18:00 | 18 | 1 | 86.4332 | 18.2374 | 2018-05-13 18:00 | 18 | 1 | 86.92 | 17.7056 | 2018-05-13 18:00 | 18 | 1 | 0 | 0 | 2018-05-13 18:00 | 18 | 1 | 33.0296 | 6.9362
2018-05-13 19:00 | 19 | 1 | 85.6794 | 18.0784 | 2018-05-13 19:00 | 19 | 1 | 85.9266 | 17.5032 | 2018-05-13 19:00 | 19 | 1 | 0 | 0 | 2018-05-13 19:00 | 19 | 1 | 32.6521 | 6.8569
2018-05-13 20:00 | 20 | 1 | 86.3294 | 18.2155 | 2018-05-13 20:00 | 20 | 1 | 86.5888 | 17.6381 | 2018-05-13 20:00 | 20 | 1 | 0 | 0 | 2018-05-13 20:00 | 20 | 1 | 32.9037 | 6.9098
2018-05-13 21:00 | 21 | 1 | 86.3569 | 18.2213 | 2018-05-13 21:00 | 21 | 1 | 86.6728 | 17.6552 | 2018-05-13 21:00 | 21 | 1 | 0 | 0 | 2018-05-13 21:00 | 21 | 1 | 32.9357 | 6.9165
2018-05-13 22:00 | 22 | 1 | 86.4881 | 18.249 | 2018-05-13 22:00 | 22 | 1 | 86.8086 | 17.6829 | 2018-05-13 22:00 | 22 | 1 | 0 | 0 | 2018-05-13 22:00 | 22 | 1 | 32.9873 | 6.9273
2018-05-13 23:00 | 23 | 1 | 86.4332 | 18.2374 | 2018-05-13 23:00 | 23 | 1 | 86.7353 | 17.668 | 2018-05-13 23:00 | 23 | 1 | 0 | 0 | 2018-05-13 23:00 | 23 | 1 | 32.9594 | 6.9215
2018-05-14 | 0 | 2 | 86.4088 | 18.2323 | 2018-05-14 | 0 | 2 | 86.7002 | 17.6608 | 2018-05-14 | 0 | 2 | 86.9352 | 18.4303 | 2018-05-14 | 0 | 2 | 65.9815 | 13.8561
2018-05-14 01:00 | 1 | 2 | 86.0426 | 18.155 | 2018-05-14 01:00 | 1 | 2 | 86.3127 | 17.5819 | 2018-05-14 01:00 | 1 | 2 | 86.5278 | 18.3439 | 2018-05-14 01:00 | 1 | 2 | 65.6794 | 13.7927
2018-05-14 02:00 | 2 | 2 | 86.392 | 18.2287 | 2018-05-14 02:00 | 2 | 2 | 86.6392 | 17.6484 | 2018-05-14 02:00 | 2 | 2 | 86.8421 | 18.4105 | 2018-05-14 02:00 | 2 | 2 | 65.9229 | 13.8438
2018-05-14 03:00 | 3 | 2 | 86.2776 | 18.2046 | 2018-05-14 03:00 | 3 | 2 | 86.5766 | 17.6357 | 2018-05-14 03:00 | 3 | 2 | 86.7536 | 18.3918 | 2018-05-14 03:00 | 3 | 2 | 65.8655 | 13.8317
2018-05-14 04:00 | 4 | 2 | 86.5034 | 18.2522 | 2018-05-14 04:00 | 4 | 2 | 86.8849 | 17.6985 | 2018-05-14 04:00 | 4 | 2 | 87.0283 | 18.45 | 2018-05-14 04:00 | 4 | 2 | 66.087 | 13.8783
2018-05-14 05:00 | 5 | 2 | 86.3661 | 18.2232 | 2018-05-14 05:00 | 5 | 2 | 86.772 | 17.6755 | 2018-05-14 05:00 | 5 | 2 | 87.0054 | 18.4451 | 2018-05-14 05:00 | 5 | 2 | 66.0354 | 13.8674
2018-05-14 06:00 | 6 | 2 | 86.2898 | 18.2071 | 2018-05-14 06:00 | 6 | 2 | 86.6499 | 17.6506 | 2018-05-14 06:00 | 6 | 2 | 86.8147 | 18.4047 | 2018-05-14 06:00 | 6 | 2 | 65.9165 | 13.8425
2018-05-14 07:00 | 7 | 2 | 86.2043 | 18.1891 | 2018-05-14 07:00 | 7 | 2 | 86.5278 | 17.6257 | 2018-05-14 07:00 | 7 | 2 | 86.7079 | 18.3821 | 2018-05-14 07:00 | 7 | 2 | 65.8296 | 13.8242
2018-05-14 08:00 | 8 | 2 | 86.3355 | 18.2168 | 2018-05-14 08:00 | 8 | 2 | 86.5461 | 17.6294 | 2018-05-14 08:00 | 8 | 2 | 86.8025 | 18.4021 | 2018-05-14 08:00 | 8 | 2 | 65.8725 | 13.8332
2018-05-14 09:00 | 9 | 2 | 86.3798 | 18.2261 | 2018-05-14 09:00 | 9 | 2 | 86.7262 | 17.6661 | 2018-05-14 09:00 | 9 | 2 | 86.8711 | 18.4167 | 2018-05-14 09:00 | 9 | 2 | 65.967 | 13.8531
2018-05-14 10:00 | 10 | 2 | 86.2272 | 18.1939 | 2018-05-14 10:00 | 10 | 2 | 86.5156 | 17.6232 | 2018-05-14 10:00 | 10 | 2 | 86.714 | 18.3834 | 2018-05-14 10:00 | 10 | 2 | 65.8272 | 13.8237
2018-05-14 11:00 | 11 | 2 | 86.2119 | 18.1907 | 2018-05-14 11:00 | 11 | 2 | 86.5141 | 17.6229 | 2018-05-14 11:00 | 11 | 2 | 86.7201 | 18.3847 | 2018-05-14 11:00 | 11 | 2 | 65.829 | 13.8241
2018-05-14 12:00 | 12 | 2 | 86.389 | 18.2281 | 2018-05-14 12:00 | 12 | 2 | 86.6835 | 17.6574 | 2018-05-14 12:00 | 12 | 2 | 86.8574 | 18.4138 | 2018-05-14 12:00 | 12 | 2 | 65.9455 | 13.8486
2018-05-14 13:00 | 13 | 2 | 86.4027 | 18.231 | 2018-05-14 13:00 | 13 | 2 | 86.6224 | 17.645 | 2018-05-14 13:00 | 13 | 2 | 86.7475 | 18.3905 | 2018-05-14 13:00 | 13 | 2 | 65.8806 | 13.8349
2018-05-14 14:00 | 14 | 2 | 86.3783 | 18.2258 | 2018-05-14 14:00 | 14 | 2 | 86.6606 | 17.6528 | 2018-05-14 14:00 | 14 | 2 | 86.7903 | 18.3995 | 2018-05-14 14:00 | 14 | 2 | 65.9113 | 13.8414
2018-05-14 15:00 | 15 | 2 | 86.3355 | 18.2168 | 2018-05-14 15:00 | 15 | 2 | 86.5248 | 17.6251 | 2018-05-14 15:00 | 15 | 2 | 86.7384 | 18.3885 | 2018-05-14 15:00 | 15 | 2 | 65.84 | 13.8264
2018-05-14 16:00 | 16 | 2 | 86.3493 | 18.2197 | 2018-05-14 16:00 | 16 | 2 | 86.4912 | 17.6183 | 2018-05-14 16:00 | 16 | 2 | 86.685 | 18.3772 | 2018-05-14 16:00 | 16 | 2 | 65.807 | 13.8195
2018-05-14 17:00 | 17 | 2 | 86.244 | 18.1975 | 2018-05-14 17:00 | 17 | 2 | 86.4683 | 17.6136 | 2018-05-14 17:00 | 17 | 2 | 86.6743 | 18.375 | 2018-05-14 17:00 | 17 | 2 | 65.7942 | 13.8168
2018-05-14 18:00 | 18 | 2 | 86.3142 | 18.2123 | 2018-05-14 18:00 | 18 | 2 | 86.4378 | 17.6074 | 2018-05-14 18:00 | 18 | 2 | 86.5934 | 18.3578 | 2018-05-14 18:00 | 18 | 2 | 65.7519 | 13.8079
2018-05-14 19:00 | 19 | 2 | 86.2089 | 18.1901 | 2018-05-14 19:00 | 19 | 2 | 86.3508 | 17.5897 | 2018-05-14 19:00 | 19 | 2 | 86.5583 | 18.3504 | 2018-05-14 19:00 | 19 | 2 | 65.7055 | 13.7981
2018-05-14 20:00 | 20 | 2 | 86.2181 | 18.192 | 2018-05-14 20:00 | 20 | 2 | 86.4836 | 17.6167 | 2018-05-14 20:00 | 20 | 2 | 86.6896 | 18.3782 | 2018-05-14 20:00 | 20 | 2 | 65.8058 | 13.8192
2018-05-14 21:00 | 21 | 2 | 86.1494 | 18.1775 | 2018-05-14 21:00 | 21 | 2 | 86.4759 | 17.6151 | 2018-05-14 21:00 | 21 | 2 | 86.63 | 18.3656 | 2018-05-14 21:00 | 21 | 2 | 65.7802 | 13.8139
2018-05-14 22:00 | 22 | 2 | 86.2593 | 18.2007 | 2018-05-14 22:00 | 22 | 2 | 86.5522 | 17.6307 | 2018-05-14 22:00 | 22 | 2 | 86.6468 | 18.3691 | 2018-05-14 22:00 | 22 | 2 | 65.8156 | 13.8213
2018-05-14 23:00 | 23 | 2 | 86.4424 | 18.2393 | 2018-05-14 23:00 | 23 | 2 | 86.8055 | 17.6823 | 2018-05-14 23:00 | 23 | 2 | 86.8864 | 18.4199 | 2018-05-14 23:00 | 23 | 2 | 66.0029 | 13.8606
2018-05-15 | 0 | 3 | 86.4637 | 18.2438 | 2018-05-15 | 0 | 3 | 0 | 0 | 2018-05-15 | 0 | 3 | 0 | 0 | 2018-05-15 | 0 | 3 | 0 | 0
2018-05-15 01:00 | 1 | 3 | 86.5629 | 18.2648 | 2018-05-15 01:00 | 1 | 3 | 0 | 0 | 2018-05-15 01:00 | 1 | 3 | 0 | 0 | 2018-05-15 01:00 | 1 | 3 | 0 | 0
2018-05-15 02:00 | 2 | 3 | 86.3706 | 18.2242 | 2018-05-15 02:00 | 2 | 3 | 0 | 0 | 2018-05-15 02:00 | 2 | 3 | 0 | 0 | 2018-05-15 02:00 | 2 | 3 | 0 | 0
2018-05-15 03:00 | 3 | 3 | 86.3523 | 18.2203 | 2018-05-15 03:00 | 3 | 3 | 0 | 0 | 2018-05-15 03:00 | 3 | 3 | 0 | 0 | 2018-05-15 03:00 | 3 | 3 | 0 | 0
2018-05-15 04:00 | 4 | 3 | 86.3676 | 18.2236 | 2018-05-15 04:00 | 4 | 3 | 0 | 0 | 2018-05-15 04:00 | 4 | 3 | 0 | 0 | 2018-05-15 04:00 | 4 | 3 | 0 | 0
2018-05-15 05:00 | 5 | 3 | 86.4027 | 18.231 | 2018-05-15 05:00 | 5 | 3 | 0 | 0 | 2018-05-15 05:00 | 5 | 3 | 0 | 0 | 2018-05-15 05:00 | 5 | 3 | 0 | 0
2018-05-15 06:00 | 6 | 3 | 86.4652 | 18.2442 | 2018-05-15 06:00 | 6 | 3 | 0 | 0 | 2018-05-15 06:00 | 6 | 3 | 0 | 0 | 2018-05-15 06:00 | 6 | 3 | 0 | 0
2018-05-15 07:00 | 7 | 3 | 86.4012 | 18.2307 | 2018-05-15 07:00 | 7 | 3 | 0 | 0 | 2018-05-15 07:00 | 7 | 3 | 0 | 0 | 2018-05-15 07:00 | 7 | 3 | 0 | 0
2018-05-15 08:00 | 8 | 3 | 86.4515 | 18.2413 | 2018-05-15 08:00 | 8 | 3 | 0 | 0 | 2018-05-15 08:00 | 8 | 3 | 0 | 0 | 2018-05-15 08:00 | 8 | 3 | 0 | 0
2018-05-15 09:00 | 9 | 3 | 86.2028 | 18.1888 | 2018-05-15 09:00 | 9 | 3 | 0 | 0 | 2018-05-15 09:00 | 9 | 3 | 0 | 0 | 2018-05-15 09:00 | 9 | 3 | 0 | 0
2018-05-15 10:00 | 10 | 3 | 86.2715 | 18.2033 | 2018-05-15 10:00 | 10 | 3 | 0 | 0 | 2018-05-15 10:00 | 10 | 3 | 0 | 0 | 2018-05-15 10:00 | 10 | 3 | 0 | 0
2018-05-15 11:00 | 11 | 3 | 86.7567 | 18.3057 | 2018-05-15 11:00 | 11 | 3 | 0 | 0 | 2018-05-15 11:00 | 11 | 3 | 0 | 0 | 2018-05-15 11:00 | 11 | 3 | 0 | 0
2018-05-15 12:00 | 12 | 3 | 86.6194 | 18.2767 | 2018-05-15 12:00 | 12 | 3 | 0 | 0 | 2018-05-15 12:00 | 12 | 3 | 0 | 0 | 2018-05-15 12:00 | 12 | 3 | 0 | 0
2018-05-15 13:00 | 13 | 3 | 86.6377 | 18.2806 | 2018-05-15 13:00 | 13 | 3 | 0 | 0 | 2018-05-15 13:00 | 13 | 3 | 0 | 0 | 2018-05-15 13:00 | 13 | 3 | 0 | 0
2018-05-15 14:00 | 14 | 3 | 86.8757 | 18.3308 | 2018-05-15 14:00 | 14 | 3 | 0 | 0 | 2018-05-15 14:00 | 14 | 3 | 0 | 0 | 2018-05-15 14:00 | 14 | 3 | 0 | 0
2018-05-15 15:00 | 15 | 3 | 86.7994 | 18.3147 | 2018-05-15 15:00 | 15 | 3 | 0 | 0 | 2018-05-15 15:00 | 15 | 3 | 0 | 0 | 2018-05-15 15:00 | 15 | 3 | 0 | 0
2018-05-15 16:00 | 16 | 3 | 86.7674 | 18.3079 | 2018-05-15 16:00 | 16 | 3 | 0 | 0 | 2018-05-15 16:00 | 16 | 3 | 0 | 0 | 2018-05-15 16:00 | 16 | 3 | 0 | 0
2018-05-15 17:00 | 17 | 3 | 86.7384 | 18.3018 | 2018-05-15 17:00 | 17 | 3 | 0 | 0 | 2018-05-15 17:00 | 17 | 3 | 0 | 0 | 2018-05-15 17:00 | 17 | 3 | 0 | 0
2018-05-15 18:00 | 18 | 3 | 86.7124 | 18.2963 | 2018-05-15 18:00 | 18 | 3 | 0 | 0 | 2018-05-15 18:00 | 18 | 3 | 0 | 0 | 2018-05-15 18:00 | 18 | 3 | 0 | 0
2018-05-15 19:00 | 19 | 3 | 86.8376 | 18.3227 | 2018-05-15 19:00 | 19 | 3 | 0 | 0 | 2018-05-15 19:00 | 19 | 3 | 0 | 0 | 2018-05-15 19:00 | 19 | 3 | 0 | 0
2018-05-15 20:00 | 20 | 3 | 86.627 | 18.2783 | 2018-05-15 20:00 | 20 | 3 | 0 | 0 | 2018-05-15 20:00 | 20 | 3 | 0 | 0 | 2018-05-15 20:00 | 20 | 3 | 0 | 0
2018-05-15 21:00 | 21 | 3 | 86.6239 | 18.2776 | 2018-05-15 21:00 | 21 | 3 | 0 | 0 | 2018-05-15 21:00 | 21 | 3 | 0 | 0 | 2018-05-15 21:00 | 21 | 3 | 0 | 0
2018-05-15 22:00 | 22 | 3 | 86.714 | 18.2967 | 2018-05-15 22:00 | 22 | 3 | 0 | 0 | 2018-05-15 22:00 | 22 | 3 | 0 | 0 | 2018-05-15 22:00 | 22 | 3 | 0 | 0
2018-05-15 23:00 | 23 | 3 | 86.8971 | 18.3353 | 2018-05-15 23:00 | 23 | 3 | 0 | 0 | 2018-05-15 23:00 | 23 | 3 | 0 | 0 | 2018-05-15 23:00 | 23 | 3 | 0 | 0
2018-05-16 | 0 | 4 | 0 | 0 | 2018-05-16 | 0 | 4 | 0 | 0 | 2018-05-16 | 0 | 4 | 86.6712 | 18.3743 | 2018-05-16 | 0 | 4 | 32.9351 | 6.9164
2018-05-16 01:00 | 1 | 4 | 0 | 0 | 2018-05-16 01:00 | 1 | 4 | 0 | 0 | 2018-05-16 01:00 | 1 | 4 | 86.511 | 18.3403 | 2018-05-16 01:00 | 1 | 4 | 32.8742 | 6.9036
2018-05-16 02:00 | 2 | 4 | 0 | 0 | 2018-05-16 02:00 | 2 | 4 | 0 | 0 | 2018-05-16 02:00 | 2 | 4 | 86.7628 | 18.3937 | 2018-05-16 02:00 | 2 | 4 | 32.9699 | 6.9237
2018-05-16 03:00 | 3 | 4 | 0 | 0 | 2018-05-16 03:00 | 3 | 4 | 0 | 0 | 2018-05-16 03:00 | 3 | 4 | 86.7384 | 18.3885 | 2018-05-16 03:00 | 3 | 4 | 32.9606 | 6.9217
2018-05-16 04:00 | 4 | 4 | 0 | 0 | 2018-05-16 04:00 | 4 | 4 | 0 | 0 | 2018-05-16 04:00 | 4 | 4 | 86.8376 | 18.4096 | 2018-05-16 04:00 | 4 | 4 | 32.9983 | 6.9296
2018-05-16 05:00 | 5 | 4 | 0 | 0 | 2018-05-16 05:00 | 5 | 4 | 0 | 0 | 2018-05-16 05:00 | 5 | 4 | 87.0222 | 18.4487 | 2018-05-16 05:00 | 5 | 4 | 33.0684 | 6.9444
2018-05-16 06:00 | 6 | 4 | 0 | 0 | 2018-05-16 06:00 | 6 | 4 | 0 | 0 | 2018-05-16 06:00 | 6 | 4 | 86.9627 | 18.4361 | 2018-05-16 06:00 | 6 | 4 | 33.0458 | 6.9396
2018-05-16 07:00 | 7 | 4 | 0 | 0 | 2018-05-16 07:00 | 7 | 4 | 0 | 0 | 2018-05-16 07:00 | 7 | 4 | 87.1321 | 18.472 | 2018-05-16 07:00 | 7 | 4 | 33.1102 | 6.9531
2018-05-16 08:00 | 8 | 4 | 0 | 0 | 2018-05-16 08:00 | 8 | 4 | 0 | 0 | 2018-05-16 08:00 | 8 | 4 | 87.1931 | 18.4849 | 2018-05-16 08:00 | 8 | 4 | 33.1334 | 6.958
2018-05-16 09:00 | 9 | 4 | 0 | 0 | 2018-05-16 09:00 | 9 | 4 | 0 | 0 | 2018-05-16 09:00 | 9 | 4 | 86.7155 | 18.3837 | 2018-05-16 09:00 | 9 | 4 | 32.9519 | 6.9199
2018-05-16 10:00 | 10 | 4 | 0 | 0 | 2018-05-16 10:00 | 10 | 4 | 0 | 0 | 2018-05-16 10:00 | 10 | 4 | 86.6743 | 18.375 | 2018-05-16 10:00 | 10 | 4 | 32.9362 | 6.9166
2018-05-16 11:00 | 11 | 4 | 0 | 0 | 2018-05-16 11:00 | 11 | 4 | 0 | 0 | 2018-05-16 11:00 | 11 | 4 | 86.8956 | 18.4219 | 2018-05-16 11:00 | 11 | 4 | 33.0203 | 6.9343
2018-05-16 12:00 | 12 | 4 | 0 | 0 | 2018-05-16 12:00 | 12 | 4 | 0 | 0 | 2018-05-16 12:00 | 12 | 4 | 86.9276 | 18.4287 | 2018-05-16 12:00 | 12 | 4 | 33.0325 | 6.9368
2018-05-16 13:00 | 13 | 4 | 0 | 0 | 2018-05-16 13:00 | 13 | 4 | 0 | 0 | 2018-05-16 13:00 | 13 | 4 | 87.2541 | 18.4979 | 2018-05-16 13:00 | 13 | 4 | 33.1566 | 6.9629
2018-05-16 14:00 | 14 | 4 | 0 | 0 | 2018-05-16 14:00 | 14 | 4 | 0 | 0 | 2018-05-16 14:00 | 14 | 4 | 87.4037 | 18.5296 | 2018-05-16 14:00 | 14 | 4 | 33.2134 | 6.9748
2018-05-16 15:00 | 15 | 4 | 0 | 0 | 2018-05-16 15:00 | 15 | 4 | 0 | 0 | 2018-05-16 15:00 | 15 | 4 | 87.2129 | 18.4891 | 2018-05-16 15:00 | 15 | 4 | 33.1409 | 6.9596
2018-05-16 16:00 | 16 | 4 | 0 | 0 | 2018-05-16 16:00 | 16 | 4 | 0 | 0 | 2018-05-16 16:00 | 16 | 4 | 86.9718 | 18.438 | 2018-05-16 16:00 | 16 | 4 | 33.0493 | 6.9403
2018-05-16 17:00 | 17 | 4 | 0 | 0 | 2018-05-16 17:00 | 17 | 4 | 0 | 0 | 2018-05-16 17:00 | 17 | 4 | 87.1397 | 18.4736 | 2018-05-16 17:00 | 17 | 4 | 33.1131 | 6.9537
2018-05-16 18:00 | 18 | 4 | 0 | 0 | 2018-05-16 18:00 | 18 | 4 | 0 | 0 | 2018-05-16 18:00 | 18 | 4 | 87.2435 | 18.4956 | 2018-05-16 18:00 | 18 | 4 | 33.1525 | 6.962
2018-05-16 19:00 | 19 | 4 | 0 | 0 | 2018-05-16 19:00 | 19 | 4 | 0 | 0 | 2018-05-16 19:00 | 19 | 4 | 86.8894 | 18.4206 | 2018-05-16 19:00 | 19 | 4 | 33.018 | 6.9338
2018-05-16 20:00 | 20 | 4 | 0 | 0 | 2018-05-16 20:00 | 20 | 4 | 0 | 0 | 2018-05-16 20:00 | 20 | 4 | 87.1839 | 18.483 | 2018-05-16 20:00 | 20 | 4 | 33.1299 | 6.9573
2018-05-16 21:00 | 21 | 4 | 0 | 0 | 2018-05-16 21:00 | 21 | 4 | 0 | 0 | 2018-05-16 21:00 | 21 | 4 | 87.2419 | 18.4953 | 2018-05-16 21:00 | 21 | 4 | 33.1519 | 6.9619
2018-05-16 22:00 | 22 | 4 | 0 | 0 | 2018-05-16 22:00 | 22 | 4 | 0 | 0 | 2018-05-16 22:00 | 22 | 4 | 87.1733 | 18.4807 | 2018-05-16 22:00 | 22 | 4 | 33.1259 | 6.9564
2018-05-16 23:00 | 23 | 4 | 0 | 0 | 2018-05-16 23:00 | 23 | 4 | 0 | 0 | 2018-05-16 23:00 | 23 | 4 | 87.2557 | 18.4982 | 2018-05-16 23:00 | 23 | 4 | 33.1572 | 6.963
2018-05-17 | 0 | 5 | 86.5492 | 18.2619 | 2018-05-17 | 0 | 5 | 0 | 0 | 2018-05-17 | 0 | 5 | 0 | 0 | 2018-05-17 | 0 | 5 | 0 | 0
2018-05-17 01:00 | 1 | 5 | 86.7201 | 18.2979 | 2018-05-17 01:00 | 1 | 5 | 0 | 0 | 2018-05-17 01:00 | 1 | 5 | 0 | 0 | 2018-05-17 01:00 | 1 | 5 | 0 | 0
2018-05-17 02:00 | 2 | 5 | 86.5095 | 18.2535 | 2018-05-17 02:00 | 2 | 5 | 0 | 0 | 2018-05-17 02:00 | 2 | 5 | 0 | 0 | 2018-05-17 02:00 | 2 | 5 | 0 | 0
2018-05-17 03:00 | 3 | 5 | 86.4576 | 18.2426 | 2018-05-17 03:00 | 3 | 5 | 0 | 0 | 2018-05-17 03:00 | 3 | 5 | 0 | 0 | 2018-05-17 03:00 | 3 | 5 | 0 | 0
2018-05-17 04:00 | 4 | 5 | 86.6316 | 18.2793 | 2018-05-17 04:00 | 4 | 5 | 0 | 0 | 2018-05-17 04:00 | 4 | 5 | 0 | 0 | 2018-05-17 04:00 | 4 | 5 | 0 | 0
2018-05-17 05:00 | 5 | 5 | 86.569 | 18.2661 | 2018-05-17 05:00 | 5 | 5 | 0 | 0 | 2018-05-17 05:00 | 5 | 5 | 0 | 0 | 2018-05-17 05:00 | 5 | 5 | 0 | 0
2018-05-17 06:00 | 6 | 5 | 86.6468 | 18.2825 | 2018-05-17 06:00 | 6 | 5 | 0 | 0 | 2018-05-17 06:00 | 6 | 5 | 0 | 0 | 2018-05-17 06:00 | 6 | 5 | 0 | 0
2018-05-17 07:00 | 7 | 5 | 86.6361 | 18.2802 | 2018-05-17 07:00 | 7 | 5 | 0 | 0 | 2018-05-17 07:00 | 7 | 5 | 0 | 0 | 2018-05-17 07:00 | 7 | 5 | 0 | 0
2018-05-17 08:00 | 8 | 5 | 86.6819 | 18.2899 | 2018-05-17 08:00 | 8 | 5 | 0 | 0 | 2018-05-17 08:00 | 8 | 5 | 0 | 0 | 2018-05-17 08:00 | 8 | 5 | 0 | 0
2018-05-17 09:00 | 9 | 5 | 86.7094 | 18.2957 | 2018-05-17 09:00 | 9 | 5 | 0 | 0 | 2018-05-17 09:00 | 9 | 5 | 0 | 0 | 2018-05-17 09:00 | 9 | 5 | 0 | 0
2018-05-17 10:00 | 10 | 5 | 86.7933 | 18.3134 | 2018-05-17 10:00 | 10 | 5 | 0 | 0 | 2018-05-17 10:00 | 10 | 5 | 0 | 0 | 2018-05-17 10:00 | 10 | 5 | 0 | 0
2018-05-17 11:00 | 11 | 5 | 86.8009 | 18.315 | 2018-05-17 11:00 | 11 | 5 | 0 | 0 | 2018-05-17 11:00 | 11 | 5 | 0 | 0 | 2018-05-17 11:00 | 11 | 5 | 0 | 0
2018-05-17 12:00 | 12 | 5 | 86.6728 | 18.288 | 2018-05-17 12:00 | 12 | 5 | 0 | 0 | 2018-05-17 12:00 | 12 | 5 | 0 | 0 | 2018-05-17 12:00 | 12 | 5 | 0 | 0
2018-05-17 13:00 | 13 | 5 | 86.6316 | 18.2793 | 2018-05-17 13:00 | 13 | 5 | 0 | 0 | 2018-05-17 13:00 | 13 | 5 | 0 | 0 | 2018-05-17 13:00 | 13 | 5 | 0 | 0
2018-05-17 14:00 | 14 | 5 | 86.6316 | 18.2793 | 2018-05-17 14:00 | 14 | 5 | 0 | 0 | 2018-05-17 14:00 | 14 | 5 | 0 | 0 | 2018-05-17 14:00 | 14 | 5 | 0 | 0
2018-05-17 15:00 | 15 | 5 | 86.6636 | 18.286 | 2018-05-17 15:00 | 15 | 5 | 0 | 0 | 2018-05-17 15:00 | 15 | 5 | 0 | 0 | 2018-05-17 15:00 | 15 | 5 | 0 | 0
2018-05-17 16:00 | 16 | 5 | 86.5568 | 18.2635 | 2018-05-17 16:00 | 16 | 5 | 0 | 0 | 2018-05-17 16:00 | 16 | 5 | 0 | 0 | 2018-05-17 16:00 | 16 | 5 | 0 | 0
2018-05-17 17:00 | 17 | 5 | 86.6865 | 18.2909 | 2018-05-17 17:00 | 17 | 5 | 0 | 0 | 2018-05-17 17:00 | 17 | 5 | 0 | 0 | 2018-05-17 17:00 | 17 | 5 | 0 | 0
2018-05-17 18:00 | 18 | 5 | 86.7262 | 18.2992 | 2018-05-17 18:00 | 18 | 5 | 0 | 0 | 2018-05-17 18:00 | 18 | 5 | 0 | 0 | 2018-05-17 18:00 | 18 | 5 | 0 | 0
2018-05-17 19:00 | 19 | 5 | 86.5187 | 18.2554 | 2018-05-17 19:00 | 19 | 5 | 0 | 0 | 2018-05-17 19:00 | 19 | 5 | 0 | 0 | 2018-05-17 19:00 | 19 | 5 | 0 | 0
2018-05-17 20:00 | 20 | 5 | 86.5766 | 18.2677 | 2018-05-17 20:00 | 20 | 5 | 0 | 0 | 2018-05-17 20:00 | 20 | 5 | 0 | 0 | 2018-05-17 20:00 | 20 | 5 | 0 | 0
2018-05-17 21:00 | 21 | 5 | 86.6194 | 18.2767 | 2018-05-17 21:00 | 21 | 5 | 0 | 0 | 2018-05-17 21:00 | 21 | 5 | 0 | 0 | 2018-05-17 21:00 | 21 | 5 | 0 | 0
2018-05-17 22:00 | 22 | 5 | 86.6743 | 18.2883 | 2018-05-17 22:00 | 22 | 5 | 0 | 0 | 2018-05-17 22:00 | 22 | 5 | 0 | 0 | 2018-05-17 22:00 | 22 | 5 | 0 | 0
2018-05-17 23:00 | 23 | 5 | 86.5644 | 18.2651 | 2018-05-17 23:00 | 23 | 5 | 0 | 0 | 2018-05-17 23:00 | 23 | 5 | 0 | 0 | 2018-05-17 23:00 | 23 | 5 | 0 | 0
2018-05-18 | 0 | 6 | 86.2226 | 18.193 | 2018-05-18 | 0 | 6 | 86.688 | 17.6583 | 2018-05-18 | 0 | 6 | 0 | 0 | 2018-05-18 | 0 | 6 | 32.9414 | 6.9177
2018-05-18 01:00 | 1 | 6 | 86.1128 | 18.1698 | 2018-05-18 01:00 | 1 | 6 | 86.5232 | 17.6248 | 2018-05-18 01:00 | 1 | 6 | 0 | 0 | 2018-05-18 01:00 | 1 | 6 | 32.8788 | 6.9046
2018-05-18 02:00 | 2 | 6 | 86.2791 | 18.2049 | 2018-05-18 02:00 | 2 | 6 | 86.6896 | 17.6587 | 2018-05-18 02:00 | 2 | 6 | 0 | 0 | 2018-05-18 02:00 | 2 | 6 | 32.942 | 6.9178
2018-05-18 03:00 | 3 | 6 | 86.0014 | 18.1463 | 2018-05-18 03:00 | 3 | 6 | 86.4485 | 17.6096 | 2018-05-18 03:00 | 3 | 6 | 0 | 0 | 2018-05-18 03:00 | 3 | 6 | 32.8504 | 6.8986
2018-05-18 04:00 | 4 | 6 | 86.0533 | 18.1572 | 2018-05-18 04:00 | 4 | 6 | 86.4347 | 17.6067 | 2018-05-18 04:00 | 4 | 6 | 0 | 0 | 2018-05-18 04:00 | 4 | 6 | 32.8452 | 6.8975
2018-05-18 05:00 | 5 | 6 | 86.2257 | 18.1936 | 2018-05-18 05:00 | 5 | 6 | 86.6117 | 17.6428 | 2018-05-18 05:00 | 5 | 6 | 0 | 0 | 2018-05-18 05:00 | 5 | 6 | 32.9124 | 6.9116
2018-05-18 06:00 | 6 | 6 | 86.4332 | 18.2374 | 2018-05-18 06:00 | 6 | 6 | 86.9352 | 17.7087 | 2018-05-18 06:00 | 6 | 6 | 0 | 0 | 2018-05-18 06:00 | 6 | 6 | 33.0354 | 6.9374
2018-05-18 07:00 | 7 | 6 | 86.5873 | 18.2699 | 2018-05-18 07:00 | 7 | 6 | 87.0619 | 17.7345 | 2018-05-18 07:00 | 7 | 6 | 0 | 0 | 2018-05-18 07:00 | 7 | 6 | 33.0835 | 6.9475
2018-05-18 08:00 | 8 | 6 | 86.3691 | 18.2239 | 2018-05-18 08:00 | 8 | 6 | 86.7811 | 17.6773 | 2018-05-18 08:00 | 8 | 6 | 0 | 0 | 2018-05-18 08:00 | 8 | 6 | 32.9768 | 6.9251
2018-05-18 09:00 | 9 | 6 | 86.334 | 18.2165 | 2018-05-18 09:00 | 9 | 6 | 86.7399 | 17.6689 | 2018-05-18 09:00 | 9 | 6 | 0 | 0 | 2018-05-18 09:00 | 9 | 6 | 32.9612 | 6.9218
2018-05-18 10:00 | 10 | 6 | 86.5126 | 18.2542 | 2018-05-18 10:00 | 10 | 6 | 86.862 | 17.6938 | 2018-05-18 10:00 | 10 | 6 | 0 | 0 | 2018-05-18 10:00 | 10 | 6 | 33.0076 | 6.9316
2018-05-18 11:00 | 11 | 6 | 86.5003 | 18.2516 | 2018-05-18 11:00 | 11 | 6 | 86.9306 | 17.7078 | 2018-05-18 11:00 | 11 | 6 | 0 | 0 | 2018-05-18 11:00 | 11 | 6 | 33.0336 | 6.9371
2018-05-18 12:00 | 12 | 6 | 86.7002 | 18.2937 | 2018-05-18 12:00 | 12 | 6 | 87.1412 | 17.7507 | 2018-05-18 12:00 | 12 | 6 | 0 | 0 | 2018-05-18 12:00 | 12 | 6 | 33.1137 | 6.9539
2018-05-18 13:00 | 13 | 6 | 86.363 | 18.2226 | 2018-05-18 13:00 | 13 | 6 | 86.8009 | 17.6813 | 2018-05-18 13:00 | 13 | 6 | 0 | 0 | 2018-05-18 13:00 | 13 | 6 | 32.9843 | 6.9267
2018-05-18 14:00 | 14 | 6 | 86.4408 | 18.239 | 2018-05-18 14:00 | 14 | 6 | 86.8635 | 17.6941 | 2018-05-18 14:00 | 14 | 6 | 0 | 0 | 2018-05-18 14:00 | 14 | 6 | 33.0081 | 6.9317
2018-05-18 15:00 | 15 | 6 | 86.2943 | 18.2081 | 2018-05-18 15:00 | 15 | 6 | 86.6743 | 17.6556 | 2018-05-18 15:00 | 15 | 6 | 0 | 0 | 2018-05-18 15:00 | 15 | 6 | 32.9362 | 6.9166
2018-05-18 16:00 | 16 | 6 | 86.3706 | 18.2242 | 2018-05-18 16:00 | 16 | 6 | 86.7491 | 17.6708 | 2018-05-18 16:00 | 16 | 6 | 0 | 0 | 2018-05-18 16:00 | 16 | 6 | 32.9647 | 6.9226
2018-05-18 17:00 | 17 | 6 | 86.2882 | 18.2068 | 2018-05-18 17:00 | 17 | 6 | 86.7445 | 17.6699 | 2018-05-18 17:00 | 17 | 6 | 0 | 0 | 2018-05-18 17:00 | 17 | 6 | 32.9629 | 6.9222
2018-05-18 18:00 | 18 | 6 | 86.1875 | 18.1856 | 2018-05-18 18:00 | 18 | 6 | 86.6667 | 17.654 | 2018-05-18 18:00 | 18 | 6 | 0 | 0 | 2018-05-18 18:00 | 18 | 6 | 32.9333 | 6.916
2018-05-18 19:00 | 19 | 6 | 86.099 | 18.1669 | 2018-05-18 19:00 | 19 | 6 | 86.5431 | 17.6288 | 2018-05-18 19:00 | 19 | 6 | 0 | 0 | 2018-05-18 19:00 | 19 | 6 | 32.8864 | 6.9061
2018-05-18 20:00 | 20 | 6 | 86.1997 | 18.1881 | 2018-05-18 20:00 | 20 | 6 | 86.5187 | 17.6239 | 2018-05-18 20:00 | 20 | 6 | 0 | 0 | 2018-05-18 20:00 | 20 | 6 | 32.8771 | 6.9042
2018-05-18 21:00 | 21 | 6 | 86.3767 | 18.2255 | 2018-05-18 21:00 | 21 | 6 | 86.7247 | 17.6658 | 2018-05-18 21:00 | 21 | 6 | 0 | 0 | 2018-05-18 21:00 | 21 | 6 | 32.9554 | 6.9206
2018-05-18 22:00 | 22 | 6 | 86.3691 | 18.2239 | 2018-05-18 22:00 | 22 | 6 | 86.7659 | 17.6742 | 2018-05-18 22:00 | 22 | 6 | 0 | 0 | 2018-05-18 22:00 | 22 | 6 | 32.971 | 6.9239
2018-05-18 23:00 | 23 | 6 | 86.4012 | 18.2307 | 2018-05-18 23:00 | 23 | 6 | 86.7918 | 17.6795 | 2018-05-18 23:00 | 23 | 6 | 0 | 0 | 2018-05-18 23:00 | 23 | 6 | 32.9809 | 6.926
2018-05-19 | 0 | 7 | 86.0121 | 18.1486 | 2018-05-19 | 0 | 7 | 0 | 0 | 2018-05-19 | 0 | 7 | 86.5507 | 18.3487 | 2018-05-19 | 0 | 7 | 32.8893 | 6.9067
2018-05-19 01:00 | 1 | 7 | 85.919 | 18.1289 | 2018-05-19 01:00 | 1 | 7 | 0 | 0 | 2018-05-19 01:00 | 1 | 7 | 86.5324 | 18.3449 | 2018-05-19 01:00 | 1 | 7 | 32.8823 | 6.9053
2018-05-19 02:00 | 2 | 7 | 86.0533 | 18.1572 | 2018-05-19 02:00 | 2 | 7 | 0 | 0 | 2018-05-19 02:00 | 2 | 7 | 86.6453 | 18.3688 | 2018-05-19 02:00 | 2 | 7 | 32.9252 | 6.9143
2018-05-19 03:00 | 3 | 7 | 86.1677 | 18.1814 | 2018-05-19 03:00 | 3 | 7 | 0 | 0 | 2018-05-19 03:00 | 3 | 7 | 86.7002 | 18.3804 | 2018-05-19 03:00 | 3 | 7 | 32.9461 | 6.9187
2018-05-19 04:00 | 4 | 7 | 86.3081 | 18.211 | 2018-05-19 04:00 | 4 | 7 | 0 | 0 | 2018-05-19 04:00 | 4 | 7 | 86.8513 | 18.4125 | 2018-05-19 04:00 | 4 | 7 | 33.0035 | 6.9307
2018-05-19 05:00 | 5 | 7 | 86.2562 | 18.2001 | 2018-05-19 05:00 | 5 | 7 | 0 | 0 | 2018-05-19 05:00 | 5 | 7 | 86.8605 | 18.4144 | 2018-05-19 05:00 | 5 | 7 | 33.007 | 6.9315
2018-05-19 06:00 | 6 | 7 | 86.1234 | 18.172 | 2018-05-19 06:00 | 6 | 7 | 0 | 0 | 2018-05-19 06:00 | 6 | 7 | 86.6682 | 18.3737 | 2018-05-19 06:00 | 6 | 7 | 32.9339 | 6.9161
2018-05-19 07:00 | 7 | 7 | 86.1906 | 18.1862 | 2018-05-19 07:00 | 7 | 7 | 0 | 0 | 2018-05-19 07:00 | 7 | 7 | 86.7247 | 18.3856 | 2018-05-19 07:00 | 7 | 7 | 32.9554 | 6.9206
2018-05-19 08:00 | 8 | 7 | 86.36 | 18.222 | 2018-05-19 08:00 | 8 | 7 | 0 | 0 | 2018-05-19 08:00 | 8 | 7 | 86.952 | 18.4338 | 2018-05-19 08:00 | 8 | 7 | 33.0418 | 6.9388
2018-05-19 09:00 | 9 | 7 | 86.4912 | 18.2496 | 2018-05-19 09:00 | 9 | 7 | 0 | 0 | 2018-05-19 09:00 | 9 | 7 | 87.0588 | 18.4565 | 2018-05-19 09:00 | 9 | 7 | 33.0823 | 6.9473
2018-05-19 10:00 | 10 | 7 | 86.1982 | 18.1878 | 2018-05-19 10:00 | 10 | 7 | 0 | 0 | 2018-05-19 10:00 | 10 | 7 | 86.6392 | 18.3675 | 2018-05-19 10:00 | 10 | 7 | 32.9229 | 6.9138
2018-05-19 11:00 | 11 | 7 | 86.1707 | 18.182 | 2018-05-19 11:00 | 11 | 7 | 0 | 0 | 2018-05-19 11:00 | 11 | 7 | 86.8849 | 18.4196 | 2018-05-19 11:00 | 11 | 7 | 33.0163 | 6.9334
2018-05-19 12:00 | 12 | 7 | 86.5019 | 18.2519 | 2018-05-19 12:00 | 12 | 7 | 0 | 0 | 2018-05-19 12:00 | 12 | 7 | 87.1504 | 18.4759 | 2018-05-19 12:00 | 12 | 7 | 33.1172 | 6.9546
2018-05-19 13:00 | 13 | 7 | 86.6148 | 18.2757 | 2018-05-19 13:00 | 13 | 7 | 0 | 0 | 2018-05-19 13:00 | 13 | 7 | 87.3167 | 18.5111 | 2018-05-19 13:00 | 13 | 7 | 33.1803 | 6.9679
2018-05-19 14:00 | 14 | 7 | 86.4439 | 18.2397 | 2018-05-19 14:00 | 14 | 7 | 0 | 0 | 2018-05-19 14:00 | 14 | 7 | 87.0832 | 18.4616 | 2018-05-19 14:00 | 14 | 7 | 33.0916 | 6.9492
2018-05-19 15:00 | 15 | 7 | 86.5522 | 18.2625 | 2018-05-19 15:00 | 15 | 7 | 0 | 0 | 2018-05-19 15:00 | 15 | 7 | 87.2938 | 18.5063 | 2018-05-19 15:00 | 15 | 7 | 33.1716 | 6.966
2018-05-19 16:00 | 16 | 7 | 86.5644 | 18.2651 | 2018-05-19 16:00 | 16 | 7 | 0 | 0 | 2018-05-19 16:00 | 16 | 7 | 87.3579 | 18.5199 | 2018-05-19 16:00 | 16 | 7 | 33.196 | 6.9712
2018-05-19 17:00 | 17 | 7 | 86.7445 | 18.3031 | 2018-05-19 17:00 | 17 | 7 | 0 | 0 | 2018-05-19 17:00 | 17 | 7 | 87.57 | 18.5648 | 2018-05-19 17:00 | 17 | 7 | 33.2766 | 6.9881
2018-05-19 18:00 | 18 | 7 | 86.4668 | 18.2445 | 2018-05-19 18:00 | 18 | 7 | 0 | 0 | 2018-05-19 18:00 | 18 | 7 | 87.3014 | 18.5079 | 2018-05-19 18:00 | 18 | 7 | 33.1745 | 6.9667
2018-05-19 19:00 | 19 | 7 | 86.3661 | 18.2232 | 2018-05-19 19:00 | 19 | 7 | 0 | 0 | 2018-05-19 19:00 | 19 | 7 | 87.0954 | 18.4642 | 2018-05-19 19:00 | 19 | 7 | 33.0963 | 6.9502
2018-05-19 20:00 | 20 | 7 | 86.1173 | 18.1708 | 2018-05-19 20:00 | 20 | 7 | 0 | 0 | 2018-05-19 20:00 | 20 | 7 | 86.891 | 18.4209 | 2018-05-19 20:00 | 20 | 7 | 33.0186 | 6.9339
2018-05-19 21:00 | 21 | 7 | 86.1555 | 18.1788 | 2018-05-19 21:00 | 21 | 7 | 0 | 0 | 2018-05-19 21:00 | 21 | 7 | 86.9245 | 18.428 | 2018-05-19 21:00 | 21 | 7 | 33.0313 | 6.9366
2018-05-19 22:00 | 22 | 7 | 86.2211 | 18.1927 | 2018-05-19 22:00 | 22 | 7 | 0 | 0 | 2018-05-19 22:00 | 22 | 7 | 87.0054 | 18.4451 | 2018-05-19 22:00 | 22 | 7 | 33.0621 | 6.943
2018-05-19 23:00 | 23 | 7 | 86.2226 | 18.193 | 2018-05-19 23:00 | 23 | 7 | 0 | 0 | 2018-05-19 23:00 | 23 | 7 | 87.0787 | 18.4607 | 2018-05-19 23:00 | 23 | 7 | 33.0899 | 6.9489
2018-05-20 | 0 | 1 | 86.2364 | 18.1959 | 2018-05-20 | 0 | 1 | 86.7994 | 17.681 | 2018-05-20 | 0 | 1 | 0 | 0 | 2018-05-20 | 0 | 1 | 32.9838 | 6.9266
2018-05-20 01:00 | 1 | 1 | 86.3188 | 18.2133 | 2018-05-20 01:00 | 1 | 1 | 86.952 | 17.7121 | 2018-05-20 01:00 | 1 | 1 | 0 | 0 | 2018-05-20 01:00 | 1 | 1 | 33.0418 | 6.9388
2018-05-20 02:00 | 2 | 1 | 86.2119 | 18.1907 | 2018-05-20 02:00 | 2 | 1 | 86.8177 | 17.6848 | 2018-05-20 02:00 | 2 | 1 | 0 | 0 | 2018-05-20 02:00 | 2 | 1 | 32.9907 | 6.9281
2018-05-20 03:00 | 3 | 1 | 86.1845 | 18.1849 | 2018-05-20 03:00 | 3 | 1 | 86.7857 | 17.6782 | 2018-05-20 03:00 | 3 | 1 | 0 | 0 | 2018-05-20 03:00 | 3 | 1 | 32.9786 | 6.9255
2018-05-20 04:00 | 4 | 1 | 86.2455 | 18.1978 | 2018-05-20 04:00 | 4 | 1 | 86.833 | 17.6879 | 2018-05-20 04:00 | 4 | 1 | 0 | 0 | 2018-05-20 04:00 | 4 | 1 | 32.9965 | 6.9293
2018-05-20 05:00 | 5 | 1 | 86.2333 | 18.1952 | 2018-05-20 05:00 | 5 | 1 | 86.833 | 17.6879 | 2018-05-20 05:00 | 5 | 1 | 0 | 0 | 2018-05-20 05:00 | 5 | 1 | 32.9965 | 6.9293
2018-05-20 06:00 | 6 | 1 | 86.2776 | 18.2046 | 2018-05-20 06:00 | 6 | 1 | 86.8528 | 17.6919 | 2018-05-20 06:00 | 6 | 1 | 0 | 0 | 2018-05-20 06:00 | 6 | 1 | 33.0041 | 6.9309
2018-05-20 07:00 | 7 | 1 | 86.2867 | 18.2065 | 2018-05-20 07:00 | 7 | 1 | 86.8452 | 17.6904 | 2018-05-20 07:00 | 7 | 1 | 0 | 0 | 2018-05-20 07:00 | 7 | 1 | 33.0012 | 6.9302
2018-05-20 08:00 | 8 | 1 | 86.2989 | 18.2091 | 2018-05-20 08:00 | 8 | 1 | 86.9032 | 17.7022 | 2018-05-20 08:00 | 8 | 1 | 0 | 0 | 2018-05-20 08:00 | 8 | 1 | 33.0232 | 6.9349
2018-05-20 09:00 | 9 | 1 | 86.2867 | 18.2065 | 2018-05-20 09:00 | 9 | 1 | 86.8162 | 17.6845 | 2018-05-20 09:00 | 9 | 1 | 0 | 0 | 2018-05-20 09:00 | 9 | 1 | 32.9902 | 6.9279
2018-05-20 10:00 | 10 | 1 | 86.2882 | 18.2068 | 2018-05-20 10:00 | 10 | 1 | 86.8528 | 17.6919 | 2018-05-20 10:00 | 10 | 1 | 0 | 0 | 2018-05-20 10:00 | 10 | 1 | 33.0041 | 6.9309
2018-05-20 11:00 | 11 | 1 | 86.1845 | 18.1849 | 2018-05-20 11:00 | 11 | 1 | 86.743 | 17.6695 | 2018-05-20 11:00 | 11 | 1 | 0 | 0 | 2018-05-20 11:00 | 11 | 1 | 32.9623 | 6.9221
2018-05-20 12:00 | 12 | 1 | 86.1418 | 18.1759 | 2018-05-20 12:00 | 12 | 1 | 86.714 | 17.6636 | 2018-05-20 12:00 | 12 | 1 | 0 | 0 | 2018-05-20 12:00 | 12 | 1 | 32.9513 | 6.9198
2018-05-20 13:00 | 13 | 1 | 86.1479 | 18.1772 | 2018-05-20 13:00 | 13 | 1 | 86.7659 | 17.6742 | 2018-05-20 13:00 | 13 | 1 | 0 | 0 | 2018-05-20 13:00 | 13 | 1 | 32.971 | 6.9239
2018-05-20 14:00 | 14 | 1 | 86.1112 | 18.1695 | 2018-05-20 14:00 | 14 | 1 | 86.7018 | 17.6612 | 2018-05-20 14:00 | 14 | 1 | 0 | 0 | 2018-05-20 14:00 | 14 | 1 | 32.9467 | 6.9188
2018-05-20 15:00 | 15 | 1 | 86.2455 | 18.1978 | 2018-05-20 15:00 | 15 | 1 | 86.8482 | 17.691 | 2018-05-20 15:00 | 15 | 1 | 0 | 0 | 2018-05-20 15:00 | 15 | 1 | 33.0023 | 6.9305
2018-05-20 16:00 | 16 | 1 | 86.3447 | 18.2187 | 2018-05-20 16:00 | 16 | 1 | 86.9398 | 17.7096 | 2018-05-20 16:00 | 16 | 1 | 0 | 0 | 2018-05-20 16:00 | 16 | 1 | 33.0371 | 6.9378
2018-05-20 17:00 | 17 | 1 | 86.4805 | 18.2474 | 2018-05-20 17:00 | 17 | 1 | 86.9856 | 17.719 | 2018-05-20 17:00 | 17 | 1 | 0 | 0 | 2018-05-20 17:00 | 17 | 1 | 33.0545 | 6.9415
2018-05-20 18:00 | 18 | 1 | 86.4332 | 18.2374 | 2018-05-20 18:00 | 18 | 1 | 86.92 | 17.7056 | 2018-05-20 18:00 | 18 | 1 | 0 | 0 | 2018-05-20 18:00 | 18 | 1 | 33.0296 | 6.9362
2018-05-20 19:00 | 19 | 1 | 85.6794 | 18.0784 | 2018-05-20 19:00 | 19 | 1 | 85.9266 | 17.5032 | 2018-05-20 19:00 | 19 | 1 | 0 | 0 | 2018-05-20 19:00 | 19 | 1 | 32.6521 | 6.8569
2018-05-20 20:00 | 20 | 1 | 86.3294 | 18.2155 | 2018-05-20 20:00 | 20 | 1 | 86.5888 | 17.6381 | 2018-05-20 20:00 | 20 | 1 | 0 | 0 | 2018-05-20 20:00 | 20 | 1 | 32.9037 | 6.9098
2018-05-20 21:00 | 21 | 1 | 86.3569 | 18.2213 | 2018-05-20 21:00 | 21 | 1 | 86.6728 | 17.6552 | 2018-05-20 21:00 | 21 | 1 | 0 | 0 | 2018-05-20 21:00 | 21 | 1 | 32.9357 | 6.9165
2018-05-20 22:00 | 22 | 1 | 86.4881 | 18.249 | 2018-05-20 22:00 | 22 | 1 | 86.8086 | 17.6829 | 2018-05-20 22:00 | 22 | 1 | 0 | 0 | 2018-05-20 22:00 | 22 | 1 | 32.9873 | 6.9273
2018-05-20 23:00 | 23 | 1 | 86.4332 | 18.2374 | 2018-05-20 23:00 | 23 | 1 | 86.7353 | 17.668 | 2018-05-20 23:00 | 23 | 1 | 0 | 0 | 2018-05-20 23:00 | 23 | 1 | 32.9594 | 6.9215
2018-05-21 | 0 | 2 | 86.4088 | 18.2323 | 2018-05-21 | 0 | 2 | 86.7002 | 17.6608 | 2018-05-21 | 0 | 2 | 86.9352 | 18.4303 | 2018-05-21 | 0 | 2 | 65.9815 | 13.8561
2018-05-21 01:00 | 1 | 2 | 86.0426 | 18.155 | 2018-05-21 01:00 | 1 | 2 | 86.3127 | 17.5819 | 2018-05-21 01:00 | 1 | 2 | 86.5278 | 18.3439 | 2018-05-21 01:00 | 1 | 2 | 65.6794 | 13.7927
2018-05-21 02:00 | 2 | 2 | 86.392 | 18.2287 | 2018-05-21 02:00 | 2 | 2 | 86.6392 | 17.6484 | 2018-05-21 02:00 | 2 | 2 | 86.8421 | 18.4105 | 2018-05-21 02:00 | 2 | 2 | 65.9229 | 13.8438
2018-05-21 03:00 | 3 | 2 | 86.2776 | 18.2046 | 2018-05-21 03:00 | 3 | 2 | 86.5766 | 17.6357 | 2018-05-21 03:00 | 3 | 2 | 86.7536 | 18.3918 | 2018-05-21 03:00 | 3 | 2 | 65.8655 | 13.8317
2018-05-21 04:00 | 4 | 2 | 86.5034 | 18.2522 | 2018-05-21 04:00 | 4 | 2 | 86.8849 | 17.6985 | 2018-05-21 04:00 | 4 | 2 | 87.0283 | 18.45 | 2018-05-21 04:00 | 4 | 2 | 66.087 | 13.8783
2018-05-21 05:00 | 5 | 2 | 86.3661 | 18.2232 | 2018-05-21 05:00 | 5 | 2 | 86.772 | 17.6755 | 2018-05-21 05:00 | 5 | 2 | 87.0054 | 18.4451 | 2018-05-21 05:00 | 5 | 2 | 66.0354 | 13.8674
2018-05-21 06:00 | 6 | 2 | 86.2898 | 18.2071 | 2018-05-21 06:00 | 6 | 2 | 86.6499 | 17.6506 | 2018-05-21 06:00 | 6 | 2 | 86.8147 | 18.4047 | 2018-05-21 06:00 | 6 | 2 | 65.9165 | 13.8425
2018-05-21 07:00 | 7 | 2 | 86.2043 | 18.1891 | 2018-05-21 07:00 | 7 | 2 | 86.5278 | 17.6257 | 2018-05-21 07:00 | 7 | 2 | 86.7079 | 18.3821 | 2018-05-21 07:00 | 7 | 2 | 65.8296 | 13.8242
2018-05-21 08:00 | 8 | 2 | 86.3355 | 18.2168 | 2018-05-21 08:00 | 8 | 2 | 86.5461 | 17.6294 | 2018-05-21 08:00 | 8 | 2 | 86.8025 | 18.4021 | 2018-05-21 08:00 | 8 | 2 | 65.8725 | 13.8332
2018-05-21 09:00 | 9 | 2 | 86.3798 | 18.2261 | 2018-05-21 09:00 | 9 | 2 | 86.7262 | 17.6661 | 2018-05-21 09:00 | 9 | 2 | 86.8711 | 18.4167 | 2018-05-21 09:00 | 9 | 2 | 65.967 | 13.8531
2018-05-21 10:00 | 10 | 2 | 86.2272 | 18.1939 | 2018-05-21 10:00 | 10 | 2 | 86.5156 | 17.6232 | 2018-05-21 10:00 | 10 | 2 | 86.714 | 18.3834 | 2018-05-21 10:00 | 10 | 2 | 65.8272 | 13.8237
2018-05-21 11:00 | 11 | 2 | 86.2119 | 18.1907 | 2018-05-21 11:00 | 11 | 2 | 86.5141 | 17.6229 | 2018-05-21 11:00 | 11 | 2 | 86.7201 | 18.3847 | 2018-05-21 11:00 | 11 | 2 | 65.829 | 13.8241
2018-05-21 12:00 | 12 | 2 | 86.389 | 18.2281 | 2018-05-21 12:00 | 12 | 2 | 86.6835 | 17.6574 | 2018-05-21 12:00 | 12 | 2 | 86.8574 | 18.4138 | 2018-05-21 12:00 | 12 | 2 | 65.9455 | 13.8486
2018-05-21 13:00 | 13 | 2 | 86.4027 | 18.231 | 2018-05-21 13:00 | 13 | 2 | 86.6224 | 17.645 | 2018-05-21 13:00 | 13 | 2 | 86.7475 | 18.3905 | 2018-05-21 13:00 | 13 | 2 | 65.8806 | 13.8349
2018-05-21 14:00 | 14 | 2 | 86.3783 | 18.2258 | 2018-05-21 14:00 | 14 | 2 | 86.6606 | 17.6528 | 2018-05-21 14:00 | 14 | 2 | 86.7903 | 18.3995 | 2018-05-21 14:00 | 14 | 2 | 65.9113 | 13.8414
2018-05-21 15:00 | 15 | 2 | 86.3355 | 18.2168 | 2018-05-21 15:00 | 15 | 2 | 86.5248 | 17.6251 | 2018-05-21 15:00 | 15 | 2 | 86.7384 | 18.3885 | 2018-05-21 15:00 | 15 | 2 | 65.84 | 13.8264
2018-05-21 16:00 | 16 | 2 | 86.3493 | 18.2197 | 2018-05-21 16:00 | 16 | 2 | 86.4912 | 17.6183 | 2018-05-21 16:00 | 16 | 2 | 86.685 | 18.3772 | 2018-05-21 16:00 | 16 | 2 | 65.807 | 13.8195
2018-05-21 17:00 | 17 | 2 | 86.244 | 18.1975 | 2018-05-21 17:00 | 17 | 2 | 86.4683 | 17.6136 | 2018-05-21 17:00 | 17 | 2 | 86.6743 | 18.375 | 2018-05-21 17:00 | 17 | 2 | 65.7942 | 13.8168
2018-05-21 18:00 | 18 | 2 | 86.3142 | 18.2123 | 2018-05-21 18:00 | 18 | 2 | 86.4378 | 17.6074 | 2018-05-21 18:00 | 18 | 2 | 86.5934 | 18.3578 | 2018-05-21 18:00 | 18 | 2 | 65.7519 | 13.8079
2018-05-21 19:00 | 19 | 2 | 86.2089 | 18.1901 | 2018-05-21 19:00 | 19 | 2 | 86.3508 | 17.5897 | 2018-05-21 19:00 | 19 | 2 | 86.5583 | 18.3504 | 2018-05-21 19:00 | 19 | 2 | 65.7055 | 13.7981
2018-05-21 20:00 | 20 | 2 | 86.2181 | 18.192 | 2018-05-21 20:00 | 20 | 2 | 86.4836 | 17.6167 | 2018-05-21 20:00 | 20 | 2 | 86.6896 | 18.3782 | 2018-05-21 20:00 | 20 | 2 | 65.8058 | 13.8192
2018-05-21 21:00 | 21 | 2 | 86.1494 | 18.1775 | 2018-05-21 21:00 | 21 | 2 | 86.4759 | 17.6151 | 2018-05-21 21:00 | 21 | 2 | 86.63 | 18.3656 | 2018-05-21 21:00 | 21 | 2 | 65.7802 | 13.8139
2018-05-21 22:00 | 22 | 2 | 86.2593 | 18.2007 | 2018-05-21 22:00 | 22 | 2 | 86.5522 | 17.6307 | 2018-05-21 22:00 | 22 | 2 | 86.6468 | 18.3691 | 2018-05-21 22:00 | 22 | 2 | 65.8156 | 13.8213
2018-05-21 23:00 | 23 | 2 | 86.4424 | 18.2393 | 2018-05-21 23:00 | 23 | 2 | 86.8055 | 17.6823 | 2018-05-21 23:00 | 23 | 2 | 86.8864 | 18.4199 | 2018-05-21 23:00 | 23 | 2 | 66.0029 | 13.8606
2018-05-22 | 0 | 3 | 86.4637 | 18.2438 | 2018-05-22 | 0 | 3 | 0 | 0 | 2018-05-22 | 0 | 3 | 0 | 0 | 2018-05-22 | 0 | 3 | 0 | 0
2018-05-22 01:00 | 1 | 3 | 86.5629 | 18.2648 | 2018-05-22 01:00 | 1 | 3 | 0 | 0 | 2018-05-22 01:00 | 1 | 3 | 0 | 0 | 2018-05-22 01:00 | 1 | 3 | 0 | 0
2018-05-22 02:00 | 2 | 3 | 86.3706 | 18.2242 | 2018-05-22 02:00 | 2 | 3 | 0 | 0 | 2018-05-22 02:00 | 2 | 3 | 0 | 0 | 2018-05-22 02:00 | 2 | 3 | 0 | 0
2018-05-22 03:00 | 3 | 3 | 86.3523 | 18.2203 | 2018-05-22 03:00 | 3 | 3 | 0 | 0 | 2018-05-22 03:00 | 3 | 3 | 0 | 0 | 2018-05-22 03:00 | 3 | 3 | 0 | 0
2018-05-22 04:00 | 4 | 3 | 86.3676 | 18.2236 | 2018-05-22 04:00 | 4 | 3 | 0 | 0 | 2018-05-22 04:00 | 4 | 3 | 0 | 0 | 2018-05-22 04:00 | 4 | 3 | 0 | 0
2018-05-22 05:00 | 5 | 3 | 86.4027 | 18.231 | 2018-05-22 05:00 | 5 | 3 | 0 | 0 | 2018-05-22 05:00 | 5 | 3 | 0 | 0 | 2018-05-22 05:00 | 5 | 3 | 0 | 0
2018-05-22 06:00 | 6 | 3 | 86.4652 | 18.2442 | 2018-05-22 06:00 | 6 | 3 | 0 | 0 | 2018-05-22 06:00 | 6 | 3 | 0 | 0 | 2018-05-22 06:00 | 6 | 3 | 0 | 0
2018-05-22 07:00 | 7 | 3 | 86.4012 | 18.2307 | 2018-05-22 07:00 | 7 | 3 | 0 | 0 | 2018-05-22 07:00 | 7 | 3 | 0 | 0 | 2018-05-22 07:00 | 7 | 3 | 0 | 0
2018-05-22 08:00 | 8 | 3 | 86.4515 | 18.2413 | 2018-05-22 08:00 | 8 | 3 | 0 | 0 | 2018-05-22 08:00 | 8 | 3 | 0 | 0 | 2018-05-22 08:00 | 8 | 3 | 0 | 0
2018-05-22 09:00 | 9 | 3 | 86.2028 | 18.1888 | 2018-05-22 09:00 | 9 | 3 | 0 | 0 | 2018-05-22 09:00 | 9 | 3 | 0 | 0 | 2018-05-22 09:00 | 9 | 3 | 0 | 0
2018-05-22 10:00 | 10 | 3 | 86.2715 | 18.2033 | 2018-05-22 10:00 | 10 | 3 | 0 | 0 | 2018-05-22 10:00 | 10 | 3 | 0 | 0 | 2018-05-22 10:00 | 10 | 3 | 0 | 0
2018-05-22 11:00 | 11 | 3 | 86.7567 | 18.3057 | 2018-05-22 11:00 | 11 | 3 | 0 | 0 | 2018-05-22 11:00 | 11 | 3 | 0 | 0 | 2018-05-22 11:00 | 11 | 3 | 0 | 0
2018-05-22 12:00 | 12 | 3 | 86.6194 | 18.2767 | 2018-05-22 12:00 | 12 | 3 | 0 | 0 | 2018-05-22 12:00 | 12 | 3 | 0 | 0 | 2018-05-22 12:00 | 12 | 3 | 0 | 0
2018-05-22 13:00 | 13 | 3 | 86.6377 | 18.2806 | 2018-05-22 13:00 | 13 | 3 | 0 | 0 | 2018-05-22 13:00 | 13 | 3 | 0 | 0 | 2018-05-22 13:00 | 13 | 3 | 0 | 0
2018-05-22 14:00 | 14 | 3 | 86.8757 | 18.3308 | 2018-05-22 14:00 | 14 | 3 | 0 | 0 | 2018-05-22 14:00 | 14 | 3 | 0 | 0 | 2018-05-22 14:00 | 14 | 3 | 0 | 0
2018-05-22 15:00 | 15 | 3 | 86.7994 | 18.3147 | 2018-05-22 15:00 | 15 | 3 | 0 | 0 | 2018-05-22 15:00 | 15 | 3 | 0 | 0 | 2018-05-22 15:00 | 15 | 3 | 0 | 0
2018-05-22 16:00 | 16 | 3 | 86.7674 | 18.3079 | 2018-05-22 16:00 | 16 | 3 | 0 | 0 | 2018-05-22 16:00 | 16 | 3 | 0 | 0 | 2018-05-22 16:00 | 16 | 3 | 0 | 0
2018-05-22 17:00 | 17 | 3 | 86.7384 | 18.3018 | 2018-05-22 17:00 | 17 | 3 | 0 | 0 | 2018-05-22 17:00 | 17 | 3 | 0 | 0 | 2018-05-22 17:00 | 17 | 3 | 0 | 0
2018-05-22 18:00 | 18 | 3 | 86.7124 | 18.2963 | 2018-05-22 18:00 | 18 | 3 | 0 | 0 | 2018-05-22 18:00 | 18 | 3 | 0 | 0 | 2018-05-22 18:00 | 18 | 3 | 0 | 0
2018-05-22 19:00 | 19 | 3 | 86.8376 | 18.3227 | 2018-05-22 19:00 | 19 | 3 | 0 | 0 | 2018-05-22 19:00 | 19 | 3 | 0 | 0 | 2018-05-22 19:00 | 19 | 3 | 0 | 0
2018-05-22 20:00 | 20 | 3 | 86.627 | 18.2783 | 2018-05-22 20:00 | 20 | 3 | 0 | 0 | 2018-05-22 20:00 | 20 | 3 | 0 | 0 | 2018-05-22 20:00 | 20 | 3 | 0 | 0
2018-05-22 21:00 | 21 | 3 | 86.6239 | 18.2776 | 2018-05-22 21:00 | 21 | 3 | 0 | 0 | 2018-05-22 21:00 | 21 | 3 | 0 | 0 | 2018-05-22 21:00 | 21 | 3 | 0 | 0
2018-05-22 22:00 | 22 | 3 | 86.714 | 18.2967 | 2018-05-22 22:00 | 22 | 3 | 0 | 0 | 2018-05-22 22:00 | 22 | 3 | 0 | 0 | 2018-05-22 22:00 | 22 | 3 | 0 | 0
2018-05-22 23:00 | 23 | 3 | 86.8971 | 18.3353 | 2018-05-22 23:00 | 23 | 3 | 0 | 0 | 2018-05-22 23:00 | 23 | 3 | 0 | 0 | 2018-05-22 23:00 | 23 | 3 | 0 | 0
2018-05-23 | 0 | 4 | 0 | 0 | 2018-05-23 | 0 | 4 | 0 | 0 | 2018-05-23 | 0 | 4 | 86.6712 | 18.3743 | 2018-05-23 | 0 | 4 | 32.9351 | 6.9164
2018-05-23 01:00 | 1 | 4 | 0 | 0 | 2018-05-23 01:00 | 1 | 4 | 0 | 0 | 2018-05-23 01:00 | 1 | 4 | 86.511 | 18.3403 | 2018-05-23 01:00 | 1 | 4 | 32.8742 | 6.9036
2018-05-23 02:00 | 2 | 4 | 0 | 0 | 2018-05-23 02:00 | 2 | 4 | 0 | 0 | 2018-05-23 02:00 | 2 | 4 | 86.7628 | 18.3937 | 2018-05-23 02:00 | 2 | 4 | 32.9699 | 6.9237
2018-05-23 03:00 | 3 | 4 | 0 | 0 | 2018-05-23 03:00 | 3 | 4 | 0 | 0 | 2018-05-23 03:00 | 3 | 4 | 86.7384 | 18.3885 | 2018-05-23 03:00 | 3 | 4 | 32.9606 | 6.9217
2018-05-23 04:00 | 4 | 4 | 0 | 0 | 2018-05-23 04:00 | 4 | 4 | 0 | 0 | 2018-05-23 04:00 | 4 | 4 | 86.8376 | 18.4096 | 2018-05-23 04:00 | 4 | 4 | 32.9983 | 6.9296
2018-05-23 05:00 | 5 | 4 | 0 | 0 | 2018-05-23 05:00 | 5 | 4 | 0 | 0 | 2018-05-23 05:00 | 5 | 4 | 87.0222 | 18.4487 | 2018-05-23 05:00 | 5 | 4 | 33.0684 | 6.9444
2018-05-23 06:00 | 6 | 4 | 0 | 0 | 2018-05-23 06:00 | 6 | 4 | 0 | 0 | 2018-05-23 06:00 | 6 | 4 | 86.9627 | 18.4361 | 2018-05-23 06:00 | 6 | 4 | 33.0458 | 6.9396
2018-05-23 07:00 | 7 | 4 | 0 | 0 | 2018-05-23 07:00 | 7 | 4 | 0 | 0 | 2018-05-23 07:00 | 7 | 4 | 87.1321 | 18.472 | 2018-05-23 07:00 | 7 | 4 | 33.1102 | 6.9531
2018-05-23 08:00 | 8 | 4 | 0 | 0 | 2018-05-23 08:00 | 8 | 4 | 0 | 0 | 2018-05-23 08:00 | 8 | 4 | 87.1931 | 18.4849 | 2018-05-23 08:00 | 8 | 4 | 33.1334 | 6.958
2018-05-23 09:00 | 9 | 4 | 0 | 0 | 2018-05-23 09:00 | 9 | 4 | 0 | 0 | 2018-05-23 09:00 | 9 | 4 | 86.7155 | 18.3837 | 2018-05-23 09:00 | 9 | 4 | 32.9519 | 6.9199
2018-05-23 10:00 | 10 | 4 | 0 | 0 | 2018-05-23 10:00 | 10 | 4 | 0 | 0 | 2018-05-23 10:00 | 10 | 4 | 86.6743 | 18.375 | 2018-05-23 10:00 | 10 | 4 | 32.9362 | 6.9166
2018-05-23 11:00 | 11 | 4 | 0 | 0 | 2018-05-23 11:00 | 11 | 4 | 0 | 0 | 2018-05-23 11:00 | 11 | 4 | 86.8956 | 18.4219 | 2018-05-23 11:00 | 11 | 4 | 33.0203 | 6.9343
2018-05-23 12:00 | 12 | 4 | 0 | 0 | 2018-05-23 12:00 | 12 | 4 | 0 | 0 | 2018-05-23 12:00 | 12 | 4 | 86.9276 | 18.4287 | 2018-05-23 12:00 | 12 | 4 | 33.0325 | 6.9368
2018-05-23 13:00 | 13 | 4 | 0 | 0 | 2018-05-23 13:00 | 13 | 4 | 0 | 0 | 2018-05-23 13:00 | 13 | 4 | 87.2541 | 18.4979 | 2018-05-23 13:00 | 13 | 4 | 33.1566 | 6.9629
2018-05-23 14:00 | 14 | 4 | 0 | 0 | 2018-05-23 14:00 | 14 | 4 | 0 | 0 | 2018-05-23 14:00 | 14 | 4 | 87.4037 | 18.5296 | 2018-05-23 14:00 | 14 | 4 | 33.2134 | 6.9748
2018-05-23 15:00 | 15 | 4 | 0 | 0 | 2018-05-23 15:00 | 15 | 4 | 0 | 0 | 2018-05-23 15:00 | 15 | 4 | 87.2129 | 18.4891 | 2018-05-23 15:00 | 15 | 4 | 33.1409 | 6.9596
2018-05-23 16:00 | 16 | 4 | 0 | 0 | 2018-05-23 16:00 | 16 | 4 | 0 | 0 | 2018-05-23 16:00 | 16 | 4 | 86.9718 | 18.438 | 2018-05-23 16:00 | 16 | 4 | 33.0493 | 6.9403
2018-05-23 17:00 | 17 | 4 | 0 | 0 | 2018-05-23 17:00 | 17 | 4 | 0 | 0 | 2018-05-23 17:00 | 17 | 4 | 87.1397 | 18.4736 | 2018-05-23 17:00 | 17 | 4 | 33.1131 | 6.9537
2018-05-23 18:00 | 18 | 4 | 0 | 0 | 2018-05-23 18:00 | 18 | 4 | 0 | 0 | 2018-05-23 18:00 | 18 | 4 | 87.2435 | 18.4956 | 2018-05-23 18:00 | 18 | 4 | 33.1525 | 6.962
2018-05-23 19:00 | 19 | 4 | 0 | 0 | 2018-05-23 19:00 | 19 | 4 | 0 | 0 | 2018-05-23 19:00 | 19 | 4 | 86.8894 | 18.4206 | 2018-05-23 19:00 | 19 | 4 | 33.018 | 6.9338
2018-05-23 20:00 | 20 | 4 | 0 | 0 | 2018-05-23 20:00 | 20 | 4 | 0 | 0 | 2018-05-23 20:00 | 20 | 4 | 87.1839 | 18.483 | 2018-05-23 20:00 | 20 | 4 | 33.1299 | 6.9573
2018-05-23 21:00 | 21 | 4 | 0 | 0 | 2018-05-23 21:00 | 21 | 4 | 0 | 0 | 2018-05-23 21:00 | 21 | 4 | 87.2419 | 18.4953 | 2018-05-23 21:00 | 21 | 4 | 33.1519 | 6.9619
2018-05-23 22:00 | 22 | 4 | 0 | 0 | 2018-05-23 22:00 | 22 | 4 | 0 | 0 | 2018-05-23 22:00 | 22 | 4 | 87.1733 | 18.4807 | 2018-05-23 22:00 | 22 | 4 | 33.1259 | 6.9564
2018-05-23 23:00 | 23 | 4 | 0 | 0 | 2018-05-23 23:00 | 23 | 4 | 0 | 0 | 2018-05-23 23:00 | 23 | 4 | 87.2557 | 18.4982 | 2018-05-23 23:00 | 23 | 4 | 33.1572 | 6.963
2018-05-24 | 0 | 5 | 86.5492 | 18.2619 | 2018-05-24 | 0 | 5 | 0 | 0 | 2018-05-24 | 0 | 5 | 0 | 0 | 2018-05-24 | 0 | 5 | 0 | 0
2018-05-24 01:00 | 1 | 5 | 86.7201 | 18.2979 | 2018-05-24 01:00 | 1 | 5 | 0 | 0 | 2018-05-24 01:00 | 1 | 5 | 0 | 0 | 2018-05-24 01:00 | 1 | 5 | 0 | 0
2018-05-24 02:00 | 2 | 5 | 86.5095 | 18.2535 | 2018-05-24 02:00 | 2 | 5 | 0 | 0 | 2018-05-24 02:00 | 2 | 5 | 0 | 0 | 2018-05-24 02:00 | 2 | 5 | 0 | 0
2018-05-24 03:00 | 3 | 5 | 86.4576 | 18.2426 | 2018-05-24 03:00 | 3 | 5 | 0 | 0 | 2018-05-24 03:00 | 3 | 5 | 0 | 0 | 2018-05-24 03:00 | 3 | 5 | 0 | 0
2018-05-24 04:00 | 4 | 5 | 86.6316 | 18.2793 | 2018-05-24 04:00 | 4 | 5 | 0 | 0 | 2018-05-24 04:00 | 4 | 5 | 0 | 0 | 2018-05-24 04:00 | 4 | 5 | 0 | 0
2018-05-24 05:00 | 5 | 5 | 86.569 | 18.2661 | 2018-05-24 05:00 | 5 | 5 | 0 | 0 | 2018-05-24 05:00 | 5 | 5 | 0 | 0 | 2018-05-24 05:00 | 5 | 5 | 0 | 0
2018-05-24 06:00 | 6 | 5 | 86.6468 | 18.2825 | 2018-05-24 06:00 | 6 | 5 | 0 | 0 | 2018-05-24 06:00 | 6 | 5 | 0 | 0 | 2018-05-24 06:00 | 6 | 5 | 0 | 0
2018-05-24 07:00 | 7 | 5 | 86.6361 | 18.2802 | 2018-05-24 07:00 | 7 | 5 | 0 | 0 | 2018-05-24 07:00 | 7 | 5 | 0 | 0 | 2018-05-24 07:00 | 7 | 5 | 0 | 0
2018-05-24 08:00 | 8 | 5 | 86.6819 | 18.2899 | 2018-05-24 08:00 | 8 | 5 | 0 | 0 | 2018-05-24 08:00 | 8 | 5 | 0 | 0 | 2018-05-24 08:00 | 8 | 5 | 0 | 0
2018-05-24 09:00 | 9 | 5 | 86.7094 | 18.2957 | 2018-05-24 09:00 | 9 | 5 | 0 | 0 | 2018-05-24 09:00 | 9 | 5 | 0 | 0 | 2018-05-24 09:00 | 9 | 5 | 0 | 0
2018-05-24 10:00 | 10 | 5 | 86.7933 | 18.3134 | 2018-05-24 10:00 | 10 | 5 | 0 | 0 | 2018-05-24 10:00 | 10 | 5 | 0 | 0 | 2018-05-24 10:00 | 10 | 5 | 0 | 0
2018-05-24 11:00 | 11 | 5 | 86.8009 | 18.315 | 2018-05-24 11:00 | 11 | 5 | 0 | 0 | 2018-05-24 11:00 | 11 | 5 | 0 | 0 | 2018-05-24 11:00 | 11 | 5 | 0 | 0
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -

## Step 3. Avg Energy Calcs
Day of Week | Hour | Circuit #1 Average Energy (kWh) | Circuit #2 Average Energy (kWh) | Circuit #3 Average Energy (kWh) | Circuit #4 Average Energy (kWh) | Total Average kWh | % Light on per hour | % Light off per hour
1 | 0 | 18.1959 | 17.681 | 0 | 6.9266 | 42.8035 | 21.4% | 78.6%
1 | 1 | 18.2133 | 17.7121 | 0 | 6.9388 | 42.8642 | 21.43% | 78.57%
1 | 2 | 18.1907 | 17.6848 | 0 | 6.9281 | 42.8035 | 21.4% | 78.6%
1 | 3 | 18.1849 | 17.6782 | 0 | 6.9255 | 42.7887 | 21.39% | 78.61%
1 | 4 | 18.1978 | 17.6879 | 0 | 6.9293 | 42.815 | 21.41% | 78.59%
1 | 5 | 18.1952 | 17.6879 | 0 | 6.9293 | 42.8124 | 21.41% | 78.59%
1 | 6 | 18.2046 | 17.6919 | 0 | 6.9309 | 42.8273 | 21.41% | 78.59%
1 | 7 | 18.2065 | 17.6904 | 0 | 6.9302 | 42.8271 | 21.41% | 78.59%
1 | 8 | 18.2091 | 17.7022 | 0 | 6.9349 | 42.8461 | 21.42% | 78.58%
1 | 9 | 18.2065 | 17.6845 | 0 | 6.9279 | 42.8189 | 21.41% | 78.59%
1 | 10 | 18.2068 | 17.6919 | 0 | 6.9309 | 42.8296 | 21.41% | 78.59%
1 | 11 | 18.1849 | 17.6695 | 0 | 6.9221 | 42.7766 | 21.39% | 78.61%
1 | 12 | 18.1759 | 17.6636 | 0 | 6.9198 | 42.7593 | 21.38% | 78.62%
1 | 13 | 18.1772 | 17.6742 | 0 | 6.9239 | 42.7753 | 21.39% | 78.61%
1 | 14 | 18.1695 | 17.6612 | 0 | 6.9188 | 42.7494 | 21.37% | 78.63%
1 | 15 | 18.1978 | 17.691 | 0 | 6.9305 | 42.8193 | 21.41% | 78.59%
1 | 16 | 18.2187 | 17.7096 | 0 | 6.9378 | 42.8662 | 21.43% | 78.57%
1 | 17 | 18.2474 | 17.719 | 0 | 6.9415 | 42.9078 | 21.45% | 78.55%
1 | 18 | 18.2374 | 17.7056 | 0 | 6.9362 | 42.8792 | 21.44% | 78.56%
1 | 19 | 18.0784 | 17.5032 | 0 | 6.8569 | 42.4385 | 21.22% | 78.78%
1 | 20 | 18.2155 | 17.6381 | 0 | 6.9098 | 42.7634 | 21.38% | 78.62%
1 | 21 | 18.2213 | 17.6552 | 0 | 6.9165 | 42.793 | 21.4% | 78.6%
1 | 22 | 18.249 | 17.6829 | 0 | 6.9273 | 42.8592 | 21.43% | 78.57%
1 | 23 | 18.2374 | 17.668 | 0 | 6.9215 | 42.8269 | 21.41% | 78.59%
2 | 0 | 18.2323 | 17.6608 | 18.4303 | 13.8561 | 68.1795 | 34.09% | 65.91%
2 | 1 | 18.155 | 17.5819 | 18.3439 | 13.7927 | 67.8735 | 33.94% | 66.06%
2 | 2 | 18.2287 | 17.6484 | 18.4105 | 13.8438 | 68.1314 | 34.07% | 65.93%
2 | 3 | 18.2046 | 17.6357 | 18.3918 | 13.8317 | 68.0637 | 34.03% | 65.97%
2 | 4 | 18.2522 | 17.6985 | 18.45 | 13.8783 | 68.2789 | 34.14% | 65.86%
2 | 5 | 18.2232 | 17.6755 | 18.4451 | 13.8674 | 68.2113 | 34.11% | 65.89%
2 | 6 | 18.2071 | 17.6506 | 18.4047 | 13.8425 | 68.1049 | 34.05% | 65.95%
2 | 7 | 18.1891 | 17.6257 | 18.3821 | 13.8242 | 68.0211 | 34.01% | 65.99%
2 | 8 | 18.2168 | 17.6294 | 18.4021 | 13.8332 | 68.0816 | 34.04% | 65.96%
2 | 9 | 18.2261 | 17.6661 | 18.4167 | 13.8531 | 68.162 | 34.08% | 65.92%
2 | 10 | 18.1939 | 17.6232 | 18.3834 | 13.8237 | 68.0243 | 34.01% | 65.99%
2 | 11 | 18.1907 | 17.6229 | 18.3847 | 13.8241 | 68.0224 | 34.01% | 65.99%
2 | 12 | 18.2281 | 17.6574 | 18.4138 | 13.8486 | 68.1478 | 34.07% | 65.93%
2 | 13 | 18.231 | 17.645 | 18.3905 | 13.8349 | 68.1013 | 34.05% | 65.95%
2 | 14 | 18.2258 | 17.6528 | 18.3995 | 13.8414 | 68.1195 | 34.06% | 65.94%
2 | 15 | 18.2168 | 17.6251 | 18.3885 | 13.8264 | 68.0568 | 34.03% | 65.97%
2 | 16 | 18.2197 | 17.6183 | 18.3772 | 13.8195 | 68.0346 | 34.02% | 65.98%
2 | 17 | 18.1975 | 17.6136 | 18.375 | 13.8168 | 68.0028 | 34% | 66%
2 | 18 | 18.2123 | 17.6074 | 18.3578 | 13.8079 | 67.9854 | 33.99% | 66.01%
2 | 19 | 18.1901 | 17.5897 | 18.3504 | 13.7981 | 67.9282 | 33.96% | 66.04%
2 | 20 | 18.192 | 17.6167 | 18.3782 | 13.8192 | 68.0061 | 34% | 66%
2 | 21 | 18.1775 | 17.6151 | 18.3656 | 13.8139 | 67.9721 | 33.99% | 66.01%
2 | 22 | 18.2007 | 17.6307 | 18.3691 | 13.8213 | 68.0218 | 34.01% | 65.99%
2 | 23 | 18.2393 | 17.6823 | 18.4199 | 13.8606 | 68.2022 | 34.1% | 65.9%
3 | 0 | 18.2438 | 0 | 0 | 0 | 18.2438 | 9.122% | 90.88%
3 | 1 | 18.2648 | 0 | 0 | 0 | 18.2648 | 9.132% | 90.87%
3 | 2 | 18.2242 | 0 | 0 | 0 | 18.2242 | 9.112% | 90.89%
3 | 3 | 18.2203 | 0 | 0 | 0 | 18.2203 | 9.11% | 90.89%
3 | 4 | 18.2236 | 0 | 0 | 0 | 18.2236 | 9.112% | 90.89%
3 | 5 | 18.231 | 0 | 0 | 0 | 18.231 | 9.115% | 90.88%
3 | 6 | 18.2442 | 0 | 0 | 0 | 18.2442 | 9.122% | 90.88%
3 | 7 | 18.2307 | 0 | 0 | 0 | 18.2307 | 9.115% | 90.88%
3 | 8 | 18.2413 | 0 | 0 | 0 | 18.2413 | 9.121% | 90.88%
3 | 9 | 18.1888 | 0 | 0 | 0 | 18.1888 | 9.094% | 90.91%
3 | 10 | 18.2033 | 0 | 0 | 0 | 18.2033 | 9.102% | 90.9%
3 | 11 | 18.3057 | 0 | 0 | 0 | 18.3057 | 9.153% | 90.85%
3 | 12 | 18.2767 | 0 | 0 | 0 | 18.2767 | 9.138% | 90.86%
3 | 13 | 18.2806 | 0 | 0 | 0 | 18.2806 | 9.14% | 90.86%
3 | 14 | 18.3308 | 0 | 0 | 0 | 18.3308 | 9.165% | 90.83%
3 | 15 | 18.3147 | 0 | 0 | 0 | 18.3147 | 9.157% | 90.84%
3 | 16 | 18.3079 | 0 | 0 | 0 | 18.3079 | 9.154% | 90.85%
3 | 17 | 18.3018 | 0 | 0 | 0 | 18.3018 | 9.151% | 90.85%
3 | 18 | 18.2963 | 0 | 0 | 0 | 18.2963 | 9.148% | 90.85%
3 | 19 | 18.3227 | 0 | 0 | 0 | 18.3227 | 9.161% | 90.84%
3 | 20 | 18.2783 | 0 | 0 | 0 | 18.2783 | 9.139% | 90.86%
3 | 21 | 18.2776 | 0 | 0 | 0 | 18.2776 | 9.139% | 90.86%
3 | 22 | 18.2967 | 0 | 0 | 0 | 18.2967 | 9.148% | 90.85%
3 | 23 | 18.3353 | 0 | 0 | 0 | 18.3353 | 9.168% | 90.83%
4 | 0 | 0 | 0 | 18.3743 | 6.9164 | 25.2907 | 12.65% | 87.35%
4 | 1 | 0 | 0 | 18.3403 | 6.9036 | 25.2439 | 12.62% | 87.38%
4 | 2 | 0 | 0 | 18.3937 | 6.9237 | 25.3174 | 12.66% | 87.34%
4 | 3 | 0 | 0 | 18.3885 | 6.9217 | 25.3103 | 12.66% | 87.34%
4 | 4 | 0 | 0 | 18.4096 | 6.9296 | 25.3392 | 12.67% | 87.33%
4 | 5 | 0 | 0 | 18.4487 | 6.9444 | 25.3931 | 12.7% | 87.3%
4 | 6 | 0 | 0 | 18.4361 | 6.9396 | 25.3757 | 12.69% | 87.31%
4 | 7 | 0 | 0 | 18.472 | 6.9531 | 25.4251 | 12.71% | 87.29%
4 | 8 | 0 | 0 | 18.4849 | 6.958 | 25.4429 | 12.72% | 87.28%
4 | 9 | 0 | 0 | 18.3837 | 6.9199 | 25.3036 | 12.65% | 87.35%
4 | 10 | 0 | 0 | 18.375 | 6.9166 | 25.2916 | 12.65% | 87.35%
4 | 11 | 0 | 0 | 18.4219 | 6.9343 | 25.3561 | 12.68% | 87.32%
4 | 12 | 0 | 0 | 18.4287 | 6.9368 | 25.3655 | 12.68% | 87.32%
4 | 13 | 0 | 0 | 18.4979 | 6.9629 | 25.4607 | 12.73% | 87.27%
4 | 14 | 0 | 0 | 18.5296 | 6.9748 | 25.5044 | 12.75% | 87.25%
4 | 15 | 0 | 0 | 18.4891 | 6.9596 | 25.4487 | 12.72% | 87.28%
4 | 16 | 0 | 0 | 18.438 | 6.9403 | 25.3784 | 12.69% | 87.31%
4 | 17 | 0 | 0 | 18.4736 | 6.9537 | 25.4274 | 12.71% | 87.29%
4 | 18 | 0 | 0 | 18.4956 | 6.962 | 25.4577 | 12.73% | 87.27%
4 | 19 | 0 | 0 | 18.4206 | 6.9338 | 25.3543 | 12.68% | 87.32%
4 | 20 | 0 | 0 | 18.483 | 6.9573 | 25.4403 | 12.72% | 87.28%
4 | 21 | 0 | 0 | 18.4953 | 6.9619 | 25.4572 | 12.73% | 87.27%
4 | 22 | 0 | 0 | 18.4807 | 6.9564 | 25.4372 | 12.72% | 87.28%
4 | 23 | 0 | 0 | 18.4982 | 6.963 | 25.4612 | 12.73% | 87.27%
5 | 0 | 18.2619 | 0 | 0 | 0 | 18.2619 | 9.131% | 90.87%
5 | 1 | 18.2979 | 0 | 0 | 0 | 18.2979 | 9.149% | 90.85%
5 | 2 | 18.2535 | 0 | 0 | 0 | 18.2535 | 9.127% | 90.87%
5 | 3 | 18.2426 | 0 | 0 | 0 | 18.2426 | 9.121% | 90.88%
5 | 4 | 18.2793 | 0 | 0 | 0 | 18.2793 | 9.14% | 90.86%
5 | 5 | 18.2661 | 0 | 0 | 0 | 18.2661 | 9.133% | 90.87%
5 | 6 | 18.2825 | 0 | 0 | 0 | 18.2825 | 9.141% | 90.86%
5 | 7 | 18.2802 | 0 | 0 | 0 | 18.2802 | 9.14% | 90.86%
5 | 8 | 18.2899 | 0 | 0 | 0 | 18.2899 | 9.145% | 90.86%
5 | 9 | 18.2957 | 0 | 0 | 0 | 18.2957 | 9.148% | 90.85%
5 | 10 | 18.3125 | 1.0389 | 1.0854 | 0.21461 | 20.6513 | 10.33% | 89.67%
5 | 11 | 18.3134 | 1.0415 | 1.0858 | 0.81671 | 21.2574 | 10.63% | 89.37%
5 | 12 | 18.2873 | 1.1057 | 1.154 | 0.86755 | 21.4145 | 10.71% | 89.29%
5 | 13 | 18.2775 | 1.1042 | 1.1531 | 0.86662 | 21.4014 | 10.7% | 89.3%
5 | 14 | 18.2781 | 1.1035 | 1.1524 | 0.86608 | 21.4 | 10.7% | 89.3%
5 | 15 | 18.2838 | 1.1039 | 1.1535 | 0.86664 | 21.4078 | 10.7% | 89.3%
5 | 16 | 18.263 | 1.1049 | 1.1533 | 0.86696 | 21.3881 | 10.69% | 89.31%
5 | 17 | 18.2868 | 1.103 | 1.1529 | 0.86607 | 21.4088 | 10.7% | 89.3%
5 | 18 | 18.2967 | 1.103 | 1.1537 | 0.86638 | 21.4198 | 10.71% | 89.29%
5 | 19 | 18.2568 | 1.1058 | 1.1546 | 0.86779 | 21.3849 | 10.69% | 89.31%
5 | 20 | 18.2671 | 1.1046 | 1.1547 | 0.86737 | 21.3938 | 10.7% | 89.3%
5 | 21 | 18.2753 | 1.1044 | 1.1525 | 0.86646 | 21.3987 | 10.7% | 89.3%
5 | 22 | 18.2863 | 1.1042 | 1.152 | 0.8662 | 21.4087 | 10.7% | 89.3%
5 | 23 | 18.2648 | 1.1061 | 1.1545 | 0.86791 | 21.3934 | 10.7% | 89.3%
6 | 0 | 17.0559 | 17.6596 | 1.1547 | 7.3528 | 43.2231 | 21.61% | 78.39%
6 | 1 | 17.0342 | 17.6291 | 1.1529 | 7.3402 | 43.1564 | 21.58% | 78.42%
6 | 2 | 17.0671 | 17.6607 | 1.1552 | 7.3535 | 43.2365 | 21.62% | 78.38%
6 | 3 | 17.0122 | 17.6149 | 1.1549 | 7.3354 | 43.1174 | 21.56% | 78.44%
6 | 4 | 17.0224 | 17.6114 | 1.1544 | 7.3338 | 43.122 | 21.56% | 78.44%
6 | 5 | 17.0565 | 17.6453 | 1.1553 | 7.3474 | 43.2045 | 21.6% | 78.4%
6 | 6 | 17.0976 | 17.7071 | 1.1551 | 7.3716 | 43.3314 | 21.67% | 78.33%
6 | 7 | 17.1281 | 17.732 | 1.1562 | 7.3818 | 43.398 | 21.7% | 78.3%
6 | 8 | 17.0849 | 17.6775 | 1.1547 | 7.3599 | 43.277 | 21.64% | 78.36%
6 | 9 | 17.0779 | 17.6709 | 1.1549 | 7.3573 | 43.2611 | 21.63% | 78.37%
6 | 10 | 17.1133 | 17.6942 | 1.1558 | 7.3668 | 43.3301 | 21.67% | 78.33%
6 | 11 | 17.1108 | 17.7057 | 1.1541 | 7.3707 | 43.3414 | 21.67% | 78.33%
6 | 12 | 17.1504 | 17.7464 | 1.1532 | 7.3863 | 43.4363 | 21.72% | 78.28%
6 | 13 | 17.0837 | 17.6823 | 1.1546 | 7.3617 | 43.2822 | 21.64% | 78.36%
6 | 14 | 17.0991 | 17.6932 | 1.1532 | 7.3655 | 43.311 | 21.66% | 78.34%
6 | 15 | 17.0701 | 17.6547 | 1.1532 | 7.3503 | 43.2283 | 21.61% | 78.39%
6 | 16 | 17.0852 | 17.6719 | 1.1545 | 7.3576 | 43.2692 | 21.63% | 78.37%
6 | 17 | 17.0689 | 17.6706 | 1.1523 | 7.3562 | 43.248 | 21.62% | 78.38%
6 | 18 | 17.049 | 17.657 | 1.1552 | 7.352 | 43.2132 | 21.61% | 78.39%
6 | 19 | 17.0315 | 17.6274 | 1.148 | 7.3377 | 43.1446 | 21.57% | 78.43%
6 | 20 | 17.0514 | 17.6255 | 1.1508 | 7.338 | 43.1657 | 21.58% | 78.42%
6 | 21 | 17.0864 | 17.6648 | 1.1524 | 7.354 | 43.2575 | 21.63% | 78.37%
6 | 22 | 17.0849 | 17.6727 | 1.1525 | 7.3571 | 43.2671 | 21.63% | 78.37%
6 | 23 | 17.0912 | 17.676 | 1.1515 | 7.3581 | 43.2769 | 21.64% | 78.36%
7 | 0 | 18.1486 | 0 | 18.3487 | 6.9067 | 43.404 | 21.7% | 78.3%
7 | 1 | 18.1289 | 0 | 18.3449 | 6.9053 | 43.3791 | 21.69% | 78.31%
7 | 2 | 18.1572 | 0 | 18.3688 | 6.9143 | 43.4403 | 21.72% | 78.28%
7 | 3 | 18.1814 | 0 | 18.3804 | 6.9187 | 43.4805 | 21.74% | 78.26%
7 | 4 | 18.211 | 0 | 18.4125 | 6.9307 | 43.5542 | 21.78% | 78.22%
7 | 5 | 18.2001 | 0 | 18.4144 | 6.9315 | 43.546 | 21.77% | 78.23%
7 | 6 | 18.172 | 0 | 18.3737 | 6.9161 | 43.4618 | 21.73% | 78.27%
7 | 7 | 18.1862 | 0 | 18.3856 | 6.9206 | 43.4925 | 21.75% | 78.25%
7 | 8 | 18.222 | 0 | 18.4338 | 6.9388 | 43.5946 | 21.8% | 78.2%
7 | 9 | 18.2496 | 0 | 18.4565 | 6.9473 | 43.6534 | 21.83% | 78.17%
7 | 10 | 18.1878 | 0 | 18.3675 | 6.9138 | 43.4691 | 21.73% | 78.27%
7 | 11 | 18.182 | 0 | 18.4196 | 6.9334 | 43.535 | 21.77% | 78.23%
7 | 12 | 18.2519 | 0 | 18.4759 | 6.9546 | 43.6824 | 21.84% | 78.16%
7 | 13 | 18.2757 | 0 | 18.5111 | 6.9679 | 43.7547 | 21.88% | 78.12%
7 | 14 | 18.2397 | 0 | 18.4616 | 6.9492 | 43.6505 | 21.83% | 78.17%
7 | 15 | 18.2625 | 0 | 18.5063 | 6.966 | 43.7348 | 21.87% | 78.13%
7 | 16 | 18.2651 | 0 | 18.5199 | 6.9712 | 43.7561 | 21.88% | 78.12%
7 | 17 | 18.3031 | 0 | 18.5648 | 6.9881 | 43.856 | 21.93% | 78.07%
7 | 18 | 18.2445 | 0 | 18.5079 | 6.9667 | 43.719 | 21.86% | 78.14%
7 | 19 | 18.2232 | 0 | 18.4642 | 6.9502 | 43.6377 | 21.82% | 78.18%
7 | 20 | 18.1708 | 0 | 18.4209 | 6.9339 | 43.5255 | 21.76% | 78.24%
7 | 21 | 18.1788 | 0 | 18.428 | 6.9366 | 43.5434 | 21.77% | 78.23%
7 | 22 | 18.1927 | 0 | 18.4451 | 6.943 | 43.5808 | 21.79% | 78.21%
7 | 23 | 18.193 | 0 | 18.4607 | 6.9489 | 43.6025 | 21.8% | 78.2%

## Step 4. Results
Day | Average Hourly kWh of all Circuits | Average Daily Weekday Electricity Usage (kWh) | Annual Weekday Electricity Usage (kWh/year) | TOTAL ANNUAL ELECTRICITY USAGE (kWh/year)
Monday | 68.0722 | 840.2067 | 219293.9602 | 327105.8049
Tuesday | 18.2684
Wednesday | 25.3868 | Average Daily Weekend Electricity Usage (kWh) | Annual Weekend Electricity Usage (kWh/year) | Approximate % of measured lighting load
Thursday | 20.0616 | 1036.6524 | 107811.8448 | 34.27%
Friday | 43.2541
Saturday | 43.5856 |  |  | Remaining Unmeasured Lighting Load (kWh/year)
Sunday | 42.8021 |  |  | 627306.8673
Total Days used in Measurement Period
112.0418

## Step 4a. Hourly Results
Average kWh per HOUR
DAY | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | Total
Sunday | 42.8035 | 42.8642 | 42.8035 | 42.7887 | 42.815 | 42.8124 | 42.8273 | 42.8271 | 42.8461 | 42.8189 | 42.8296 | 42.7766 | 42.7593 | 42.7753 | 42.7494 | 42.8193 | 42.8662 | 42.9078 | 42.8792 | 42.4385 | 42.7634 | 42.793 | 42.8592 | 42.8269 | 1027.2505
Monday | 68.1795 | 67.8735 | 68.1314 | 68.0637 | 68.2789 | 68.2113 | 68.1049 | 68.0211 | 68.0816 | 68.162 | 68.0243 | 68.0224 | 68.1478 | 68.1013 | 68.1195 | 68.0568 | 68.0346 | 68.0028 | 67.9854 | 67.9282 | 68.0061 | 67.9721 | 68.0218 | 68.2022 | 1633.7333
Tuesday | 18.2438 | 18.2648 | 18.2242 | 18.2203 | 18.2236 | 18.231 | 18.2442 | 18.2307 | 18.2413 | 18.1888 | 18.2033 | 18.3057 | 18.2767 | 18.2806 | 18.3308 | 18.3147 | 18.3079 | 18.3018 | 18.2963 | 18.3227 | 18.2783 | 18.2776 | 18.2967 | 18.3353 | 438.4408
Wednesday | 25.2907 | 25.2439 | 25.3174 | 25.3103 | 25.3392 | 25.3931 | 25.3757 | 25.4251 | 25.4429 | 25.3036 | 25.2916 | 25.3561 | 25.3655 | 25.4607 | 25.5044 | 25.4487 | 25.3784 | 25.4274 | 25.4577 | 25.3543 | 25.4403 | 25.4572 | 25.4372 | 25.4612 | 609.2825
Thursday | 18.2619 | 18.2979 | 18.2535 | 18.2426 | 18.2793 | 18.2661 | 18.2825 | 18.2802 | 18.2899 | 18.2957 | 20.6513 | 21.2574 | 21.4145 | 21.4014 | 21.4 | 21.4078 | 21.3881 | 21.4088 | 21.4198 | 21.3849 | 21.3938 | 21.3987 | 21.4087 | 21.3934 | 481.4783
Friday | 43.2231 | 43.1564 | 43.2365 | 43.1174 | 43.122 | 43.2045 | 43.3314 | 43.398 | 43.277 | 43.2611 | 43.3301 | 43.3414 | 43.4363 | 43.2822 | 43.311 | 43.2283 | 43.2692 | 43.248 | 43.2132 | 43.1446 | 43.1657 | 43.2575 | 43.2671 | 43.2769 | 1038.0988
Saturday | 43.404 | 43.3791 | 43.4403 | 43.4805 | 43.5542 | 43.546 | 43.4618 | 43.4925 | 43.5946 | 43.6534 | 43.4691 | 43.535 | 43.6824 | 43.7547 | 43.6505 | 43.7348 | 43.7561 | 43.856 | 43.719 | 43.6377 | 43.5255 | 43.5434 | 43.5808 | 43.6025 | 1046.0542